Rosedale College

Text for Water Cycle Strategy report

Water efficiency

The buildings have been designed to minimise water use where possible and all appliances in the new and redeveloped buildings will be low water-use appliances in order to reduce water usage to the minimum.

WCs

WCs will be low-flush devices with 4/2.5 litre flushes.

Taps and outlets

All outlets will be fitted with flow restrictors to ensure water flow is not excessive. The flow restrictors will be fitted with a cartridge to restrict flow as follows:

- Hand wash basins:				8 litres/minute

- Sinks in classrooms, staff rooms etc.:		8 litres/minute

- Sinks in main kitchen and cleaner’s cupboards: 	15 litres/minute

- Showers: 					8 litres/minute

All taps for handwash basins will be non-concussive press-down type taps with automatic shut-off in order to avoid taps running unnecessarily.

Landscape

The Landscape has been designed to minimise water use for irrigation with drought-resistant planting.