## Bill of materials
Colt London 4, London
Layer | Description (intensity metric and recycled content provided where available) | QTY | Unit
Sub-structure works | Building 1
Excavations
| Excavation to reduce levels (Building Footprint) | 13065 | m³
| Allowance for removing below ground obstructions | 13065 | m³
| Muck Away Exported Soil | 7839 | m³
| Stockpiling Soil on Site of remaining material | 5226 | m3
Piling
| Piling Mat | 5226 | m²
| Allowance for out of sequence piling | 1 | Item
| Gantry; Allowance for 900mm insitu RC piles, 35m depth, rotary bored. | 113 | nr
| Data hall; Allowance for 900mm insitu RC piles, 35m depth, rotary bored. | 370 | nr
| Allowance for disposal of arisings from piles - Removal from site | 10754.4963 | m²
Pile Caps
| Gantry Pile caps (allowance includes for formwork, concrete, DPM, sundry items) | 1130 | m³
| Reinforcent to Pile Caps - Assumed 200kg/m3 | 226 | t
| Data Hall; Allowance for pile caps (allowance includes for formwork, concrete, DPM, sundry items) | 4933.3333 | m3
| Reinforcent to Pile Caps - Assumed 200kg/m3 | 986.6667 | t
| Allowance for disposal of arisings from pile caps - Removal from site | Inc | m²
Ground Beams
Gantry; ground beams (600mm x 600mm)
| Formwork | 108 | m²
| Concrete | 32.4 | m³
| Reinforcement - Assumed 200kg/m3 | 6.48 | T
| DPM | 162 | m²
| Sundries (5%) | 5%
Allowance for ground beams to perimeter of data centre building (600mm x 600mm)
| Formwork | 364.8 | m²
| Concrete | 109.44 | m³
| Reinforcement - Assumed 200kg/m3 | 21.888 | T
| DPM | 547.2 | m²
| Sundries (5%) | 5%
Ground Floor Slab
| Whin dust 250mm type 3 sub base | 5226 | m²
| 50mm Blinding Layer | 5226 | m²
| Allowance for gas resistant membrane beneath slab | 5226 | m²
| 300mm thick C40 RC ground bearing slab | 1567.8 | m³
| Formwork | 5226 | m²
| Concrete Reinforcement - assume 130kg/m3 - Slab | 203.814 | T
| DPM | 5226 | m²
| Allowance for power float finish | 5226 | m²
| Allowance for Expansion Joint - New concrete upstand (with No Shear connectors) and a APF 400/50 as the expansion joint cover | 108 | m
| Allowance for 75mm structural screed to GF slab | 5226 | m²
| Allowance for gas proof membrane, venting strips and proprietary venting to perimeter of building. | 108 | m
Building 2
Excavations
| Excavation to reduce levels (Building Footprint) | 11257.5 | m³
| Allowance for removing below ground obstructions | 11257.5 | m³
| Muck Away Exported Soil | 6754.5 | m³
| Stockpiling Soil on Site of remaining material | 4503 | m3
Piling
| Piling Mat | 4503 | m²
| Allowance for out of sequence piling | 1 | Item
| Gantry; 900mm insitu RC piles, 35m depth, rotary bored. | 113 | nr
| Data hall; 900mm insitu RC piles, 35m depth, rotary bored. | 302 | nr
| Allowance for disposal of arisings from piles - Removal from site | 9240.4057 | m²
Pile Caps
| Gantry Pile; caps (allowance includes for formwork, concrete, DPM, sundry items) | 1130 | m3
| Reinforcent to Pile Caps - Assumed 200kg/m3 | 226 | T
| Data Hall; Allowance for pile caps (allowance includes for formwork, concrete, DPM, sundry items) | 4026.6667 | m3
| Reinforcent to Pile Caps - Assumed 200kg/m3 | 805.3333 | T
Ground Beams
Gantry; ground beams (600mm x 600mm)
| Formwork | 108 | m²
| Concrete | 32.4 | m³
| Reinforcement - Assumed 200kg/m3 | 6.48 | T
| DPM | 162 | m²
| Sundries (5%) | 5%
Allowance for ground beams to perimeter of data centre building (600mm x 600mm)
| Formwork | 291.6 | m²
| Concrete | 87.48 | m³
| Reinforcement - Assumed 200kg/m3 | 17.496 | T
| DPM | 437.4 | m²
| Sundries (5%) | 0.05
Ground floor slab
| Whin dust 250mm type 3 sub base | 4503 | m²
| 50mm Blinding Layer | 4503 | m²
| Allowance for gas resistant membrane beneath slab | 4503 | m²
| 300mm thick C40 RC ground bearing slab | 1350.9 | m³
| Formwork | 1350.9 | m²
| Concrete Reinforcement - assume 130kg/m3 - Slab | 175.617 | T
| DPM | 4503 | m²
| Allowance for power float finish | 4503 | m²
| Allowance for Expansion Joint - New concrete upstand (with No Shear connectors) and a APF 400/50 as the expansion joint cover | 352 | m
| Allowance for 75mm structural screed to GF slab | 4503 | m²
| Allowance for gas proof membrane, venting strips and proprietary venting to perimeter of building. | 244 | m
| Lift Pits Building 1 | 4 | Nr
| Lift Pits Building 2 | 3 | Nr
| Dock Leveller | 1 | Nr
Frame/upper floors | Building 1
Steel
Structural Steel - Data Centre
Level 00
| Raw steelwork allowance (76.2kg/m2) | 151.7904 | T
| Connections (7.6kg/m2) | 15.179 | T
| Bracing (3.8kg/m2) | 7.5895 | T
| Secondary Steel & Misc Steelwork @ 20% | 34.9118 | T
Level 01
| Raw steelwork allowance (76.2kg/m2) | 303.5808 | T
| Connections (7.6kg/m2) | 30.3581 | T
| Bracing (3.8kg/m2) | 15.179 | T
| Secondary Steel & Misc Steelwork @ 20% | 69.8236 | T
Level 02
| Raw steelwork allowance (76.2kg/m2) | 301.371 | T
| Connections (7.6kg/m2) | 30.1371 | T
| Bracing (3.8kg/m2) | 15.0686 | T
| Secondary Steel & Misc Steelwork @ 20% | 69.3153 | T
Level 03
| Raw steelwork allowance (76.2kg/m2) | 302.3616 | T
| Connections (7.6kg/m2) | 30.2362 | T
| Bracing (3.8kg/m2) | 15.1181 | T
| Secondary Steel & Misc Steelwork @ 20% | 69.5432 | T
Level 04
| Raw steelwork allowance (76.2kg/m2) | 300.1518 | T
| Connections (7.6kg/m2) | 30.0152 | T
| Bracing (3.8kg/m2) | 15.0076 | T
| Secondary Steel & Misc Steelwork @ 20% | 69.0349 | T
Level Roof
| Raw steelwork allowance (76.2kg/m2) | 298.7802 | T
| Connections (7.6kg/m2) | 29.878 | T
| Bracing (3.8kg/m2) | 14.939 | T
| Secondary Steel & Misc Steelwork @ 20% | 68.7194 | T
| Intumescent paint of structural steel frame (2 Hour) | 2288.0894 | T
Structural Steel - Gantry
Level 00
| Raw steelwork allowance (103.1kg/m2) | 96.0376 | T
| Connections (15.5kg/m2) | 14.4056 | T
| Bracing (5.2kg/m2) | 4.8019 | T
| Secondary Steel & Misc Steelwork @ 20% | 23.049 | T
Level 01
| Raw steelwork allowance (103.1kg/m2) | 128.0502 | T
| Connections (15.5kg/m2) | 19.2075 | T
| Bracing (5.2kg/m2) | 6.4025 | T
| Secondary Steel & Misc Steelwork @ 20% | 30.732 | T
Level 02
| Raw steelwork allowance (103.1kg/m2) | 146.402 | T
| Connections (15.5kg/m2) | 21.9603 | T
| Bracing (5.2kg/m2) | 7.3201 | T
| Provisional Allowance for addt. Secondary Steel | 35.1365 | T
Level 03
| Raw steelwork allowance (103.1kg/m2) | 147.5361 | T
| Connections (15.5kg/m2) | 22.1304 | T
| Bracing (5.2kg/m2) | 7.3768 | T
| Provisional Allowance for addt. Secondary Steel | 35.4087 | T
Level 04
| Raw steelwork allowance (103.1kg/m2) | 130.2153 | T
| Connections (15.5kg/m2) | 19.5323 | T
| Bracing (5.2kg/m2) | 6.5108 | T
| Provisional Allowance for addt. Secondary Steel | 31.2517 | T
Level 05
| Raw steelwork allowance (103.1kg/m2) | 130.2153 | T
| Connections (15.5kg/m2) | 19.5323 | T
| Bracing (5.2kg/m2) | 6.5108 | T
| Provisional Allowance for addt. Secondary Steel | 31.2517 | T
Level Roof
| Raw steelwork allowance (103.1kg/m2) | 65.1076 | T
| Connections (15.5kg/m2) | 9.7661 | T
| Bracing (5.2kg/m2) | 3.2554 | T
| Provisional Allowance for addt. Secondary Steel | 15.6258 | T
Chiller Gantry - Building 1
Level 5
| Raw steelwork allowance (103.1kg/m2) | 374.6654 | T
| Connections (15.5kg/m2) | 26.6012 | T
| Bracing (5.2kg/m2) | 13.488 | T
| Provisional Allowance for addt. Secondary Steel | 82.9509 | T
| Galvanisation of External Steel | 1712.438 | T
Building 2
Steel
Structural Steel - Data Centre
Level 00
| Raw steelwork allowance (76.2kg/m2) | 123.2916 | T
| Connections (7.6kg/m2) | 12.3292 | T
| Bracing (3.8kg/m2) | 6.1646 | T
| Provisional Allowance for addt. Secondary Steel | 28.3571 | T
Level 01
| Raw steelwork allowance (76.2kg/m2) | 246.5832 | T
| Connections (7.6kg/m2) | 24.6583 | T
| Bracing (3.8kg/m2) | 12.3292 | T
| Provisional Allowance for addt. Secondary Steel | 56.7141 | T
Level 02
| Raw steelwork allowance (76.2kg/m2) | 245.8974 | T
| Connections (7.6kg/m2) | 24.5897 | T
| Bracing (3.8kg/m2) | 12.2949 | T
| Provisional Allowance for addt. Secondary Steel | 56.5564 | T
Level 03
| Raw steelwork allowance (76.2kg/m2) | 246.0498 | T
| Connections (7.6kg/m2) | 24.605 | T
| Bracing (3.8kg/m2) | 12.3025 | T
| Provisional Allowance for addt. Secondary Steel | 56.5915 | T
Level 04
| Raw steelwork allowance (76.2kg/m2) | 246.0498 | T
| Connections (7.6kg/m2) | 24.605 | T
| Bracing (3.8kg/m2) | 12.3025 | T
| Provisional Allowance for addt. Secondary Steel | 56.5915 | T
Level Roof
| Raw steelwork allowance (76.2kg/m2) | 123.0249 | T
| Connections (7.6kg/m2) | 12.3025 | T
| Bracing (3.8kg/m2) | 6.1512 | T
| Provisional Allowance for addt. Secondary Steel | 28.2957 | T
| Intumescent paint of structural steel frame (2 Hour) | 1698.6374 | T
Structural Steel - Gantry
Level 00
| Raw steelwork allowance (103.1kg/m2) | 72.9433 | T
| Connections (15.5kg/m2) | 10.9415 | T
| Bracing (5.2kg/m2) | 3.6472 | T
| Provisional Allowance for addt. Secondary Steel | 17.5064 | T
Level 01
| Raw steelwork allowance (103.1kg/m2) | 145.8865 | T
| Connections (15.5kg/m2) | 21.883 | T
| Bracing (5.2kg/m2) | 7.2943 | T
| Provisional Allowance for addt. Secondary Steel | 35.0128 | T
Level 02
| Raw steelwork allowance (103.1kg/m2) | 145.8865 | T
| Connections (15.5kg/m2) | 21.883 | T
| Bracing (5.2kg/m2) | 7.2943 | T
| Provisional Allowance for addt. Secondary Steel | 35.0128 | T
Level 03
| Raw steelwork allowance (103.1kg/m2) | 145.8865 | T
| Connections (15.5kg/m2) | 21.883 | T
| Bracing (5.2kg/m2) | 7.2943 | T
| Provisional Allowance for addt. Secondary Steel | 35.0128 | T
Level 04
| Raw steelwork allowance (103.1kg/m2) | 147.1237 | T
| Connections (15.5kg/m2) | 22.0686 | T
| Bracing (5.2kg/m2) | 7.3562 | T
| Provisional Allowance for addt. Secondary Steel | 35.3097 | T
Level 05
| Raw steelwork allowance (103.1kg/m2) | 147.1237 | T
| Connections (15.5kg/m2) | 22.0686 | T
| Bracing (5.2kg/m2) | 7.3562 | T
| Provisional Allowance for addt. Secondary Steel | 35.3097 | T
Structural Steel - Roof Gantry
| Raw steelwork allowance (103.1kg/m2) | 73.5618 | T
| Connections (15.5kg/m2) | 11.0343 | T
| Bracing (5.2kg/m2) | 3.6781 | T
| Provisional Allowance for addt. Secondary Steel | 17.6548 | T
Chiller Gantry - Building 2
| Raw steelwork allowance (103.1kg/m2) | 201.779 | T
| Connections (15.5kg/m2) | 20.093 | T
| Bracing (5.2kg/m2) | 10.188 | T
| Provisional Allowance for addt. Secondary Steel | 46.412 | T
| Galvanisation of Steel | 1543.3853 | T
Building 1
Upper Floor Slab - Data Centre
Level 01 Floor Slab
| Metal Decking (Comflor R51) | 3955 | m²
| C40 Concrete Slabs poured on metal floor deck- 200mm thick | 791 | m³
| Allowance of 15kg/m2 reinforcement (loose bars and mesh) | 59.325 | T
| Allowance for Power Float Finish | 3955 | m²
Level 02 Floor Slab
| Metal Decking (Comflor R51) | 3968 | m²
| C40 Concrete Slabs poured on metal floor deck- 200mm thick | 793.6 | m³
| Allowance of 15kg/m2 reinforcement (loose bars and mesh) | 59.52 | T
| Allowance for Power Float Finish | 3968 | m²
Level 03 Floor Slab
| Metal Decking (Comflor R51) | 3939 | m²
| C40 Concrete Slabs poured on metal floor deck- 200mm thick | 787.8 | m³
| Allowance of 15kg/m2 reinforcement (loose bars and mesh) | 59.085 | T
| Allowance for Power Float Finish | 3939 | m²
Level 04 Floor Slab
| Metal Decking (Comflor R51) | 3921 | m²
| C40 Concrete Slabs poured on metal floor deck- 200mm thick | 784.2 | m³
| Allowance of 15kg/m2 reinforcement (loose bars and mesh) | 58.815 | T
| Allowance for Power Float Finish | 3921 | m²
Lift and stair cores - Building 1
| Shaft wall - Ground Floor, 1st Floor, 2nd Floor, 3rd Floor, 4th Floor | 709.5 | m3
| Allowance for 2 additional Shafts as recommended by Fire Strategy (No Design) All Floors | 198 | m3
| Concrete Reinforcement @ 130kg/m³ | 117.975 | T
Upper Floor Slab - Gantry
Level 01 Floor Slab
| 250mm concrete slab (100mm PC unit, 150mm C40 insitu RC) | 354.75 | m³
| Reinforcement allowance (25kg/m2) | 35.475 | T
| Allowance for Power Float Finish | 1419 | m²
Level 02 Floor Slab
| 250mm concrete slab (100mm PC unit, 150mm C40 insitu RC | 355 | m³
| Reinforcement allowance (25kg/m2) | 35.5 | T
| Allowance for Power Float Finish | 1420 | m²
Level 03 Floor Slab
| 250mm concrete slab (100mm PC unit, 150mm C40 insitu RC | 357.75 | m³
| Reinforcement allowance (25kg/m2) | 35.775 | T
| Allowance for Power Float Finish | 1431 | m²
Level 04 Floor Slab
| 250mm concrete slab (100mm PC unit, 150mm C40 insitu RC | 315.75 | m³
| Reinforcement allowance (25kg/m2) | 31.575 | T
| Allowance for Power Float Finish | 1263 | m²
Level 05 Roof Gantry Floor Slab
| 250mm concrete slab (100mm PC unit, 150mm C40 insitu RC) | 315.75 | m³
| Reinforcement allowance (25kg/m2) | 31.575 | T
| Allowance for Power Float Finish | 1263 | m²
Link Bridge
Building 2
Upper Floor Slabs - Data Centre
1st Floor Slab
| Metal Decking (Comflor R51) | 3236 | m²
| C40 Concrete Slabs poured on metal floor deck- 200mm thick | 647.2 | m³
| Allowance of 15kg/m2 reinforcement (loose bars and mesh) | 48.54 | T
| Allowance for Power Float Finish | 3236 | m²
2nd Floor Slab
| Metal Decking (Comflor R51) | 3227 | m²
| C40 Concrete Slabs poured on metal floor deck- 200mm thick | 645.4 | m³
| Allowance of 15kg/m2 reinforcement (loose bars and mesh) | 48.405 | T
| Allowance for Power Float Finish | 3227 | m²
3rd Floor Slab
| Metal Decking (Comflor R51) | 3229 | m²
| C40 Concrete Slabs poured on metal floor deck- 200mm thick | 645.8 | m³
| Allowance of 15kg/m2 reinforcement (loose bars and mesh) | 48.435 | T
| Allowance for Power Float Finish | 3229 | m²
4th Floor Slab
| Metal Decking (Comflor R51) | 3229 | m²
| C40 Concrete Slabs poured on metal floor deck- 200mm thick | 645.8 | m³
| Allowance of 15kg/m2 reinforcement (loose bars and mesh) | 48.435 | T
| Allowance for Power Float Finish | 3229 | m²
77
Lift and stair cores - Building 2
| Shaft wall - Ground Floor | 165 | m3
| Concrete Reinforcement @ 130kg/m³ | 21.45 | T
| Shaft wall - 1st Floor, 2nd Floor, 3rd Floor, 4th Floor | 660 | m3
| Allowance for additional Shaft as recommended by Fire Strategy (No Design) All Floors | 99 | m3
| Concrete Reinforcement @ 130kg/m³ | 98.67 | T
Upper Floor Slab - Gantry
Level 01 Floor Slab
| 250mm concrete slab (100mm PC unit, 150mm C40 insitu RC) | 353.75 | m³
| Reinforcement allowance (25kg/m2) | 35.375 | T
| Allowance for Power Float Finish | 1415 | m²
Level 02 Floor Slab
| 250mm concrete slab (100mm PC unit, 150mm C40 insitu RC | 353.75 | m³
| Reinforcement allowance (25kg/m2) | 35.375 | T
| Allowance for Power Float Finish | 1415 | m²
Level 03 Floor Slab
| 250mm concrete slab (100mm PC unit, 150mm C40 insitu RC | 353.75 | m³
| Reinforcement allowance (25kg/m2) | 35.375 | T
| Allowance for Power Float Finish | 1415 | m²
Level 04 Floor Slab
| 250mm concrete slab (100mm PC unit, 150mm C40 insitu RC | 356.75 | m³
| Reinforcement allowance (25kg/m2) | 35.675 | T
| Allowance for Power Float Finish | 1427 | m²
Level 05 Roof Gantry Floor Slab
| 250mm concrete slab (100mm PC unit, 150mm C40 insitu RC | 356.75 | m³
| Reinforcement allowance (25kg/m2) | 35.675 | T
| Allowance for Power Float Finish | 1427 | m²
Allowance for Pre-Fab Concrete Staircases
| Building 1 | 64 | nr
| Building 2 | 48 | nr
Chiller Cover to Mitigate Overheating Issues as requested by Design Team (Not in Design)
| Building 1 | 3921 | m2
| Building 2 | 3229 | m2
Roof | Building 1
| Reinforced bitumen membrane warm roof covering systems. | 3921 | m²
| Allowance for roof penetrations, upstands etc | 3921 | m²
| Gutter System; to suit above | 225 | m
| RWP; to suit above | 350 | m
| Extra Over for Man Safe System - General Allowance | 3921 | m²
| Extra Over for Temporary Protection - General Allowance | 3921 | m²
| Plant Screen - Acoustic louvres | 625.4 | m²
| Mesh Flooring to Chiller Gantry | 845 | m2
| Allowance for Dog Houses | 1 | item
| Allowance for Stairs / Walk Ways | 1 | item
Building 2
| Reinforced bitumen membrane warm roof covering systems. | 3229 | m²
| Allowance for roof penetrations, upstands etc | 3229 | m²
| Gutter System; to suit above | 225 | m
| RWP; to suit above | 350 | m
| Extra Over for Man Safe System - General Allowance | 3229 | m²
| Extra Over for Temporary Protection - General Allowance | 3229 | m²
| Plant Screen - Acoustic louvres | 556.5 | m²
| Mesh Flooring to Chiller Gantry | 680 | m2
| Allowance for Dog Houses | 1 | item
| Allowance for Stairs / Walk Ways | 1 | item
| Allowance for Green Roof - Office Area | 421 | m2
External Façade / Cladding | Data Centre Façade
Building One
| Composite Cladding - Grey; To comply with Part B & L regulations min. | 4455 | m2
| Glazed Curtain Walling | 1623 | m2
| Curtain Walling System - Integral look alike panels | 0 | m2
| Horizontal Aluminium Fin Light Shelves and Brise Soleil | 1605 | m
| Architectural Masonry | 974 | m2
| Green Wall | 107 | m2
| Louvres for Switchrooms | 1 | item
| Glazed Balustrade - Balcony | 28 | m
| Translucent façade to generator gantry - spec tbc. | 2984 | m2
Building Two
| Composite Cladding - Grey; To comply with Part B & L regulations min. | 3840 | m2
| Curtain Walling System - Integral Look alike panels | 1006 | m2
| Horizontal Shelves with PV Panels | 160.488 | m2
| Architectural Masonry | 878 | m2
| Allowance for louvres | 1 | item
| Translucent façade to generator gantry - spec tbc. | 3707 | m2
External doors/windows | Building One
External doors
| External double door sets | 1 | Nr
| External single door sets | 1 | Nr
| Glazed external door set - Double | 1 | Nr
| Allowance for Canopy | 1 | Nr
Windows & Glazing
| Glazed Windows | 29 | m2
| Entrance lobby glazing/door set | 17 | m2
Building Two
External doors
| External double door sets | 1 | Nr
| External single door sets | 2 | Nr
| Glazed external door set - Double | 0 | Nr
Windows & Glazing
| Glazed Windows - East Elevation | 201 | m2
| Allowance for External Staircases Building 1 |  | Nr
| Allowance for External Staircases Building 2 |  | Nr
Internal partitions/walls | Internal walls fitout
Building 1
Ground floor
| Whitespace | 4411 | m²
| Stud Partition | 836 | m²
| Chequer Plate Wall Protection; 1m high | 364 | m²
| External Wall Lining | 1083.5 | m²
First Floor
| Whitespace | 3443 | m²
| Stud Partition | 154 | m²
| Chequer Plate Wall Protection; 1m high | 304 | m²
| External Wall Lining | 1083.5 | m²
Second Floor
| Whitespace | 3443 | m²
| Stud Partition | 154 | m²
| Chequer Plate Wall Protection; 1m high | 304 | m²
| External Wall Lining | 1083.5 | m²
Third Floor
| Whitespace | 3443 | m²
| Stud Partition | 154 | m²
| Chequer Plate Wall Protection; 1m high | 304 | m²
| External Wall Lining | 1083.5 | m²
Fourth Floor
| Whitespace | 3443 | m²
| Stud Partition | 154 | m²
| Chequer Plate Wall Protection; 1m high | 304 | m²
| External Wall Lining | 1083.5 | m²
Building 2
Ground floor
| Whitespace | 3635.5 | m²
| Chequer Plate Wall Protection; 1m high | 420 | m²
| External Wall Lining | 1193.5 | m²
First Floor
| Whitespace | 2750 | m²
| Chequer Plate Wall Protection; 1m high | 391 | m²
| External Wall Lining | 1193.5 | m²
Second Floor
| Whitespace | 2750 | m²
| Chequer Plate Wall Protection; 1m high | 391 | m²
| External Wall Lining | 1193.5 | m²
Third Floor
| Whitespace | 2750 | m²
| Chequer Plate Wall Protection; 1m high | 391 | m²
| External Wall Lining | 1193.5 | m²
Fourth Floor
| Whitespace | 2750 | m²
| Chequer Plate Wall Protection; 1m high | 391 | m²
| External Wall Lining | 1193.5 | m²
| Allowance for corrosion protection | 1 | item
Internal doors | Internal Doors
Building 1
Ground floor
| Double Doors (Technical Space) | 26 | nr
| Double Doors (Office) | 1 | nr
| Single Doors (Technical Space) | 16 | nr
| Single Doors (Office) | 12 | nr
| Data Hall Doors (Double) | 4 | nr
| Prov Allowance for Mantrap Doors | 2 | nr
First Floor
| Double Doors (Technical Space) | 16 | nr
| Double Doors (Office) | 1 | nr
| Single Doors (Technical Space) | 3 | nr
| Single Doors (Office) | 3 | nr
| Data Hall Doors (Double) | 8 | nr
Second Floor
| Double Doors (Technical Space) | 16 | nr
| Double Doors (Office) | 1 | nr
| Single Doors (Technical Space) | 3 | nr
| Single Doors (Office) | 3 | nr
| Data Hall Doors (Double) | 8 | nr
Third Floor
| Double Doors (Technical Space) | 16 | nr
| Double Doors (Office) | 1 | nr
| Single Doors (Technical Space) | 3 | nr
| Single Doors (Office) | 3 | nr
| Data Hall Doors (Double) | 8 | nr
Fourth Floor
| Double Doors (Technical Space) | 16 | nr
| Double Doors (Office) | 1 | nr
| Single Doors (Technical Space) | 3 | nr
| Single Doors (Office) | 3 | nr
| Data Hall Doors (Double) | 8 | nr
Building 2
Ground floor
| Double Doors | 21 | nr
| Single Doors | 21 | nr
| Data Hall Doors (Double) | 4 | nr
| Prov Allowance for Mantrap Doors | 1 | nr
First Floor
| Double Doors | 11 | nr
| Single Doors | 11 | nr
| Data Hall Doors (Double) | 8 | nr
Second Floor
| Double Doors | 13 | nr
| Single Doors | 12 | nr
| Data Hall Doors (Double) | 8 | nr
Third Floor
| Double Doors | 12 | nr
| Single Doors | 10 | nr
| Data Hall Doors (Double) | 8 | nr
Fourth Floor
| Double Doors | 11 | nr
| Single Doors | 11 | nr
| Data Hall Doors (Double) | 8 | nr
Floor finishes | Building 1
Ground floor
| Whitespace - Epoxy finish | 1920 | m²
| Whitespace Data Hall - Epoxy finish | 981 | m²
| Office - carpet | 796 | m²
| Office - RAF | 796 | m²
| MDF Skirtings | 202 | m
| Entrance Matting | 1 | nr
First Floor
| Whitespace - Epoxy finish | 3242 | m²
| Office - carpet | 516 | m²
| Office - RAF | 516 | m²
| MDF Skirtings | 85 | m
Second Floor
| Whitespace - Epoxy finish | 3260 | m²
| Office - carpet | 516 | m²
| Office - RAF | 516 | m²
| MDF Skirtings | 85 | m
Third Floor
| Whitespace - Epoxy finish | 3273 | m²
| Office - carpet | 473 | m²
| Office - RAF | 473 | m²
| MDF Skirtings | 84 | m
Fourth Floor
| Whitespace - Epoxy finish | 3306 | m²
| Office - carpet | 421 | m²
| Office - RAF | 421 | m²
| MDF Skirtings | 59 | m
Building 2
Ground floor
| Whitespace - Epoxy finish | 1961 | m²
| Whitespace Data Hall - Epoxy finish | 981 | m²
| Entrance Matting | 1 | nr
First Floor
| Whitespace - Epoxy finish | 3101 | m²
Second Floor
| Whitespace - Epoxy finish | 3092 | m²
Third Floor
| Whitespace - Epoxy finish | 3094 | m²
Fourth Floor
| Whitespace - Epoxy finish | 3094 | m²
Wall finishes | Building 1
Ground Floor
| Finish to shaft walls | 1281.5 | m2
| Finishes to stud partition walls | 836 | m2
First Floor
| Finish to shaft walls | 1281.5 | m2
| Finishes to stud partition walls | 154 | m2
Second Floor
| Finish to shaft walls | 1281.5 | m2
| Finishes to stud partition walls | 154 | m2
Third Floor
| Finish to shaft walls | 1281.5 | m2
| Finishes to stud partition walls | 154 | m2
Fourth Floor
| Finish to shaft walls | 1281.5 | m2
| Finishes to stud partition walls | 154 | m2
Building 2
Ground Floor
| Finish to shaft walls | 1344.2 | m2
First Floor
| Finish to shaft walls | 1344.2 | m2
Second Floor
| Finish to shaft walls | 1344.2 | m2
Third Floor
| Finish to shaft walls | 1344.2 | m2
Fourth Floor
| Finish to shaft walls | 1344.2 | m2
Ceiling finishes | Building 1
Ground Floor
| Ceiling - Data Suites - Kingspan Tate | 981 | m2
| General ceilings elsewhere - Armstrong Ceiling- Perla | 3004 | m2
First Floor
| Ceiling - Data Suites - Kingspan Tate | 1962 | m2
| General ceilings elsewhere - Armstrong Ceiling- Perla | 1993 | m2
Second Floor
| Ceiling - Data Suites - Kingspan Tate | 1962 | m2
| General ceilings elsewhere - Armstrong Ceiling- Perla | 2006 | m2
Third Floor
| Ceiling - Data Suites - Kingspan Tate | 1962 | m2
| General ceilings elsewhere - Armstrong Ceiling- Perla | 1977 | m2
Fourth Floor
| Ceiling - Data Suites - Kingspan Tate | 1962 | m2
| General ceilings elsewhere - Armstrong Ceiling- Perla | 1959 | m2
Building 2
Ground Floor
| Ceiling - Data Suites- Kingspan Tate | 981 | m2
| General ceilings elsewhere - Armstrong Ceiling- Perla | 2157 | m2
First Floor
| Ceiling - Data Suites | 1962 | m2
| General ceilings elsewhere | 1274 | m2
Second Floor
| Ceiling - Data Suites | 1962 | m2
| General ceilings elsewhere | 1265 | m2
Third Floor
| Ceiling - Data Suites | 1962 | m2
| General ceilings elsewhere | 1267 | m2
Fourth Floor
| Ceiling - Data Suites | 1962 | m2
| General ceilings elsewhere | 1267 | m2
Furniture | Building 1
| Security reception desk | 1 | Item
| Allowance for kitchen fit out - white goods, joinery / carcussing etc | 1 | Item
| Mirrors / vanity units etc to WCs | 1 | Item
| Allowance for statutory signage | 1 | Item
| Allowance for directional signage | 1 | Item
| Allowance for data hall signage | 4 | No.
| Allowance for external furniture - bins / cycle stores | 1 | Item
| Allowance for sanitaryware / showers | 1 | Item
Building 2
| Allowance for kitchen fit out - white goods, joinery / carcussing etc | 1 | Item
| Mirrors / vanity units etc to WCs | 1 | Item
| Allowance for statutory signage | 1 | Item
| Allowance for directional signage | 1 | Item
| Allowance for data hall signage | 4 | No.
| Allowance for external furniture - bins / cycle stores / smoking shelters etc | 1 | Item
| Allowance for sanitaryware / showers | 1 | Item
External works | External works - Landscaping
| Site Area | 56102 | m²
| Site area less building footprint | 7898 | m²
Excavation
| Site Strip: Topsoil | 0 | m³
| Disposal on site | 0 | m³
| Disposal off site (Assumed non contaminated) | 0 | m³
Pathways
| Kerbstones - assume wide profile concrete kerb | 800 | m
| Proposed Walk Ways (Assumed Asphalt); Includes filling required | 222 | m²
| Paving Flags to car-park | 789.8 | m²
Soft Landscaping
| Covered Bike Stand (10m2) | 1 | Nr
| Smoking Shelter | 1 | Nr
| Turnstiles for Bikes | 1 | Nr
Provision for Development of Landscaping Scope
| Provision for Development of Landscaping Scope; Includes Existing Embankment to be re-profiled, Proposed Grass Areas & Grass Crete Landscape Areas and All cultivating of Bushes, Trees etc | 623 | m2
Hard Landscaping
| Car Park White Lining | 50 | Nr
| Road Marking | 1 | Item
| Asphalt surface - suitable for heavy vehicle loading. Currently assumed SMA Surf. With AC Base/ Binder to better resist rutting/ static deformation. | 5380 | m2
| Block Paving/ grasscrete area - designed to allow fire tender vehicle access, in line with Architect's requirements | 1022 | m2
| Block Paving/ asphalt footway area in line with Architect's requirements | 1731 | m2
| Permeable Paving - in line with Architect's requirements, subject to below ground utilities and loading requirements | 914 | m2
| Tactile Paving | 7 | m2
| Full height Kerb | 828 | m
| Dropped Bull nose/ channel kerb for flush/ Laying edge/ Crossing areas | 232 | m
| Splay Kerb for fire tender/ maintenance access only | 28 | m
| Water attentuation - Temp Item for Building 1 | 1 | item
| Water attentuation - Permanent Item for Building 2 | 1 | item
Fence
| 358 Welded Mesh Fence - LPS1175SR1/2 & Crash Gates | 600 | m
| Allowance for removal of exisiting Fences | 1 | item
| Crash Gates | 1 | item
| Gates (Main Entrance) | 1 | Nr
| Gates (Electronic) Assumption | 1 | Nr
| Folding Entrance Gates | 12 | m
| Bollards; Steel bollard; galvanised mild steel etch primed; finish painted white and red; including all necessary fixings and grouting, welds, base plates, fixings, supports, bearers, fillets, packers etc. necessary; complete | 50 | Nr
Other
| Provisional Allowance for Fuel Interceptor | 2 | Nr
External works - Services distribution
Scope not yet defined
| Allowance for below ground drainage - Surface water | 56102 | m²
| Extra over for rainwater harvesting | 1 | item
| Allowance for below ground drainage - Foul water | 56102 | m²
| Allowance for trenching to MV Power distribution | 56102 | m²
| Allowance for trenching to Fuel Distribution | 56102 | m²
| Allowance for trenching to Water | 56102 | m²
| Allowance for trenching to Fire Protection system | 56102 | m²
| Allowance for trenching to Sitewide small power | 1 | Nr
| 1 KV Supply Route1 KV A Supply Route (3no. 250mm + 3no. 150mm MV Duct) | 201 | m
| 1 KV Alternative Supply Route (3no. 250mm + 3no. 150mm MV Duct) | 170 | m
| 66 KV | 196 | m
| District Heating (2no. DN700/900 pipes, 2600mm wide trench) | 152 | m
| Extension of Existing 11KV Supply | 153 | m
| Extension of Existing Chamber | 1 | Nr
| Fibre A 13no. 95mm Ductwork | 110 | m
| Fibre A Chambers | 4 | Nr
| Fibre B 6no. 95mm Ductwork | 118 | m
| Fibre B Chambers | 4 | Nr
| Fibre C 8no. 95mm Ductwork | 142 | m
| Fibre C Chambers | 5 | Nr
| Fibre D 16no. 95mm Ductwork | 152 | m
| Fibre D Chambers | 5 | Nr
| Fibre Duct Ring (16no. 150mm) | 188 | m
| Fibre Duct Ring Chamber | 3 | Nr
| Fibre Interconnection of MMR Rooms 58no. 150mm Fibre Ducts | 153 | m
| Fibre Interconnection Chambers | 2 | Nr
| Fuel Fill Cabinet | 1 | Nr
| Small Power & ELV (2no. 150mm for SP & 2no. 150mm for ELV) | 737 | m
| Water Supply Connections 1no. 200m pipe | 142 | m
External works - Other items
| General allowance for earthing and bonding | 56102 | m²
| Allowance for External Cameras | 20 | Nr
| Allowance for Access Control to Gates | 3 | Nr
| Control Wiring for Below Ground Pumps | 1 | Nr
| Allowance for external lighting | 56102 | m²
| Allowance for fire hydrants | 20 | Nr