## Table 1
3.0 Assessment Scope Table 1 below presents those issues we propose to be scoped in (included) and those scoped out (excluded) from the air quality assessment. Table 1: Proposed Scope of Air Quality Assessment
Issue | Scoped In / Out | LBH Requirement
Detailed dispersion modelling of generator emissions – Further detail on the scope and methodology is provided in the following section. | In | In
Cumulative Impact Assessment with adjacent Data Centre – Further detail on the scope and methodology is provided in the following section. | In | In
Construction Phase Dust Assessment – Construction operations are largely associated with alterations to buildings, fabrication and installation of plant, with no major excavation or earthworks. It is envisaged that construction dust control measures would be enforced by planning condition. | Out | Out
Traffic Emissions Screening Assessment – The extant use is as a logistics park, as such overall trip generation associated with the Site will not exceed the established baseline and therefore a screening assessment is scoped out. | Out | In? depending of the duration of the construction phase
Air Quality Neutral (AQN) Assessment – There is a clear statement in the Air Quality Neutral guidance that back-up generators should be excluded “3.3.1: Backup plants installed for emergency and life safety power supply, such as diesel generators, may be excluded from the calculation of predicted building emissions.” And further “2.2.2 Developments that are subject to Environmental Permits, issued either by the Environment Agency or the Borough Council, are subject to the Air Quality Neutral benchmarks for all emission sources within the development not controlled by the Environmental Permit.” All emission points will be controlled by Environmental Permits. The air quality assessment will include a statement on the Environment Agency’s current position on Best Available Techniques with respect to emission concentrations and how the operator will comply with this. The proposed overall trip generation associated with the Site will not exceed the established baseline. Therefore, it is considered that the development meets the ‘excluded development’ criteria and it is proposed an AQN assessment is scoped out. | Out | In | Must be included - the guidance does not exclude them at all. These are not
Air Quality Positive – The current LBH Air Quality Action Plan 2019-2024 emphasizes the need for an Air Quality positive approach in Air Quality Focus Areas (AQFA). The Site is not within an AQFA, neither is it within the revised AQFA outlined in the ‘Pre-consultation draft Air Quality Action Plan – 2025- 2030’. The London Plan Air Quality Positive (AQP) guidance only requires its application for planning applications that are classified as ‘large scale development’ as defined in Appendix 1 of the AQP guidance. This development does not fall within those categories and therefore we propose Air Quality positive is scoped out. The air quality assessment will include a statement on the Environment Agency’s current position on Best Available Techniques with respect to emission concentrations and how the operator will comply with this. | Out | In
Damage Cost Calculation (DCC) – The AQN guidance is not applicable to the development. There is no Local Plan or Supplementary Planning Guidance requiring a DCC. The current AQAP does not require a DCC. The ‘Pre- | To be confirmed | In
consultation draft Air Quality Action Plan – 2025-2030’ contains Actions 8 and 9, however these do not strictly apply as the Site is not within an AQFA, and it is not an ‘applicable’ development under the AQN guidance. However, the draft Air Quality Action Plan notes that historically for back-up generators where ‘mitigation provided by the developer was insufficient to mitigate total emissions’ a DCC has been used to secure s106 payments. As such, we would seek to clarify under what circumstances a DCC would be required. |  | In
Assessment of Impacts on Ecological Receptors – The Site falls within the SSSI Impact Risk Zone for ‘energy from waste incineration, other incineration, landfill gas generation plant, pyrolysis/gasification, anaerobic digestion, sewage treatment works, other incineration/combustion’ >50MW energy input. Given the generators are operated in a back-up provision they are not considered to fall within the same category as the examples, which are continuously operating plant. For context, the nearest SSSI is 5km distant. On this basis assessment of impacts on ecological receptors is screened out. | Out
Emissions Management Plan – The NPPF Paragraph 201, states: ‘The focus of planning policies and decisions should be on whether proposed development is an acceptable use of land, rather than the control of processes or emissions (where these are subject to separate pollution control regimes). Planning decisions should assume that these regimes will operate effectively’. On the basis that all emission points to air at the Site will fall within the scope of the Environmental Permit (EP) issued by the Environment Agency, an emissions management plan is scoped out of the planning application. The air quality assessment will include a statement on the Environment Agency’s current position on Best Available Techniques with respect to emission concentrations, alongside details on the standard EP testing regime. | Out | In

## Table 2
4.0 Assessment Approach and Methodology The assessment would comprise the following:  detailed dispersion modelling completed using either AERMOD or ADMS, both models are accepted by regulatory authorities as appropriate for similar installations, with inclusion of: o buildings for plume downwash effects; o topography; o a minimum of 3 years’ of meteorological data from Heathrow Airport.  sensitive receptors will be modelled using a combination of discrete receptors (for isolated properties, e.g. the neighbouring daycare centre), and gridded receptors (over residential areas);  a review of the existing air quality in the area of the installation on the basis of monitoring and modelled data obtained from the LBH and other national networks (e.g. London Air maps, Defra backgrounds etc). It is not proposed to undertake any site-specific monitoring as part of the assessment;  derivation of emission source term: o for the proposed data centre based on the selected generator manufacturer emissions datasheets;
o for the adjacent data centre based upon publicly available information from the planning portal and Environment Agency decision documents;  modelling of combustion emissions from the generators during the following scenarios: o routine testing and maintenance; and o grid outage scenarios (realistic grid outage durations will be selected based upon the latest data);  statistical analysis (applying the hypergeometric mean approach as outlined in Environment Agency guidance3) of probability of operational hours (during routine testing and maintenance, and grid outage scenarios) coinciding with worst case meteorological dispersion conditions; and  assessment of predicted ground level impacts against Limit Values for nitrogen dioxide and particulate PM10 and PM2.5) in the Air Quality Standards Regulations (as amended). Closure We trust that the above provides sufficient information on the proposed scope of the air quality assessment to be completed under the relevant regulatory framework of the ES. We would be grateful if you could confirm as part of the response to the pre-application meeting that the scope is agreed by LBH or if not any additional elements of work required. Please do not hesitate to contact us if you would like clarification on any aspect. Regards, SLR Consulting Limited
Morgan Fitzpatrick Air Quality Technical Discipline Manager mfitzpatrick@slrconsulting.com
3 https://www.gov.uk/guidance/specified-generators-dispersion-modelling-assessment