## Sheet1
Bullsbrook Road Sub-station
71554/APP/2025/47
LLFA Planning Application Review
Comment Responses
Parameter | Assessment & Reasoning | Response
3a) Runoff Destination (at site boundary) | MORE INFORMATION REQUIRED – The applicant should consider implementing small-scale SuDS, such as raingardens and tree pits, in the margins of the site, or justify their exclusion. | There are no opportunities for tree pits within the sub-compound, as there are no trees permitted. Marginal rain gardens within the sub-compound were considered, but were discounted due maintenance requirements within a restricted area. Instead, opportunities for rain gardens and tree pits will be explored when developing the surrounding car parking as part of the wider masterplan.
3c) Peak Flow Control | FAIL – The proposed runoff rate is not the greenfield runoff rate, nor has it met Hillingdon’s guidance of 1-2l/s. The proposed runoff rate must be reduced as much as possible, and a site constraints plan provided where guidance cannot be met. | As discussed in the meeting of 24/10/24 (minutes agreed by Metis by email 04/11/24) and outlined in the report, existing drained areas and runoff rates have been used when considering storm water restrictions. This is because the application boundary is less than 1ha, not in a Critical Drainage Area, and not in an area at risk of surface water flooding, this is not classed as a major development in accordance with LBH criteria. As such, the requirements of LBH Local Plan Part 2 Policy DMEI 10 do not apply.
3d) Volume Control | MORE INFORMATION REQUIRED – The applicant should provide the greenfield, existing and proposed runoff volumes for a 6 hour 1 in 100 year rainfall event. | InfoDrainage Calculated Greenfield Volume (FEH2022). 100 Year 360 Minute Storm = 62.408m3 Post development 100 year 360 minute (+40%CC) = 155.77m3 Pre and post development impermeable areas are similar, and as such pre and post development discharge volumes will be similar.
3e) Flood Risk | FAIL – The applicant must demonstrate how exceedance flows are suitably managed and add the exceedance flow routes to the drainage layout. MORE INFROMATION REQUIRED – The InfoDrainage calculations should use the entire site area, not just the impermeable area. This is to represent a worst-case scenario because, following prolonged periods of rainfall, it is likely that any permeable areas will be saturated and act as impermeable, therefore any rainfall is likely to runoff the surface and enter the drainage system. MORE INFORMATION REQUIRED – The calculations do not use the latest rainfall data (FEH22). | Exceedance flow routes have been added to the layout. See attached updated layout. A contribution from permeable areas that could enter the drainage system has been added to the model. The network was modelled using InfoDrainage 2023, which does not allow FEH 2022. The network has been re-modelled with InfoDrainage 2024 using FEH 2022. See attached results
3f) Maintenance | FAIL – The drainage strategy does not contain the maintenance tasks and frequencies for all proposed drainage components. | Maintenance strategy attached.