## 2 Units Operational
UP4 - 4.080MW DATAHALL DIRECT AIR SOLUTION @ 100% LOAD - 2 DAO's OPERATIONAL
Drawing Reference - BRG - 0474 - UP4 - 02 - DR - A - 010201
2017 ASHRAE Handbook - Fundamentals (SI) |  | Annual Consumption Calculation Basics
LONDON HEATHROW, United Kingdom |  | Constant full year cooling load |  | [kW] | 552 | This IT load is based on 500 W/m2 Datahall Area 1105m2
Lat: | 51.478N
Long: | 0.461W | Qty. of units |  | (pcs.) | 2 | 2 Units at full load provide 680kW of cooling capacity each Based on a total load of552KW 2 units would be operational at. 276kW each.
Elev: | 150 | Resilience |  | (pcs.) | 0
|  | Supply Temperature |  | [°C ] | 26
|  | Return Temperature |  | [°C ] | 39
|  | Air Volume per DAO |  | [m3/s] | 21.13
|  | Design pressure |  | [Pa] | 187
|  | Filter Condition |  |  | Moderate
|  | All data per single unit |  | Average = | 35.2761
Dry bulb temperature | Wet Bulb Temperature | hours / year | Absorbed Power Total | Cooling per single unit | SEER per hour (Cooling / Power input)
°C | °C | h | kW
TOTALS
4 | 3.3648 | 1 | 7.824 | 276 | 35.2761
2 | 1.4482 | 1 | 7.824 | 276 | 35.2761
0.3 | -0.046933 | 1 | 7.824 | 276 | 35.2761
0 | -0.25849 | 1 | 7.824 | 276 | 35.2761
-0.3 | -0.55507 | 1 | 7.824 | 276 | 35.2761
-1 | -1.2876 | 1 | 7.824 | 276 | 35.2761
-0.4 | -0.65368 | 1 | 7.824 | 276 | 35.2761
0.7 | 0.36673 | 1 | 7.824 | 276 | 35.2761
0.8 | 0.20246 | 1 | 7.824 | 276 | 35.2761
1.7 | 1.1151 | 1 | 7.824 | 276 | 35.2761
3.1 | 2.072 | 1 | 7.824 | 276 | 35.2761
4.4 | 2.9538 | 1 | 7.824 | 276 | 35.2761
6 | 4.3055 | 1 | 7.824 | 276 | 35.2761
6.2 | 4.4098 | 1 | 7.824 | 276 | 35.2761
6 | 4.3046 | 1 | 7.824 | 276 | 35.2761
5.7 | 4.2307 | 1 | 7.824 | 276 | 35.2761
5.1 | 3.9549 | 1 | 7.824 | 276 | 35.2761
4.9 | 3.8907 | 1 | 7.824 | 276 | 35.2761
5.1 | 4.305 | 1 | 7.824 | 276 | 35.2761
5.4 | 4.5965 | 1 | 7.824 | 276 | 35.2761
5.7 | 4.7966 | 1 | 7.824 | 276 | 35.2761
5.8 | 5.0307 | 1 | 7.824 | 276 | 35.2761
5.6 | 4.9272 | 1 | 7.824 | 276 | 35.2761
5.5 | 4.9216 | 1 | 7.824 | 276 | 35.2761
6 | 5.4594 | 1 | 7.824 | 276 | 35.2761
6.6 | 6.147 | 1 | 7.824 | 276 | 35.2761
6.5 | 6.2967 | 1 | 7.824 | 276 | 35.2761
7 | 6.6413 | 1 | 7.824 | 276 | 35.2761
8.5 | 7.8136 | 1 | 7.824 | 276 | 35.2761
8.8 | 7.8017 | 1 | 7.824 | 276 | 35.2761
8.8 | 7.7014 | 1 | 7.824 | 276 | 35.2761
8.4 | 6.9267 | 1 | 7.824 | 276 | 35.2761
7.8 | 6.354 | 1 | 7.824 | 276 | 35.2761
8.4 | 6.6017 | 1 | 7.824 | 276 | 35.2761
8.8 | 6.6609 | 1 | 7.824 | 276 | 35.2761
9.4 | 7.597 | 1 | 7.824 | 276 | 35.2761
9 | 7.2185 | 1 | 7.824 | 276 | 35.2761
9.4 | 7.5979 | 1 | 7.824 | 276 | 35.2761
8.7 | 6.4358 | 1 | 7.824 | 276 | 35.2761
8.4 | 6.514 | 1 | 7.824 | 276 | 35.2761
8.3 | 6.5115 | 1 | 7.824 | 276 | 35.2761
7.5 | 6.0254 | 1 | 7.824 | 276 | 35.2761
7.4 | 5.9306 | 1 | 7.824 | 276 | 35.2761
6.8 | 5.5841 | 1 | 7.824 | 276 | 35.2761
6.9 | 5.6809 | 1 | 7.824 | 276 | 35.2761
6.5 | 5.3872 | 1 | 7.824 | 276 | 35.2761
6.9 | 5.544 | 1 | 7.824 | 276 | 35.2761
5.7 | 5.0255 | 1 | 7.824 | 276 | 35.2761
4.9 | 4.3337 | 1 | 7.824 | 276 | 35.2761
5.2 | 4.7681 | 1 | 7.824 | 276 | 35.2761
5 | 4.6647 | 1 | 7.824 | 276 | 35.2761
4.4 | 4.0709 | 1 | 7.824 | 276 | 35.2761
5.2 | 4.8622 | 1 | 7.824 | 276 | 35.2761
5.5 | 5.0636 | 1 | 7.824 | 276 | 35.2761
6 | 5.7512 | 1 | 7.824 | 276 | 35.2761
6.6 | 6.3968 | 1 | 7.824 | 276 | 35.2761
7.8 | 7.3315 | 1 | 7.824 | 276 | 35.2761
8.5 | 7.7129 | 1 | 7.824 | 276 | 35.2761
8.3 | 7.2667 | 1 | 7.824 | 276 | 35.2761
6.8 | 6.0013 | 1 | 7.824 | 276 | 35.2761
6.1 | 5.4113 | 1 | 7.824 | 276 | 35.2761
6.2 | 5.8489 | 1 | 7.824 | 276 | 35.2761
6.8 | 6.1453 | 1 | 7.824 | 276 | 35.2761
8 | 6.3059 | 1 | 7.824 | 276 | 35.2761
7.8 | 5.2853 | 1 | 7.824 | 276 | 35.2761
6.4 | 4.7445 | 1 | 7.824 | 276 | 35.2761
5.4 | 4.0542 | 1 | 7.824 | 276 | 35.2761
5.6 | 4.1167 | 1 | 7.824 | 276 | 35.2761
5.6 | 4.2469 | 1 | 7.824 | 276 | 35.2761
5 | 3.6308 | 1 | 7.824 | 276 | 35.2761
4.7 | 3.5566 | 1 | 7.824 | 276 | 35.2761
5 | 3.9765 | 1 | 7.824 | 276 | 35.2761
5.6 | 4.7837 | 1 | 7.824 | 276 | 35.2761
4.9 | 4.1018 | 1 | 7.824 | 276 | 35.2761
4.6 | 3.8992 | 1 | 7.824 | 276 | 35.2761
5.2 | 4.394 | 1 | 7.824 | 276 | 35.2761
5.4 | 4.7269 | 1 | 7.824 | 276 | 35.2761
5.2 | 4.303 | 1 | 7.824 | 276 | 35.2761
5.5 | 4.8244 | 1 | 7.824 | 276 | 35.2761
5.7 | 4.9263 | 1 | 7.824 | 276 | 35.2761
5.7 | 4.7876 | 1 | 7.824 | 276 | 35.2761
5.9 | 5.1214 | 1 | 7.824 | 276 | 35.2761
5.5 | 4.8241 | 1 | 7.824 | 276 | 35.2761
5.7 | 4.7871 | 1 | 7.824 | 276 | 35.2761
5.5 | 4.685 | 1 | 7.824 | 276 | 35.2761
5.7 | 5.0198 | 1 | 7.824 | 276 | 35.2761
5.5 | 4.3687 | 1 | 7.824 | 276 | 35.2761
5.1 | 4.0726 | 1 | 7.824 | 276 | 35.2761
4.9 | 4.2383 | 1 | 7.824 | 276 | 35.2761
5.5 | 4.7331 | 1 | 7.824 | 276 | 35.2761
4.7 | 3.9977 | 1 | 7.824 | 276 | 35.2761
3.5 | 2.8259 | 1 | 7.824 | 276 | 35.2761
2.5 | 1.9328 | 1 | 7.824 | 276 | 35.2761
2.5 | 1.9328 | 1 | 7.824 | 276 | 35.2761
2.9 | 2.3249 | 1 | 7.824 | 276 | 35.2761
3.7 | 3.1089 | 1 | 7.824 | 276 | 35.2761
3.9 | 3.2164 | 1 | 7.824 | 276 | 35.2761
3.8 | 3.1179 | 1 | 7.824 | 276 | 35.2761
4.4 | 3.93 | 1 | 7.824 | 276 | 35.2761
5 | 4.6618 | 1 | 7.824 | 276 | 35.2761
5.9 | 5.4542 | 1 | 7.824 | 276 | 35.2761
7.6 | 7.0289 | 1 | 7.824 | 276 | 35.2761
8.2 | 7.6185 | 1 | 7.824 | 276 | 35.2761
8.6 | 7.9074 | 1 | 7.824 | 276 | 35.2761
8.9 | 8.0972 | 1 | 7.824 | 276 | 35.2761
7.2 | 6.1925 | 1 | 7.824 | 276 | 35.2761
7.6 | 6.3403 | 1 | 7.824 | 276 | 35.2761
8.2 | 6.7259 | 1 | 7.824 | 276 | 35.2761
8.1 | 6.1657 | 1 | 7.824 | 276 | 35.2761
8.4 | 6.003 | 1 | 7.824 | 276 | 35.2761
7.7 | 5.4393 | 1 | 7.824 | 276 | 35.2761
6.3 | 4.6012 | 1 | 7.824 | 276 | 35.2761
5.9 | 3.8477 | 1 | 7.824 | 276 | 35.2761
5.5 | 3.4346 | 1 | 7.824 | 276 | 35.2761
4.7 | 2.8465 | 1 | 7.824 | 276 | 35.2761
4.3 | 2.5898 | 1 | 7.824 | 276 | 35.2761
4.5 | 2.5405 | 1 | 7.824 | 276 | 35.2761
3.9 | 2.4104 | 1 | 7.824 | 276 | 35.2761
4.4 | 3.2599 | 1 | 7.824 | 276 | 35.2761
4.6 | 4.0314 | 1 | 7.824 | 276 | 35.2761
4.5 | 3.9332 | 1 | 7.824 | 276 | 35.2761
3.9 | 3.2103 | 1 | 7.824 | 276 | 35.2761
4 | 3.308 | 1 | 7.824 | 276 | 35.2761
3.1 | 2.3005 | 1 | 7.824 | 276 | 35.2761
2.9 | 2.5382 | 1 | 7.824 | 276 | 35.2761
3.5 | 3.1762 | 1 | 7.824 | 276 | 35.2761
3.4 | 3.0772 | 1 | 7.824 | 276 | 35.2761
3.8 | 3.3815 | 1 | 7.824 | 276 | 35.2761
2.6 | 2.3746 | 1 | 7.824 | 276 | 35.2761
4.3 | 3.7375 | 1 | 7.824 | 276 | 35.2761
4.4 | 3.61 | 1 | 7.824 | 276 | 35.2761
4.6 | 3.895 | 1 | 7.824 | 276 | 35.2761
4.7 | 4.1298 | 1 | 7.824 | 276 | 35.2761
4.9 | 3.9616 | 1 | 7.824 | 276 | 35.2761
4.9 | 4.0966 | 1 | 7.824 | 276 | 35.2761
4.6 | 4.0317 | 1 | 7.824 | 276 | 35.2761
4.3 | 3.8287 | 1 | 7.824 | 276 | 35.2761
3 | 2.549 | 1 | 7.824 | 276 | 35.2761
1.6 | 1.2547 | 1 | 7.824 | 276 | 35.2761
0.5 | 0.37402 | 1 | 7.824 | 276 | 35.2761
0.6 | 0.47371 | 1 | 7.824 | 276 | 35.2761
1.6 | 1.2555 | 1 | 7.824 | 276 | 35.2761
1.6 | 1.1304 | 1 | 7.824 | 276 | 35.2761
0.9 | 0.29545 | 1 | 7.824 | 276 | 35.2761
0.5 | 0.017434 | 1 | 7.824 | 276 | 35.2761
-0.2 | -0.58603 | 1 | 7.824 | 276 | 35.2761
-0.7 | -0.99551 | 1 | 7.824 | 276 | 35.2761
-0.1 | -0.3605 | 1 | 7.824 | 276 | 35.2761
0.3 | -0.17813 | 1 | 7.824 | 276 | 35.2761
0.2 | -0.27559 | 1 | 7.824 | 276 | 35.2761
0.5 | -0.065762 | 1 | 7.824 | 276 | 35.2761
0.8 | 0.10668 | 1 | 7.824 | 276 | 35.2761
1.7 | 1.1079 | 1 | 7.824 | 276 | 35.2761
2 | 1.4431 | 1 | 7.824 | 276 | 35.2761
2.6 | 1.7816 | 1 | 7.824 | 276 | 35.2761
3.2 | 2.2813 | 1 | 7.824 | 276 | 35.2761
4 | 2.9709 | 1 | 7.824 | 276 | 35.2761
4.1 | 3.1954 | 1 | 7.824 | 276 | 35.2761
4.5 | 3.3685 | 1 | 7.824 | 276 | 35.2761
3.7 | 2.8938 | 1 | 7.824 | 276 | 35.2761
3 | 2.2974 | 1 | 7.824 | 276 | 35.2761
2.5 | 1.9351 | 1 | 7.824 | 276 | 35.2761
2.6 | 2.0334 | 1 | 7.824 | 276 | 35.2761
2.7 | 2.1314 | 1 | 7.824 | 276 | 35.2761
2.4 | 1.9642 | 1 | 7.824 | 276 | 35.2761
2.6 | 2.0341 | 1 | 7.824 | 276 | 35.2761
2.4 | 2.05 | 1 | 7.824 | 276 | 35.2761
2 | 1.5291 | 1 | 7.824 | 276 | 35.2761
0.5 | 0.24792 | 1 | 7.824 | 276 | 35.2761
0.2 | -0.061261 | 1 | 7.824 | 276 | 35.2761
-0.2 | -0.45689 | 1 | 7.824 | 276 | 35.2761
-0.7 | -0.86865 | 1 | 7.824 | 276 | 35.2761
-0.9 | -1.0672 | 1 | 7.824 | 276 | 35.2761
-1.5 | -1.5819 | 1 | 7.824 | 276 | 35.2761
-1.6 | -1.6815 | 1 | 7.824 | 276 | 35.2761
-0.8 | -0.96783 | 1 | 7.824 | 276 | 35.2761
-1 | -1.1664 | 1 | 7.824 | 276 | 35.2761
1.4 | 1.0629 | 1 | 7.824 | 276 | 35.2761
1.9 | 1.3493 | 1 | 7.824 | 276 | 35.2761
2.7 | 2.133 | 1 | 7.824 | 276 | 35.2761
4.2 | 3.5143 | 1 | 7.824 | 276 | 35.2761
4.8 | 4.0111 | 1 | 7.824 | 276 | 35.2761
4.7 | 4.138 | 1 | 7.824 | 276 | 35.2761
4.2 | 3.7371 | 1 | 7.824 | 276 | 35.2761
4 | 3.6757 | 1 | 7.824 | 276 | 35.2761
4.5 | 3.9416 | 1 | 7.824 | 276 | 35.2761
5 | 4.341 | 1 | 7.824 | 276 | 35.2761
5.5 | 4.9234 | 1 | 7.824 | 276 | 35.2761
5.8 | 5.2179 | 1 | 7.824 | 276 | 35.2761
6 | 5.4616 | 1 | 7.824 | 276 | 35.2761
6 | 5.4616 | 1 | 7.824 | 276 | 35.2761
6.2 | 5.7547 | 1 | 7.824 | 276 | 35.2761
6.3 | 5.7563 | 1 | 7.824 | 276 | 35.2761
6.3 | 5.6127 | 1 | 7.824 | 276 | 35.2761
6.3 | 5.8531 | 1 | 7.824 | 276 | 35.2761
6.1 | 5.8508 | 1 | 7.824 | 276 | 35.2761
6.3 | 6.0989 | 1 | 7.824 | 276 | 35.2761
7.2 | 6.8412 | 1 | 7.824 | 276 | 35.2761
7.7 | 7.2339 | 1 | 7.824 | 276 | 35.2761
7.7 | 7.3871 | 1 | 7.824 | 276 | 35.2761
8.3 | 7.8777 | 1 | 7.824 | 276 | 35.2761
9.2 | 8.4 | 1 | 7.824 | 276 | 35.2761
9.5 | 8.385 | 1 | 7.824 | 276 | 35.2761
9.6 | 8.4814 | 1 | 7.824 | 276 | 35.2761
9 | 7.8999 | 1 | 7.824 | 276 | 35.2761
8.2 | 7.5223 | 1 | 7.824 | 276 | 35.2761
8.4 | 7.516 | 1 | 7.824 | 276 | 35.2761
8.6 | 7.3632 | 1 | 7.824 | 276 | 35.2761
8.5 | 7.364 | 1 | 7.824 | 276 | 35.2761
8.7 | 7.4584 | 1 | 7.824 | 276 | 35.2761
8.8 | 7.5543 | 1 | 7.824 | 276 | 35.2761
8.5 | 7.7125 | 1 | 7.824 | 276 | 35.2761
8.4 | 7.8192 | 1 | 7.824 | 276 | 35.2761
8.7 | 8.1662 | 1 | 7.824 | 276 | 35.2761
8.9 | 8.4688 | 1 | 7.824 | 276 | 35.2761
8.5 | 8.1788 | 1 | 7.824 | 276 | 35.2761
8 | 7.5279 | 1 | 7.824 | 276 | 35.2761
7.5 | 7.395 | 1 | 7.824 | 276 | 35.2761
7.5 | 7.0346 | 1 | 7.824 | 276 | 35.2761
7.5 | 7.1875 | 1 | 7.824 | 276 | 35.2761
7 | 6.6415 | 1 | 7.824 | 276 | 35.2761
7 | 6.6415 | 1 | 7.824 | 276 | 35.2761
7 | 6.5411 | 1 | 7.824 | 276 | 35.2761
7.5 | 6.8336 | 1 | 7.824 | 276 | 35.2761
7.2 | 6.7386 | 1 | 7.824 | 276 | 35.2761
7.3 | 6.8373 | 1 | 7.824 | 276 | 35.2761
7.9 | 7.2259 | 1 | 7.824 | 276 | 35.2761
8 | 7.4254 | 1 | 7.824 | 276 | 35.2761
8.4 | 7.7162 | 1 | 7.824 | 276 | 35.2761
8.6 | 7.8099 | 1 | 7.824 | 276 | 35.2761
9.5 | 8.3802 | 1 | 7.824 | 276 | 35.2761
9.1 | 8.0938 | 1 | 7.824 | 276 | 35.2761
9 | 7.8957 | 1 | 7.824 | 276 | 35.2761
8.3 | 7.6185 | 1 | 7.824 | 276 | 35.2761
8.5 | 7.3629 | 1 | 7.824 | 276 | 35.2761
8.5 | 7.1678 | 1 | 7.824 | 276 | 35.2761
8.4 | 7.1691 | 1 | 7.824 | 276 | 35.2761
7.6 | 6.5891 | 1 | 7.824 | 276 | 35.2761
7.2 | 6.2974 | 1 | 7.824 | 276 | 35.2761
6.7 | 5.9061 | 1 | 7.824 | 276 | 35.2761
6.6 | 5.8085 | 1 | 7.824 | 276 | 35.2761
5.7 | 5.0237 | 1 | 7.824 | 276 | 35.2761
5.8 | 5.2158 | 1 | 7.824 | 276 | 35.2761
6 | 5.4602 | 1 | 7.824 | 276 | 35.2761
5.3 | 4.9608 | 1 | 7.824 | 276 | 35.2761
5.3 | 4.9609 | 1 | 7.824 | 276 | 35.2761
6 | 5.4607 | 1 | 7.824 | 276 | 35.2761
6.1 | 5.7526 | 1 | 7.824 | 276 | 35.2761
6.8 | 6.3459 | 1 | 7.824 | 276 | 35.2761
7.6 | 6.9346 | 1 | 7.824 | 276 | 35.2761
8.8 | 7.7066 | 1 | 7.824 | 276 | 35.2761
9.1 | 7.6517 | 1 | 7.824 | 276 | 35.2761
10.4 | 8.5004 | 1 | 7.824 | 276 | 35.2761
10.1 | 7.9761 | 1 | 7.824 | 276 | 35.2761
9.6 | 7.3664 | 1 | 7.824 | 276 | 35.2761
8.5 | 7.2667 | 1 | 7.824 | 276 | 35.2761
8.1 | 7.4236 | 1 | 7.824 | 276 | 35.2761
8.6 | 7.8118 | 1 | 7.824 | 276 | 35.2761
8.4 | 7.516 | 1 | 7.824 | 276 | 35.2761
8.3 | 7.2702 | 1 | 7.824 | 276 | 35.2761
8.2 | 7.3219 | 1 | 7.824 | 276 | 35.2761
7.6 | 6.6884 | 1 | 7.824 | 276 | 35.2761
7.1 | 5.8728 | 1 | 7.824 | 276 | 35.2761
7.3 | 6.159 | 1 | 7.824 | 276 | 35.2761
7.5 | 6.4001 | 1 | 7.824 | 276 | 35.2761
7.8 | 7.0315 | 1 | 7.824 | 276 | 35.2761
8.2 | 7.4226 | 1 | 7.824 | 276 | 35.2761
8.3 | 7.6211 | 1 | 7.824 | 276 | 35.2761
9 | 8.2041 | 1 | 7.824 | 276 | 35.2761
9.4 | 8.4918 | 1 | 7.824 | 276 | 35.2761
9.5 | 8.5889 | 1 | 7.824 | 276 | 35.2761
9.3 | 8.4967 | 1 | 7.824 | 276 | 35.2761
9.4 | 8.8571 | 1 | 7.824 | 276 | 35.2761
9.6 | 9.0539 | 1 | 7.824 | 276 | 35.2761
10.4 | 9.9521 | 1 | 7.824 | 276 | 35.2761
11.9 | 11.1515 | 1 | 7.824 | 276 | 35.2761
12.6 | 11.7245 | 1 | 7.824 | 276 | 35.2761
12.5 | 11.4022 | 1 | 7.824 | 276 | 35.2761
12.4 | 11.4159 | 1 | 7.824 | 276 | 35.2761
12.3 | 11.4301 | 1 | 7.824 | 276 | 35.2761
12.1 | 11.4606 | 1 | 7.824 | 276 | 35.2761
12.5 | 11.1806 | 1 | 7.824 | 276 | 35.2761
12.3 | 10.6108 | 1 | 7.824 | 276 | 35.2761
10.6 | 10.2608 | 1 | 7.824 | 276 | 35.2761
10.1 | 9.1197 | 1 | 7.824 | 276 | 35.2761
10.1 | 8.3091 | 1 | 7.824 | 276 | 35.2761
9.8 | 7.8805 | 1 | 7.824 | 276 | 35.2761
10 | 7.3294 | 1 | 7.824 | 276 | 35.2761
9.3 | 6.7274 | 1 | 7.824 | 276 | 35.2761
8.5 | 6.2494 | 1 | 7.824 | 276 | 35.2761
8 | 5.8724 | 1 | 7.824 | 276 | 35.2761
7.9 | 5.7799 | 1 | 7.824 | 276 | 35.2761
7.7 | 5.6806 | 1 | 7.824 | 276 | 35.2761
8.3 | 6.2887 | 1 | 7.824 | 276 | 35.2761
9 | 6.8556 | 1 | 7.824 | 276 | 35.2761
9 | 6.7668 | 1 | 7.824 | 276 | 35.2761
9.3 | 7.0481 | 1 | 7.824 | 276 | 35.2761
9.9 | 7.3364 | 1 | 7.824 | 276 | 35.2761
10.6 | 7.583 | 1 | 7.824 | 276 | 35.2761
10.8 | 7.5909 | 1 | 7.824 | 276 | 35.2761
11 | 7.6428 | 1 | 7.824 | 276 | 35.2761
11.4 | 7.9607 | 1 | 7.824 | 276 | 35.2761
11.1 | 7.5187 | 1 | 7.824 | 276 | 35.2761
10.4 | 7.6192 | 1 | 7.824 | 276 | 35.2761
7.1 | 6.2046 | 1 | 7.824 | 276 | 35.2761
7.4 | 5.8437 | 1 | 7.824 | 276 | 35.2761
7.6 | 5.4633 | 1 | 7.824 | 276 | 35.2761
7.4 | 5.1507 | 1 | 7.824 | 276 | 35.2761
6.9 | 4.8937 | 1 | 7.824 | 276 | 35.2761
6.9 | 5.1072 | 1 | 7.824 | 276 | 35.2761
6.4 | 4.5934 | 1 | 7.824 | 276 | 35.2761
6.1 | 4.3946 | 1 | 7.824 | 276 | 35.2761
6.2 | 4.6166 | 1 | 7.824 | 276 | 35.2761
6.3 | 4.4992 | 1 | 7.824 | 276 | 35.2761
6.3 | 4.6268 | 1 | 7.824 | 276 | 35.2761
6.1 | 4.3955 | 1 | 7.824 | 276 | 35.2761
5.7 | 4.2276 | 1 | 7.824 | 276 | 35.2761
5.9 | 4.2066 | 1 | 7.824 | 276 | 35.2761
6.1 | 4.3118 | 1 | 7.824 | 276 | 35.2761
6 | 4.301 | 1 | 7.824 | 276 | 35.2761
6.1 | 4.3128 | 1 | 7.824 | 276 | 35.2761
6.7 | 4.6681 | 1 | 7.824 | 276 | 35.2761
7.6 | 5.1331 | 1 | 7.824 | 276 | 35.2761
8.4 | 5.6222 | 1 | 7.824 | 276 | 35.2761
8.9 | 5.6744 | 1 | 7.824 | 276 | 35.2761
8.3 | 5.3701 | 1 | 7.824 | 276 | 35.2761
8.8 | 5.9053 | 1 | 7.824 | 276 | 35.2761
8.1 | 5.4293 | 1 | 7.824 | 276 | 35.2761
7.5 | 5.0422 | 1 | 7.824 | 276 | 35.2761
7.5 | 5.2482 | 1 | 7.824 | 276 | 35.2761
6.8 | 4.7636 | 1 | 7.824 | 276 | 35.2761
6.5 | 4.6075 | 1 | 7.824 | 276 | 35.2761
6.5 | 4.6913 | 1 | 7.824 | 276 | 35.2761
5.9 | 4.3352 | 1 | 7.824 | 276 | 35.2761
4.9 | 3.7625 | 1 | 7.824 | 276 | 35.2761
4.2 | 3.4296 | 1 | 7.824 | 276 | 35.2761
3.8 | 2.9972 | 1 | 7.824 | 276 | 35.2761
2.7 | 2.1349 | 1 | 7.824 | 276 | 35.2761
3.2 | 2.6246 | 1 | 7.824 | 276 | 35.2761
3.4 | 2.9508 | 1 | 7.824 | 276 | 35.2761
2.8 | 2.4462 | 1 | 7.824 | 276 | 35.2761
3.6 | 3.3709 | 1 | 7.824 | 276 | 35.2761
4.6 | 4.3632 | 1 | 7.824 | 276 | 35.2761
5.6 | 5.164 | 1 | 7.824 | 276 | 35.2761
5.7 | 5.3581 | 1 | 7.824 | 276 | 35.2761
6.1 | 5.561 | 1 | 7.824 | 276 | 35.2761
6.6 | 6.0524 | 1 | 7.824 | 276 | 35.2761
7.2 | 6.6425 | 1 | 7.824 | 276 | 35.2761
7.5 | 6.8379 | 1 | 7.824 | 276 | 35.2761
7.4 | 6.5925 | 1 | 7.824 | 276 | 35.2761
6.8 | 6.0069 | 1 | 7.824 | 276 | 35.2761
6.4 | 5.8552 | 1 | 7.824 | 276 | 35.2761
6.2 | 5.7549 | 1 | 7.824 | 276 | 35.2761
6.2 | 5.6585 | 1 | 7.824 | 276 | 35.2761
6.3 | 5.7568 | 1 | 7.824 | 276 | 35.2761
6.2 | 5.5155 | 1 | 7.824 | 276 | 35.2761
6 | 5.1802 | 1 | 7.824 | 276 | 35.2761
5.8 | 4.8937 | 1 | 7.824 | 276 | 35.2761
5.7 | 4.9339 | 1 | 7.824 | 276 | 35.2761
5.5 | 4.8311 | 1 | 7.824 | 276 | 35.2761
5.4 | 4.596 | 1 | 7.824 | 276 | 35.2761
4.9 | 4.2439 | 1 | 7.824 | 276 | 35.2761
4.8 | 4.237 | 1 | 7.824 | 276 | 35.2761
4.5 | 3.3746 | 1 | 7.824 | 276 | 35.2761
3.5 | 2.8315 | 1 | 7.824 | 276 | 35.2761
3.4 | 2.4816 | 1 | 7.824 | 276 | 35.2761
2.8 | 2.1065 | 1 | 7.824 | 276 | 35.2761
2.4 | 1.7167 | 1 | 7.824 | 276 | 35.2761
2.6 | 1.7894 | 1 | 7.824 | 276 | 35.2761
3.5 | 2.3756 | 1 | 7.824 | 276 | 35.2761
3.9 | 2.7598 | 1 | 7.824 | 276 | 35.2761
4.4 | 2.8339 | 1 | 7.824 | 276 | 35.2761
4.9 | 2.9905 | 1 | 7.824 | 276 | 35.2761
5 | 2.9683 | 1 | 7.824 | 276 | 35.2761
5 | 2.7272 | 1 | 7.824 | 276 | 35.2761
4.5 | 2.5793 | 1 | 7.824 | 276 | 35.2761
4 | 2.3014 | 1 | 7.824 | 276 | 35.2761
3.3 | 1.8225 | 1 | 7.824 | 276 | 35.2761
2.5 | 1.3672 | 1 | 7.824 | 276 | 35.2761
1.8 | 0.74653 | 1 | 7.824 | 276 | 35.2761
1.4 | 0.17659 | 1 | 7.824 | 276 | 35.2761
0.8 | -0.28664 | 1 | 7.824 | 276 | 35.2761
0.9 | -0.19066 | 1 | 7.824 | 276 | 35.2761
1.7 | 0.51942 | 1 | 7.824 | 276 | 35.2761
1.2 | 0.10008 | 1 | 7.824 | 276 | 35.2761
1.5 | 0.035267 | 1 | 7.824 | 276 | 35.2761
1.5 | 0.036128 | 1 | 7.824 | 276 | 35.2761
2 | 0.33185 | 1 | 7.824 | 276 | 35.2761
2.3 | 0.6275 | 1 | 7.824 | 276 | 35.2761
2.6 | 1.2126 | 1 | 7.824 | 276 | 35.2761
2.6 | 1.2134 | 1 | 7.824 | 276 | 35.2761
2.5 | 1.2422 | 1 | 7.824 | 276 | 35.2761
2.7 | 1.5745 | 1 | 7.824 | 276 | 35.2761
2.8 | 1.5885 | 1 | 7.824 | 276 | 35.2761
3.1 | 1.6314 | 1 | 7.824 | 276 | 35.2761
3.5 | 1.775 | 1 | 7.824 | 276 | 35.2761
4 | 1.9364 | 1 | 7.824 | 276 | 35.2761
4.4 | 2.2436 | 1 | 7.824 | 276 | 35.2761
4 | 1.8157 | 1 | 7.824 | 276 | 35.2761
3.5 | 1.653 | 1 | 7.824 | 276 | 35.2761
2.6 | 1.094 | 1 | 7.824 | 276 | 35.2761
1.5 | 0.16455 | 1 | 7.824 | 276 | 35.2761
0.4 | -0.80853 | 1 | 7.824 | 276 | 35.2761
0.7 | -0.14088 | 1 | 7.824 | 276 | 35.2761
-0.3 | -0.67482 | 1 | 7.824 | 276 | 35.2761
-2.1 | -2.9104 | 1 | 7.824 | 276 | 35.2761
-1 | -1.9954 | 1 | 7.824 | 276 | 35.2761
-0.6 | -1.5777 | 1 | 7.824 | 276 | 35.2761
-1.3 | -2.0335 | 1 | 7.824 | 276 | 35.2761
-0.6 | -1.5783 | 1 | 7.824 | 276 | 35.2761
-0.2 | -1.1591 | 1 | 7.824 | 276 | 35.2761
0 | -0.93015 | 1 | 7.824 | 276 | 35.2761
0.8 | -0.085009 | 1 | 7.824 | 276 | 35.2761
1 | -0.35289 | 1 | 7.824 | 276 | 35.2761
1.9 | -0.1604 | 1 | 7.824 | 276 | 35.2761
2.5 | 0.71299 | 1 | 7.824 | 276 | 35.2761
3.9 | 1.719 | 1 | 7.824 | 276 | 35.2761
4.5 | 2.3407 | 1 | 7.824 | 276 | 35.2761
5.6 | 3.1558 | 1 | 7.824 | 276 | 35.2761
5.8 | 3.6854 | 1 | 7.824 | 276 | 35.2761
6.6 | 4.4674 | 1 | 7.824 | 276 | 35.2761
7.2 | 4.8611 | 1 | 7.824 | 276 | 35.2761
7.4 | 5.1679 | 1 | 7.824 | 276 | 35.2761
7.5 | 5.2596 | 1 | 7.824 | 276 | 35.2761
7.5 | 5.3851 | 1 | 7.824 | 276 | 35.2761
7.6 | 5.6061 | 1 | 7.824 | 276 | 35.2761
8 | 5.7653 | 1 | 7.824 | 276 | 35.2761
8.1 | 6.1177 | 1 | 7.824 | 276 | 35.2761
7.7 | 6.3683 | 1 | 7.824 | 276 | 35.2761
7.5 | 6.7446 | 1 | 7.824 | 276 | 35.2761
7.5 | 6.842 | 1 | 7.824 | 276 | 35.2761
7.7 | 7.0382 | 1 | 7.824 | 276 | 35.2761
7.5 | 7.1916 | 1 | 7.824 | 276 | 35.2761
7.7 | 7.1375 | 1 | 7.824 | 276 | 35.2761
7 | 6.5472 | 1 | 7.824 | 276 | 35.2761
6.9 | 6.3504 | 1 | 7.824 | 276 | 35.2761
5.9 | 5.4619 | 1 | 7.824 | 276 | 35.2761
6.4 | 5.3907 | 1 | 7.824 | 276 | 35.2761
5.9 | 4.7731 | 1 | 7.824 | 276 | 35.2761
5.4 | 4.0762 | 1 | 7.824 | 276 | 35.2761
4.5 | 3.3825 | 1 | 7.824 | 276 | 35.2761
4.5 | 3.2582 | 1 | 7.824 | 276 | 35.2761
4.6 | 3.2715 | 1 | 7.824 | 276 | 35.2761
6.3 | 4.1861 | 1 | 7.824 | 276 | 35.2761
7.2 | 4.1638 | 1 | 7.824 | 276 | 35.2761
7.5 | 4.1319 | 1 | 7.824 | 276 | 35.2761
6.9 | 3.8952 | 1 | 7.824 | 276 | 35.2761
6.2 | 3.9747 | 1 | 7.824 | 276 | 35.2761
4.5 | 3.0558 | 1 | 7.824 | 276 | 35.2761
4.2 | 2.8507 | 1 | 7.824 | 276 | 35.2761
2.8 | 2.0298 | 1 | 7.824 | 276 | 35.2761
2.2 | 1.6489 | 1 | 7.824 | 276 | 35.2761
2.1 | 1.4294 | 1 | 7.824 | 276 | 35.2761
1.3 | 0.58885 | 1 | 7.824 | 276 | 35.2761
-0.2 | -1.049 | 1 | 7.824 | 276 | 35.2761
-0.4 | -1.012 | 1 | 7.824 | 276 | 35.2761
0.3 | -0.16826 | 1 | 7.824 | 276 | 35.2761
0.6 | 0.0014137 | 1 | 7.824 | 276 | 35.2761
1.1 | 0.0046775 | 1 | 7.824 | 276 | 35.2761
1.5 | 0.70602 | 1 | 7.824 | 276 | 35.2761
1.6 | 0.94103 | 1 | 7.824 | 276 | 35.2761
2 | 1.4529 | 1 | 7.824 | 276 | 35.2761
2.6 | 1.9172 | 1 | 7.824 | 276 | 35.2761
3.5 | 2.5865 | 1 | 7.824 | 276 | 35.2761
4.5 | 3.5974 | 1 | 7.824 | 276 | 35.2761
5.2 | 4.1886 | 1 | 7.824 | 276 | 35.2761
6.4 | 5.3948 | 1 | 7.824 | 276 | 35.2761
6.8 | 5.7821 | 1 | 7.824 | 276 | 35.2761
7.7 | 6.6059 | 1 | 7.824 | 276 | 35.2761
8.9 | 7.3341 | 1 | 7.824 | 276 | 35.2761
9.4 | 7.7636 | 1 | 7.824 | 276 | 35.2761
8 | 6.8961 | 1 | 7.824 | 276 | 35.2761
7.5 | 6.5074 | 1 | 7.824 | 276 | 35.2761
8.7 | 7.3806 | 1 | 7.824 | 276 | 35.2761
7.6 | 6.8452 | 1 | 7.824 | 276 | 35.2761
7.2 | 6.6482 | 1 | 7.824 | 276 | 35.2761
7.6 | 6.9426 | 1 | 7.824 | 276 | 35.2761
7.3 | 6.7465 | 1 | 7.824 | 276 | 35.2761
6.1 | 5.7571 | 1 | 7.824 | 276 | 35.2761
6.5 | 6.3003 | 1 | 7.824 | 276 | 35.2761
5.9 | 5.6555 | 1 | 7.824 | 276 | 35.2761
7 | 6.8982 | 1 | 7.824 | 276 | 35.2761
7.1 | 6.9979 | 1 | 7.824 | 276 | 35.2761
7.3 | 6.9444 | 1 | 7.824 | 276 | 35.2761
7.5 | 7.1926 | 1 | 7.824 | 276 | 35.2761
7.7 | 7.2393 | 1 | 7.824 | 276 | 35.2761
6.5 | 5.9592 | 1 | 7.824 | 276 | 35.2761
6.1 | 5.6133 | 1 | 7.824 | 276 | 35.2761
6.7 | 5.9179 | 1 | 7.824 | 276 | 35.2761
7.1 | 6.3083 | 1 | 7.824 | 276 | 35.2761
7.8 | 6.8459 | 1 | 7.824 | 276 | 35.2761
6.7 | 5.9176 | 1 | 7.824 | 276 | 35.2761
8.4 | 6.9502 | 1 | 7.824 | 276 | 35.2761
8.7 | 7.3799 | 1 | 7.824 | 276 | 35.2761
9.5 | 7.8581 | 1 | 7.824 | 276 | 35.2761
9.5 | 7.8581 | 1 | 7.824 | 276 | 35.2761
9.2 | 7.8601 | 1 | 7.824 | 276 | 35.2761
9 | 7.7655 | 1 | 7.824 | 276 | 35.2761
9.3 | 8.1042 | 1 | 7.824 | 276 | 35.2761
9.4 | 8.2008 | 1 | 7.824 | 276 | 35.2761
9.3 | 8.3037 | 1 | 7.824 | 276 | 35.2761
9 | 8.3153 | 1 | 7.824 | 276 | 35.2761
9.1 | 8.3111 | 1 | 7.824 | 276 | 35.2761
9.2 | 8.4089 | 1 | 7.824 | 276 | 35.2761
8.9 | 8.4753 | 1 | 7.824 | 276 | 35.2761
9.1 | 8.5684 | 1 | 7.824 | 276 | 35.2761
9.5 | 8.8578 | 1 | 7.824 | 276 | 35.2761
9.6 | 8.956 | 1 | 7.824 | 276 | 35.2761
9.6 | 8.8518 | 1 | 7.824 | 276 | 35.2761
9.6 | 8.9557 | 1 | 7.824 | 276 | 35.2761
9.8 | 8.9439 | 1 | 7.824 | 276 | 35.2761
9.9 | 9.0415 | 1 | 7.824 | 276 | 35.2761
10.1 | 9.4476 | 1 | 7.824 | 276 | 35.2761
10.6 | 9.7256 | 1 | 7.824 | 276 | 35.2761
11 | 9.9044 | 1 | 7.824 | 276 | 35.2761
10.5 | 9.7338 | 1 | 7.824 | 276 | 35.2761
10.6 | 9.9388 | 1 | 7.824 | 276 | 35.2761
10.3 | 9.0711 | 1 | 7.824 | 276 | 35.2761
10.9 | 9.3439 | 1 | 7.824 | 276 | 35.2761
10.1 | 8.0967 | 1 | 7.824 | 276 | 35.2761
7.8 | 6.3767 | 1 | 7.824 | 276 | 35.2761
7.5 | 6.181 | 1 | 7.824 | 276 | 35.2761
7.9 | 6.2458 | 1 | 7.824 | 276 | 35.2761
7.1 | 5.5294 | 1 | 7.824 | 276 | 35.2761
7 | 5.5661 | 1 | 7.824 | 276 | 35.2761
7.1 | 5.6616 | 1 | 7.824 | 276 | 35.2761
7.1 | 5.527 | 1 | 7.824 | 276 | 35.2761
7.7 | 6.4633 | 1 | 7.824 | 276 | 35.2761
9.4 | 8.5002 | 1 | 7.824 | 276 | 35.2761
10.6 | 9.6173 | 1 | 7.824 | 276 | 35.2761
10.9 | 9.9091 | 1 | 7.824 | 276 | 35.2761
11.1 | 9.9972 | 1 | 7.824 | 276 | 35.2761
11.5 | 10.1729 | 1 | 7.824 | 276 | 35.2761
11.7 | 10.1561 | 1 | 7.824 | 276 | 35.2761
11 | 10.1125 | 1 | 7.824 | 276 | 35.2761
10.6 | 9.9362 | 1 | 7.824 | 276 | 35.2761
10.4 | 9.8475 | 1 | 7.824 | 276 | 35.2761
10.6 | 9.8291 | 1 | 7.824 | 276 | 35.2761
11.1 | 9.5823 | 1 | 7.824 | 276 | 35.2761
11.1 | 9.3295 | 1 | 7.824 | 276 | 35.2761
11.1 | 9.2308 | 1 | 7.824 | 276 | 35.2761
11 | 7.665 | 1 | 7.824 | 276 | 35.2761
10.4 | 6.5217 | 1 | 7.824 | 276 | 35.2761
9.5 | 6.0751 | 1 | 7.824 | 276 | 35.2761
7.9 | 4.7963 | 1 | 7.824 | 276 | 35.2761
7.1 | 4.0786 | 1 | 7.824 | 276 | 35.2761
5.6 | 3.3454 | 1 | 7.824 | 276 | 35.2761
4.8 | 3.0234 | 1 | 7.824 | 276 | 35.2761
3.7 | 2.3355 | 1 | 7.824 | 276 | 35.2761
4.2 | 2.8522 | 1 | 7.824 | 276 | 35.2761
3.8 | 2.5504 | 1 | 7.824 | 276 | 35.2761
4.1 | 2.637 | 1 | 7.824 | 276 | 35.2761
3.9 | 2.5647 | 1 | 7.824 | 276 | 35.2761
4.1 | 2.8764 | 1 | 7.824 | 276 | 35.2761
4.5 | 3.3837 | 1 | 7.824 | 276 | 35.2761
4.3 | 3.5307 | 1 | 7.824 | 276 | 35.2761
4.1 | 3.7776 | 1 | 7.824 | 276 | 35.2761
4 | 3.7692 | 1 | 7.824 | 276 | 35.2761
4 | 3.7691 | 1 | 7.824 | 276 | 35.2761
4.4 | 4.0739 | 1 | 7.824 | 276 | 35.2761
4.4 | 4.1659 | 1 | 7.824 | 276 | 35.2761
4.6 | 4.3643 | 1 | 7.824 | 276 | 35.2761
5 | 4.6673 | 1 | 7.824 | 276 | 35.2761
5.2 | 4.9596 | 1 | 7.824 | 276 | 35.2761
5.4 | 5.1579 | 1 | 7.824 | 276 | 35.2761
5.9 | 5.6541 | 1 | 7.824 | 276 | 35.2761
6.3 | 5.9529 | 1 | 7.824 | 276 | 35.2761
6.5 | 6.2991 | 1 | 7.824 | 276 | 35.2761
7.6 | 7.1886 | 1 | 7.824 | 276 | 35.2761
7.9 | 7.6907 | 1 | 7.824 | 276 | 35.2761
8.9 | 8.5785 | 1 | 7.824 | 276 | 35.2761
9.8 | 9.3626 | 1 | 7.824 | 276 | 35.2761
9.9 | 9.4614 | 1 | 7.824 | 276 | 35.2761
10.1 | 9.6591 | 1 | 7.824 | 276 | 35.2761
10 | 9.4526 | 1 | 7.824 | 276 | 35.2761
10.1 | 9.5511 | 1 | 7.824 | 276 | 35.2761
10.1 | 9.5509 | 1 | 7.824 | 276 | 35.2761
10.1 | 9.6587 | 1 | 7.824 | 276 | 35.2761
10.5 | 9.9448 | 1 | 7.824 | 276 | 35.2761
10.5 | 9.7287 | 1 | 7.824 | 276 | 35.2761
11 | 10.003 | 1 | 7.824 | 276 | 35.2761
11.4 | 10.178 | 1 | 7.824 | 276 | 35.2761
10.9 | 10.3383 | 1 | 7.824 | 276 | 35.2761
11 | 10.1098 | 1 | 7.824 | 276 | 35.2761
11 | 10.0025 | 1 | 7.824 | 276 | 35.2761
10.7 | 9.5007 | 1 | 7.824 | 276 | 35.2761
11.4 | 9.968 | 1 | 7.824 | 276 | 35.2761
11.5 | 9.8567 | 1 | 7.824 | 276 | 35.2761
12.2 | 9.3289 | 1 | 7.824 | 276 | 35.2761
11.1 | 8.0884 | 1 | 7.824 | 276 | 35.2761
10.8 | 7.6808 | 1 | 7.824 | 276 | 35.2761
10 | 6.8668 | 1 | 7.824 | 276 | 35.2761
9.7 | 7.0203 | 1 | 7.824 | 276 | 35.2761
9.7 | 6.8028 | 1 | 7.824 | 276 | 35.2761
8.7 | 7.1282 | 1 | 7.824 | 276 | 35.2761
7.6 | 6.0781 | 1 | 7.824 | 276 | 35.2761
6.6 | 5.1245 | 1 | 7.824 | 276 | 35.2761
6.8 | 5.2267 | 1 | 7.824 | 276 | 35.2761
6.4 | 4.9345 | 1 | 7.824 | 276 | 35.2761
5.8 | 3.9835 | 1 | 7.824 | 276 | 35.2761
6.9 | 4.5193 | 1 | 7.824 | 276 | 35.2761
5.5 | 3.8234 | 1 | 7.824 | 276 | 35.2761
7.5 | 3.9785 | 1 | 7.824 | 276 | 35.2761
7.2 | 3.7848 | 1 | 7.824 | 276 | 35.2761
6.2 | 3.2525 | 1 | 7.824 | 276 | 35.2761
5.8 | 3.2013 | 1 | 7.824 | 276 | 35.2761
6 | 3.2712 | 1 | 7.824 | 276 | 35.2761
6.3 | 3.3551 | 1 | 7.824 | 276 | 35.2761
6.8 | 3.6282 | 1 | 7.824 | 276 | 35.2761
7.7 | 4.3485 | 1 | 7.824 | 276 | 35.2761
8.7 | 5.1296 | 1 | 7.824 | 276 | 35.2761
9.3 | 5.2945 | 1 | 7.824 | 276 | 35.2761
9.5 | 5.3613 | 1 | 7.824 | 276 | 35.2761
9.4 | 5.601 | 1 | 7.824 | 276 | 35.2761
9.4 | 5.8274 | 1 | 7.824 | 276 | 35.2761
9.1 | 6.193 | 1 | 7.824 | 276 | 35.2761
8.8 | 6.1258 | 1 | 7.824 | 276 | 35.2761
9.2 | 6.324 | 1 | 7.824 | 276 | 35.2761
9.2 | 6.6626 | 1 | 7.824 | 276 | 35.2761
9.2 | 6.6613 | 1 | 7.824 | 276 | 35.2761
9.3 | 6.7525 | 1 | 7.824 | 276 | 35.2761
9.3 | 6.7525 | 1 | 7.824 | 276 | 35.2761
9.1 | 6.8732 | 1 | 7.824 | 276 | 35.2761
9.2 | 6.8765 | 1 | 7.824 | 276 | 35.2761
9.2 | 6.7433 | 1 | 7.824 | 276 | 35.2761
8.7 | 6.4537 | 1 | 7.824 | 276 | 35.2761
9.1 | 6.6495 | 1 | 7.824 | 276 | 35.2761
9.4 | 7.2853 | 1 | 7.824 | 276 | 35.2761
9.8 | 7.7997 | 1 | 7.824 | 276 | 35.2761
10.3 | 8.319 | 1 | 7.824 | 276 | 35.2761
10.7 | 8.696 | 1 | 7.824 | 276 | 35.2761
10.5 | 8.8501 | 1 | 7.824 | 276 | 35.2761
10.3 | 9.0616 | 1 | 7.824 | 276 | 35.2761
10 | 9.3443 | 1 | 7.824 | 276 | 35.2761
10.9 | 9.5889 | 1 | 7.824 | 276 | 35.2761
10.3 | 9.6388 | 1 | 7.824 | 276 | 35.2761
10.8 | 8.5944 | 1 | 7.824 | 276 | 35.2761
10.7 | 8.5955 | 1 | 7.824 | 276 | 35.2761
11 | 10.2165 | 1 | 7.824 | 276 | 35.2761
10.5 | 7.3586 | 1 | 7.824 | 276 | 35.2761
10.2 | 6.9559 | 1 | 7.824 | 276 | 35.2761
10.2 | 7.1659 | 1 | 7.824 | 276 | 35.2761
8.4 | 7.1715 | 1 | 7.824 | 276 | 35.2761
5.4 | 4.2807 | 1 | 7.824 | 276 | 35.2761
5.6 | 3.7945 | 1 | 7.824 | 276 | 35.2761
4.6 | 2.7782 | 1 | 7.824 | 276 | 35.2761
5 | 3.0756 | 1 | 7.824 | 276 | 35.2761
4.5 | 1.7996 | 1 | 7.824 | 276 | 35.2761
5 | 2.4751 | 1 | 7.824 | 276 | 35.2761
5.3 | 3.2839 | 1 | 7.824 | 276 | 35.2761
5.3 | 3.1703 | 1 | 7.824 | 276 | 35.2761
5.5 | 3.1301 | 1 | 7.824 | 276 | 35.2761
5.6 | 2.47 | 1 | 7.824 | 276 | 35.2761
5 | 2.2141 | 1 | 7.824 | 276 | 35.2761
4.3 | 2.2642 | 1 | 7.824 | 276 | 35.2761
4.5 | 1.937 | 1 | 7.824 | 276 | 35.2761
4.2 | 2.0055 | 1 | 7.824 | 276 | 35.2761
5.6 | 2.8687 | 1 | 7.824 | 276 | 35.2761
7.1 | 3.5728 | 1 | 7.824 | 276 | 35.2761
7.4 | 3.5496 | 1 | 7.824 | 276 | 35.2761
7.6 | 3.2366 | 1 | 7.824 | 276 | 35.2761
7.8 | 2.9562 | 1 | 7.824 | 276 | 35.2761
7.5 | 2.4039 | 1 | 7.824 | 276 | 35.2761
7.1 | 2.4771 | 1 | 7.824 | 276 | 35.2761
6.2 | 2.2609 | 1 | 7.824 | 276 | 35.2761
5.2 | 1.565 | 1 | 7.824 | 276 | 35.2761
4.3 | 1.645 | 1 | 7.824 | 276 | 35.2761
4 | 1.5498 | 1 | 7.824 | 276 | 35.2761
3.3 | 1.1857 | 1 | 7.824 | 276 | 35.2761
2.6 | 0.85634 | 1 | 7.824 | 276 | 35.2761
2.5 | 0.71912 | 1 | 7.824 | 276 | 35.2761
1.4 | 0.18866 | 1 | 7.824 | 276 | 35.2761
2 | 0.83165 | 1 | 7.824 | 276 | 35.2761
2.4 | 0.89997 | 1 | 7.824 | 276 | 35.2761
2.6 | 1.2228 | 1 | 7.824 | 276 | 35.2761
2.7 | 1.8159 | 1 | 7.824 | 276 | 35.2761
3.3 | 2.5196 | 1 | 7.824 | 276 | 35.2761
3.6 | 2.9375 | 1 | 7.824 | 276 | 35.2761
4.1 | 3.7793 | 1 | 7.824 | 276 | 35.2761
4.9 | 4.5706 | 1 | 7.824 | 276 | 35.2761
5.9 | 5.5599 | 1 | 7.824 | 276 | 35.2761
7.5 | 7.1933 | 1 | 7.824 | 276 | 35.2761
8.8 | 8.2741 | 1 | 7.824 | 276 | 35.2761
10 | 9.0374 | 1 | 7.824 | 276 | 35.2761
10.1 | 9.238 | 1 | 7.824 | 276 | 35.2761
10.5 | 9.4193 | 1 | 7.824 | 276 | 35.2761
10.7 | 9.407 | 1 | 7.824 | 276 | 35.2761
10.4 | 8.9654 | 1 | 7.824 | 276 | 35.2761
10.1 | 8.7771 | 1 | 7.824 | 276 | 35.2761
9.9 | 8.5844 | 1 | 7.824 | 276 | 35.2761
9.5 | 8.2974 | 1 | 7.824 | 276 | 35.2761
9.1 | 7.911 | 1 | 7.824 | 276 | 35.2761
9.3 | 7.7636 | 1 | 7.824 | 276 | 35.2761
9.3 | 7.8591 | 1 | 7.824 | 276 | 35.2761
9.2 | 8.0065 | 1 | 7.824 | 276 | 35.2761
9.5 | 7.9533 | 1 | 7.824 | 276 | 35.2761
9.6 | 7.9518 | 1 | 7.824 | 276 | 35.2761
9 | 7.5695 | 1 | 7.824 | 276 | 35.2761
9.3 | 7.8571 | 1 | 7.824 | 276 | 35.2761
9.3 | 7.7607 | 1 | 7.824 | 276 | 35.2761
9.2 | 7.8576 | 1 | 7.824 | 276 | 35.2761
9.1 | 8.0071 | 1 | 7.824 | 276 | 35.2761
8.6 | 8.0233 | 1 | 7.824 | 276 | 35.2761
8.6 | 7.9217 | 1 | 7.824 | 276 | 35.2761
8 | 7.3333 | 1 | 7.824 | 276 | 35.2761
8.7 | 7.4744 | 1 | 7.824 | 276 | 35.2761
9.3 | 5.9746 | 1 | 7.824 | 276 | 35.2761
9.9 | 5.6767 | 1 | 7.824 | 276 | 35.2761
9.5 | 5.0285 | 1 | 7.824 | 276 | 35.2761
9.5 | 5.1417 | 1 | 7.824 | 276 | 35.2761
9.4 | 4.7888 | 1 | 7.824 | 276 | 35.2761
9 | 5.0033 | 1 | 7.824 | 276 | 35.2761
7.7 | 4.2416 | 1 | 7.824 | 276 | 35.2761
6.9 | 4.0087 | 1 | 7.824 | 276 | 35.2761
5.2 | 3.1664 | 1 | 7.824 | 276 | 35.2761
4.5 | 2.7053 | 1 | 7.824 | 276 | 35.2761
4.1 | 2.4062 | 1 | 7.824 | 276 | 35.2761
3.5 | 1.775 | 1 | 7.824 | 276 | 35.2761
4.2 | 2.2542 | 1 | 7.824 | 276 | 35.2761
3 | 1.617 | 1 | 7.824 | 276 | 35.2761
0.7 | -0.022844 | 1 | 7.824 | 276 | 35.2761
1.3 | 0.84669 | 1 | 7.824 | 276 | 35.2761
2.9 | 2.0061 | 1 | 7.824 | 276 | 35.2761
1.3 | 0.84669 | 1 | 7.824 | 276 | 35.2761
0.7 | 0.36924 | 1 | 7.824 | 276 | 35.2761
1.1 | 0.76999 | 1 | 7.824 | 276 | 35.2761
1.3 | 0.96754 | 1 | 7.824 | 276 | 35.2761
2.5 | 2.0682 | 1 | 7.824 | 276 | 35.2761
3.4 | 2.9544 | 1 | 7.824 | 276 | 35.2761
4.4 | 3.7167 | 1 | 7.824 | 276 | 35.2761
6 | 4.6542 | 1 | 7.824 | 276 | 35.2761
6.9 | 4.7873 | 1 | 7.824 | 276 | 35.2761
7.4 | 4.8452 | 1 | 7.824 | 276 | 35.2761
7.6 | 4.4893 | 1 | 7.824 | 276 | 35.2761
7.4 | 3.9209 | 1 | 7.824 | 276 | 35.2761
7 | 3.473 | 1 | 7.824 | 276 | 35.2761
6.7 | 3.5428 | 1 | 7.824 | 276 | 35.2761
6.6 | 3.8067 | 1 | 7.824 | 276 | 35.2761
6.5 | 4.2512 | 1 | 7.824 | 276 | 35.2761
6.4 | 4.2791 | 1 | 7.824 | 276 | 35.2761
6 | 3.9887 | 1 | 7.824 | 276 | 35.2761
5.7 | 3.951 | 1 | 7.824 | 276 | 35.2761
5.5 | 4.0937 | 1 | 7.824 | 276 | 35.2761
5.4 | 4.1262 | 1 | 7.824 | 276 | 35.2761
5.9 | 4.3515 | 1 | 7.824 | 276 | 35.2761
5.5 | 4.3536 | 1 | 7.824 | 276 | 35.2761
5.5 | 4.3548 | 1 | 7.824 | 276 | 35.2761
5.1 | 4.5863 | 1 | 7.824 | 276 | 35.2761
5.6 | 4.9859 | 1 | 7.824 | 276 | 35.2761
5.7 | 5.2228 | 1 | 7.824 | 276 | 35.2761
6.5 | 5.8212 | 1 | 7.824 | 276 | 35.2761
6.9 | 6.1653 | 1 | 7.824 | 276 | 35.2761
7.5 | 6.5613 | 1 | 7.824 | 276 | 35.2761
7.9 | 6.8073 | 1 | 7.824 | 276 | 35.2761
8.1 | 6.8592 | 1 | 7.824 | 276 | 35.2761
8.1 | 6.9061 | 1 | 7.824 | 276 | 35.2761
8.8 | 7.4848 | 1 | 7.824 | 276 | 35.2761
9.4 | 7.7271 | 1 | 7.824 | 276 | 35.2761
9.7 | 7.6396 | 1 | 7.824 | 276 | 35.2761
9.8 | 7.2851 | 1 | 7.824 | 276 | 35.2761
9.5 | 7.051 | 1 | 7.824 | 276 | 35.2761
9.3 | 7.0846 | 1 | 7.824 | 276 | 35.2761
9.1 | 7.1207 | 1 | 7.824 | 276 | 35.2761
8.8 | 7.0187 | 1 | 7.824 | 276 | 35.2761
8.7 | 7.0612 | 1 | 7.824 | 276 | 35.2761
8.5 | 6.9168 | 1 | 7.824 | 276 | 35.2761
8.3 | 6.6807 | 1 | 7.824 | 276 | 35.2761
8.1 | 6.3569 | 1 | 7.824 | 276 | 35.2761
8 | 5.9144 | 1 | 7.824 | 276 | 35.2761
7.8 | 5.6432 | 1 | 7.824 | 276 | 35.2761
7.1 | 5.4961 | 1 | 7.824 | 276 | 35.2761
7.2 | 5.3332 | 1 | 7.824 | 276 | 35.2761
7.4 | 5.2281 | 1 | 7.824 | 276 | 35.2761
7.3 | 5.0535 | 1 | 7.824 | 276 | 35.2761
6.8 | 4.5116 | 1 | 7.824 | 276 | 35.2761
6.2 | 4.5588 | 1 | 7.824 | 276 | 35.2761
6.2 | 5.0744 | 1 | 7.824 | 276 | 35.2761
7.9 | 6.3453 | 1 | 7.824 | 276 | 35.2761
7.9 | 5.9926 | 1 | 7.824 | 276 | 35.2761
9.2 | 5.9924 | 1 | 7.824 | 276 | 35.2761
8.7 | 5.7758 | 1 | 7.824 | 276 | 35.2761
8.9 | 5.9574 | 1 | 7.824 | 276 | 35.2761
9.6 | 6.5522 | 1 | 7.824 | 276 | 35.2761
8.9 | 6.1601 | 1 | 7.824 | 276 | 35.2761
8 | 5.4153 | 1 | 7.824 | 276 | 35.2761
6.9 | 4.8442 | 1 | 7.824 | 276 | 35.2761
7.2 | 5.2072 | 1 | 7.824 | 276 | 35.2761
6.5 | 5.0114 | 1 | 7.824 | 276 | 35.2761
6.7 | 5.2018 | 1 | 7.824 | 276 | 35.2761
6 | 4.9246 | 1 | 7.824 | 276 | 35.2761
6.1 | 5.0211 | 1 | 7.824 | 276 | 35.2761
4.8 | 4.2461 | 1 | 7.824 | 276 | 35.2761
5 | 4.4422 | 1 | 7.824 | 276 | 35.2761
4.3 | 3.8438 | 1 | 7.824 | 276 | 35.2761
3.6 | 3.1978 | 1 | 7.824 | 276 | 35.2761
4.6 | 4.275 | 1 | 7.824 | 276 | 35.2761
5.1 | 4.677 | 1 | 7.824 | 276 | 35.2761
5.6 | 5.1702 | 1 | 7.824 | 276 | 35.2761
6.2 | 5.5265 | 1 | 7.824 | 276 | 35.2761
4.8 | 4.2008 | 1 | 7.824 | 276 | 35.2761
7.3 | 6.5553 | 1 | 7.824 | 276 | 35.2761
8.1 | 7.2394 | 1 | 7.824 | 276 | 35.2761
8.6 | 7.5308 | 1 | 7.824 | 276 | 35.2761
8.9 | 7.6748 | 1 | 7.824 | 276 | 35.2761
10.1 | 8.4869 | 1 | 7.824 | 276 | 35.2761
10.4 | 8.7726 | 1 | 7.824 | 276 | 35.2761
10.5 | 8.7693 | 1 | 7.824 | 276 | 35.2761
10.3 | 8.7254 | 1 | 7.824 | 276 | 35.2761
9.6 | 8.1522 | 1 | 7.824 | 276 | 35.2761
8.5 | 7.3834 | 1 | 7.824 | 276 | 35.2761
9.4 | 8.1063 | 1 | 7.824 | 276 | 35.2761
9.6 | 8.3979 | 1 | 7.824 | 276 | 35.2761
9.8 | 8.5413 | 1 | 7.824 | 276 | 35.2761
8.8 | 8.0203 | 1 | 7.824 | 276 | 35.2761
9.2 | 8.3101 | 1 | 7.824 | 276 | 35.2761
9.9 | 8.6378 | 1 | 7.824 | 276 | 35.2761
9.9 | 8.5378 | 1 | 7.824 | 276 | 35.2761
9.5 | 8.4003 | 1 | 7.824 | 276 | 35.2761
9.4 | 8.2036 | 1 | 7.824 | 276 | 35.2761
9.2 | 7.8148 | 1 | 7.824 | 276 | 35.2761
9.4 | 7.8621 | 1 | 7.824 | 276 | 35.2761
9.8 | 8.1479 | 1 | 7.824 | 276 | 35.2761
9.9 | 8.1463 | 1 | 7.824 | 276 | 35.2761
10.1 | 8.2875 | 1 | 7.824 | 276 | 35.2761
10.4 | 8.524 | 1 | 7.824 | 276 | 35.2761
10.5 | 8.7157 | 1 | 7.824 | 276 | 35.2761
10.7 | 9.0043 | 1 | 7.824 | 276 | 35.2761
11.3 | 9.3762 | 1 | 7.824 | 276 | 35.2761
12.5 | 10.1095 | 1 | 7.824 | 276 | 35.2761
12.6 | 10.252 | 1 | 7.824 | 276 | 35.2761
12.7 | 10.4455 | 1 | 7.824 | 276 | 35.2761
12.2 | 10.1755 | 1 | 7.824 | 276 | 35.2761
11.4 | 9.769 | 1 | 7.824 | 276 | 35.2761
11.1 | 9.4827 | 1 | 7.824 | 276 | 35.2761
10.7 | 9.1502 | 1 | 7.824 | 276 | 35.2761
10.4 | 8.7629 | 1 | 7.824 | 276 | 35.2761
11.1 | 9.4827 | 1 | 7.824 | 276 | 35.2761
10.3 | 6.9946 | 1 | 7.824 | 276 | 35.2761
9.2 | 5.3921 | 1 | 7.824 | 276 | 35.2761
8.1 | 4.7112 | 1 | 7.824 | 276 | 35.2761
7.3 | 4.2537 | 1 | 7.824 | 276 | 35.2761
8 | 4.5496 | 1 | 7.824 | 276 | 35.2761
7.7 | 4.7251 | 1 | 7.824 | 276 | 35.2761
8.1 | 4.8579 | 1 | 7.824 | 276 | 35.2761
7.8 | 4.8523 | 1 | 7.824 | 276 | 35.2761
7.5 | 4.813 | 1 | 7.824 | 276 | 35.2761
7.4 | 4.8003 | 1 | 7.824 | 276 | 35.2761
7.7 | 4.9956 | 1 | 7.824 | 276 | 35.2761
8.3 | 5.4645 | 1 | 7.824 | 276 | 35.2761
8.7 | 5.7465 | 1 | 7.824 | 276 | 35.2761
9.5 | 6.1506 | 1 | 7.824 | 276 | 35.2761
8.9 | 6.1329 | 1 | 7.824 | 276 | 35.2761
9.6 | 6.12 | 1 | 7.824 | 276 | 35.2761
9.5 | 5.8761 | 1 | 7.824 | 276 | 35.2761
9.1 | 5.409 | 1 | 7.824 | 276 | 35.2761
8.1 | 5.0079 | 1 | 7.824 | 276 | 35.2761
8 | 5.1505 | 1 | 7.824 | 276 | 35.2761
7.7 | 4.8778 | 1 | 7.824 | 276 | 35.2761
7.4 | 5.0006 | 1 | 7.824 | 276 | 35.2761
6.8 | 5.0656 | 1 | 7.824 | 276 | 35.2761
7.2 | 4.6948 | 1 | 7.824 | 276 | 35.2761
7.6 | 4.9029 | 1 | 7.824 | 276 | 35.2761
7.3 | 5.0293 | 1 | 7.824 | 276 | 35.2761
7.2 | 5.1008 | 1 | 7.824 | 276 | 35.2761
7.4 | 5.2874 | 1 | 7.824 | 276 | 35.2761
7.4 | 5.2874 | 1 | 7.824 | 276 | 35.2761
7.3 | 5.1107 | 1 | 7.824 | 276 | 35.2761
7.1 | 5.0901 | 1 | 7.824 | 276 | 35.2761
7 | 5.2088 | 1 | 7.824 | 276 | 35.2761
6.6 | 5.2218 | 1 | 7.824 | 276 | 35.2761
6.7 | 4.8834 | 1 | 7.824 | 276 | 35.2761
6.7 | 4.8412 | 1 | 7.824 | 276 | 35.2761
6.7 | 4.7992 | 1 | 7.824 | 276 | 35.2761
7.2 | 5.0569 | 1 | 7.824 | 276 | 35.2761
7.9 | 5.2933 | 1 | 7.824 | 276 | 35.2761
8.1 | 5.2738 | 1 | 7.824 | 276 | 35.2761
7.9 | 5.5391 | 1 | 7.824 | 276 | 35.2761
8.8 | 5.6271 | 1 | 7.824 | 276 | 35.2761
8.6 | 5.4863 | 1 | 7.824 | 276 | 35.2761
8.1 | 5.5952 | 1 | 7.824 | 276 | 35.2761
7.9 | 5.2867 | 1 | 7.824 | 276 | 35.2761
7.4 | 5.4065 | 1 | 7.824 | 276 | 35.2761
6.6 | 5.6722 | 1 | 7.824 | 276 | 35.2761
6.7 | 6.2488 | 1 | 7.824 | 276 | 35.2761
6.7 | 5.4454 | 1 | 7.824 | 276 | 35.2761
6.3 | 4.84 | 1 | 7.824 | 276 | 35.2761
6.5 | 4.986 | 1 | 7.824 | 276 | 35.2761
5.9 | 3.9975 | 1 | 7.824 | 276 | 35.2761
4.9 | 3.5046 | 1 | 7.824 | 276 | 35.2761
4.5 | 3.2474 | 1 | 7.824 | 276 | 35.2761
4.1 | 2.5828 | 1 | 7.824 | 276 | 35.2761
3.3 | 1.8578 | 1 | 7.824 | 276 | 35.2761
3 | 1.4723 | 1 | 7.824 | 276 | 35.2761
3 | 1.3877 | 1 | 7.824 | 276 | 35.2761
2.6 | 0.90996 | 1 | 7.824 | 276 | 35.2761
2 | 0.7715 | 1 | 7.824 | 276 | 35.2761
2.3 | 0.15433 | 1 | 7.824 | 276 | 35.2761
2.7 | -0.43142 | 1 | 7.824 | 276 | 35.2761
3.3 | -0.42711 | 1 | 7.824 | 276 | 35.2761
3.7 | -0.74224 | 1 | 7.824 | 276 | 35.2761
4.2 | -0.50054 | 1 | 7.824 | 276 | 35.2761
4.7 | -0.05827 | 1 | 7.824 | 276 | 35.2761
4.8 | 0.22405 | 1 | 7.824 | 276 | 35.2761
4.2 | -0.41039 | 1 | 7.824 | 276 | 35.2761
3.7 | -0.62395 | 1 | 7.824 | 276 | 35.2761
2.9 | -1.1805 | 1 | 7.824 | 276 | 35.2761
2.2 | -1.1105 | 1 | 7.824 | 276 | 35.2761
1.7 | -1.1794 | 1 | 7.824 | 276 | 35.2761
1.1 | -1.1992 | 1 | 7.824 | 276 | 35.2761
0.9 | -1.3163 | 1 | 7.824 | 276 | 35.2761
0.7 | -1.402 | 1 | 7.824 | 276 | 35.2761
-1.1 | -2.4444 | 1 | 7.824 | 276 | 35.2761
0.4 | -1.7063 | 1 | 7.824 | 276 | 35.2761
0.6 | -1.2668 | 1 | 7.824 | 276 | 35.2761
-0.2 | -1.7718 | 1 | 7.824 | 276 | 35.2761
-0.1 | -1.2959 | 1 | 7.824 | 276 | 35.2761
-0.4 | -1.6163 | 1 | 7.824 | 276 | 35.2761
-0.5 | -1.4954 | 1 | 7.824 | 276 | 35.2761
0.7 | -0.57728 | 1 | 7.824 | 276 | 35.2761
0.6 | -0.55984 | 1 | 7.824 | 276 | 35.2761
1.2 | -0.29364 | 1 | 7.824 | 276 | 35.2761
1.8 | 0.48507 | 1 | 7.824 | 276 | 35.2761
2.5 | 1.1 | 1 | 7.824 | 276 | 35.2761
2.8 | 1.2709 | 1 | 7.824 | 276 | 35.2761
2.6 | 1.5834 | 1 | 7.824 | 276 | 35.2761
2.3 | 1.4528 | 1 | 7.824 | 276 | 35.2761
2.5 | 1.7687 | 1 | 7.824 | 276 | 35.2761
2.2 | 1.558 | 1 | 7.824 | 276 | 35.2761
2.2 | 1.3951 | 1 | 7.824 | 276 | 35.2761
2.4 | 1.712 | 1 | 7.824 | 276 | 35.2761
2.7 | 1.7989 | 1 | 7.824 | 276 | 35.2761
2.6 | 1.7021 | 1 | 7.824 | 276 | 35.2761
2.2 | 1.3951 | 1 | 7.824 | 276 | 35.2761
0.6 | 0.036115 | 1 | 7.824 | 276 | 35.2761
-0.3 | -0.42944 | 1 | 7.824 | 276 | 35.2761
0.1 | -0.84938 | 1 | 7.824 | 276 | 35.2761
-0.4 | -1.5134 | 1 | 7.824 | 276 | 35.2761
-1.1 | -2.1081 | 1 | 7.824 | 276 | 35.2761
-1.7 | -2.7494 | 1 | 7.824 | 276 | 35.2761
-1.6 | -2.5152 | 1 | 7.824 | 276 | 35.2761
-1 | -1.9038 | 1 | 7.824 | 276 | 35.2761
-0.7 | -1.5789 | 1 | 7.824 | 276 | 35.2761
-1.1 | -1.9991 | 1 | 7.824 | 276 | 35.2761
-1.3 | -2.3322 | 1 | 7.824 | 276 | 35.2761
-1 | -2.1163 | 1 | 7.824 | 276 | 35.2761
-0.1 | -1.2987 | 1 | 7.824 | 276 | 35.2761
1 | -0.51749 | 1 | 7.824 | 276 | 35.2761
1.9 | -0.61725 | 1 | 7.824 | 276 | 35.2761
2.5 | -0.27579 | 1 | 7.824 | 276 | 35.2761
3.2 | -0.064929 | 1 | 7.824 | 276 | 35.2761
3.1 | -0.060973 | 1 | 7.824 | 276 | 35.2761
3 | -0.63157 | 1 | 7.824 | 276 | 35.2761
2.3 | -0.8382 | 1 | 7.824 | 276 | 35.2761
1.3 | -1.118 | 1 | 7.824 | 276 | 35.2761
0.3 | -1.7681 | 1 | 7.824 | 276 | 35.2761
0.9 | -1.5357 | 1 | 7.824 | 276 | 35.2761
0.1 | -2.0412 | 1 | 7.824 | 276 | 35.2761
-0.1 | -2.0053 | 1 | 7.824 | 276 | 35.2761
-0.8 | -2.1648 | 1 | 7.824 | 276 | 35.2761
-0.8 | -2.0285 | 1 | 7.824 | 276 | 35.2761
-1.5 | -2.5196 | 1 | 7.824 | 276 | 35.2761
-1.4 | -2.3192 | 1 | 7.824 | 276 | 35.2761
-1.5 | -2.7557 | 1 | 7.824 | 276 | 35.2761
-1.1 | -2.5769 | 1 | 7.824 | 276 | 35.2761
-1.2 | -2.7966 | 1 | 7.824 | 276 | 35.2761
-0.2 | -1.8722 | 1 | 7.824 | 276 | 35.2761
-0.4 | -1.858 | 1 | 7.824 | 276 | 35.2761
-0.3 | -1.626 | 1 | 7.824 | 276 | 35.2761
0.6 | -0.44202 | 1 | 7.824 | 276 | 35.2761
1.6 | -0.68578 | 1 | 7.824 | 276 | 35.2761
2.7 | -0.30683 | 1 | 7.824 | 276 | 35.2761
3.2 | 0.54339 | 1 | 7.824 | 276 | 35.2761
3.5 | 0.82687 | 1 | 7.824 | 276 | 35.2761
4.2 | 1.1955 | 1 | 7.824 | 276 | 35.2761
4.3 | 0.94466 | 1 | 7.824 | 276 | 35.2761
4.1 | 0.76446 | 1 | 7.824 | 276 | 35.2761
3.4 | 0.69873 | 1 | 7.824 | 276 | 35.2761
2.5 | 0.28119 | 1 | 7.824 | 276 | 35.2761
2 | -0.28591 | 1 | 7.824 | 276 | 35.2761
1.9 | -0.507 | 1 | 7.824 | 276 | 35.2761
1.5 | -0.80152 | 1 | 7.824 | 276 | 35.2761
0.2 | -1.3254 | 1 | 7.824 | 276 | 35.2761
0.2 | -1.6905 | 1 | 7.824 | 276 | 35.2761
-1 | -2.1076 | 1 | 7.824 | 276 | 35.2761
-0.2 | -1.7644 | 1 | 7.824 | 276 | 35.2761
-2.3 | -3.1087 | 1 | 7.824 | 276 | 35.2761
-1.5 | -2.4101 | 1 | 7.824 | 276 | 35.2761
-1.1 | -2.0973 | 1 | 7.824 | 276 | 35.2761
-1.3 | -2.3229 | 1 | 7.824 | 276 | 35.2761
-1.5 | -2.4095 | 1 | 7.824 | 276 | 35.2761
-1.5 | -2.409 | 1 | 7.824 | 276 | 35.2761
-1.6 | -2.3988 | 1 | 7.824 | 276 | 35.2761
-1.5 | -2.4095 | 1 | 7.824 | 276 | 35.2761
0.9 | -0.70495 | 1 | 7.824 | 276 | 35.2761
3.6 | 1.229 | 1 | 7.824 | 276 | 35.2761
5.3 | 1.7713 | 1 | 7.824 | 276 | 35.2761
5 | 1.7394 | 1 | 7.824 | 276 | 35.2761
5.2 | 1.6446 | 1 | 7.824 | 276 | 35.2761
5.3 | 2.0516 | 1 | 7.824 | 276 | 35.2761
5.3 | 2.5008 | 1 | 7.824 | 276 | 35.2761
4.9 | 2.6402 | 1 | 7.824 | 276 | 35.2761
4.8 | 2.7922 | 1 | 7.824 | 276 | 35.2761
4.3 | 2.5149 | 1 | 7.824 | 276 | 35.2761
3.9 | 2.6046 | 1 | 7.824 | 276 | 35.2761
4 | 2.621 | 1 | 7.824 | 276 | 35.2761
3.4 | 2.5303 | 1 | 7.824 | 276 | 35.2761
3.2 | 2.4184 | 1 | 7.824 | 276 | 35.2761
3 | 2.4327 | 1 | 7.824 | 276 | 35.2761
3.2 | 2.5022 | 1 | 7.824 | 276 | 35.2761
3.4 | 2.4892 | 1 | 7.824 | 276 | 35.2761
3.1 | 2.363 | 1 | 7.824 | 276 | 35.2761
3.2 | 2.3775 | 1 | 7.824 | 276 | 35.2761
3 | 2.4327 | 1 | 7.824 | 276 | 35.2761
2.9 | 2.4192 | 1 | 7.824 | 276 | 35.2761
3.1 | 2.363 | 1 | 7.824 | 276 | 35.2761
3.2 | 2.296 | 1 | 7.824 | 276 | 35.2761
3.6 | 2.5201 | 1 | 7.824 | 276 | 35.2761
4.1 | 2.8784 | 1 | 7.824 | 276 | 35.2761
4.7 | 3.2888 | 1 | 7.824 | 276 | 35.2761
5.8 | 4.1685 | 1 | 7.824 | 276 | 35.2761
6.5 | 4.4979 | 1 | 7.824 | 276 | 35.2761
7.1 | 4.8531 | 1 | 7.824 | 276 | 35.2761
7.1 | 4.6527 | 1 | 7.824 | 276 | 35.2761
7.3 | 4.7574 | 1 | 7.824 | 276 | 35.2761
6.9 | 4.6688 | 1 | 7.824 | 276 | 35.2761
6.1 | 4.2059 | 1 | 7.824 | 276 | 35.2761
5.3 | 3.8614 | 1 | 7.824 | 276 | 35.2761
4.7 | 3.5377 | 1 | 7.824 | 276 | 35.2761
4.4 | 3.3747 | 1 | 7.824 | 276 | 35.2761
4 | 3.1145 | 1 | 7.824 | 276 | 35.2761
4.1 | 3.1693 | 1 | 7.824 | 276 | 35.2761
3.7 | 3.0349 | 1 | 7.824 | 276 | 35.2761
3.7 | 2.9923 | 1 | 7.824 | 276 | 35.2761
3.7 | 2.8658 | 1 | 7.824 | 276 | 35.2761
3.4 | 2.4107 | 1 | 7.824 | 276 | 35.2761
3.6 | 2.2838 | 1 | 7.824 | 276 | 35.2761
3.7 | 2.1861 | 1 | 7.824 | 276 | 35.2761
3.1 | 1.9246 | 1 | 7.824 | 276 | 35.2761
3 | 1.907 | 1 | 7.824 | 276 | 35.2761
1.9 | 1.0744 | 1 | 7.824 | 276 | 35.2761
3 | 1.4963 | 1 | 7.824 | 276 | 35.2761
4.1 | 2.1235 | 1 | 7.824 | 276 | 35.2761
5.1 | 2.5655 | 1 | 7.824 | 276 | 35.2761
5.9 | 2.4487 | 1 | 7.824 | 276 | 35.2761
6.5 | 1.3152 | 1 | 7.824 | 276 | 35.2761
6.7 | 2.143 | 1 | 7.824 | 276 | 35.2761
7 | 1.8587 | 1 | 7.824 | 276 | 35.2761
5.8 | 1.3098 | 1 | 7.824 | 276 | 35.2761
4.9 | 0.53576 | 1 | 7.824 | 276 | 35.2761
4.4 | 0.23937 | 1 | 7.824 | 276 | 35.2761
3.3 | 0.20487 | 1 | 7.824 | 276 | 35.2761
2.5 | -0.22941 | 1 | 7.824 | 276 | 35.2761
1.7 | -0.69068 | 1 | 7.824 | 276 | 35.2761
0.6 | -1.0048 | 1 | 7.824 | 276 | 35.2761
0.1 | -1.2993 | 1 | 7.824 | 276 | 35.2761
-1.2 | -2.1834 | 1 | 7.824 | 276 | 35.2761
-1.9 | -2.6811 | 1 | 7.824 | 276 | 35.2761
-1.6 | -2.3921 | 1 | 7.824 | 276 | 35.2761
-2.4 | -3.0951 | 1 | 7.824 | 276 | 35.2761
-2.4 | -3.231 | 1 | 7.824 | 276 | 35.2761
-1.5 | -2.6393 | 1 | 7.824 | 276 | 35.2761
-2.7 | -3.5196 | 1 | 7.824 | 276 | 35.2761
-1 | -2.2343 | 1 | 7.824 | 276 | 35.2761
-0.9 | -2.107 | 1 | 7.824 | 276 | 35.2761
0.4 | -0.98697 | 1 | 7.824 | 276 | 35.2761
1.5 | -0.41996 | 1 | 7.824 | 276 | 35.2761
3.8 | 1.5478 | 1 | 7.824 | 276 | 35.2761
4.4 | 2.6527 | 1 | 7.824 | 276 | 35.2761
5.4 | 3.7511 | 1 | 7.824 | 276 | 35.2761
5.7 | 4.0336 | 1 | 7.824 | 276 | 35.2761
6.1 | 4.5788 | 1 | 7.824 | 276 | 35.2761
5.9 | 4.955 | 1 | 7.824 | 276 | 35.2761
6.1 | 5.5659 | 1 | 7.824 | 276 | 35.2761
6.5 | 6.1038 | 1 | 7.824 | 276 | 35.2761
6.6 | 6.2026 | 1 | 7.824 | 276 | 35.2761
6.6 | 6.2515 | 1 | 7.824 | 276 | 35.2761
7 | 6.5978 | 1 | 7.824 | 276 | 35.2761
7 | 6.4995 | 1 | 7.824 | 276 | 35.2761
7.2 | 6.7458 | 1 | 7.824 | 276 | 35.2761
6.6 | 6.0573 | 1 | 7.824 | 276 | 35.2761
6.1 | 5.1935 | 1 | 7.824 | 276 | 35.2761
5.6 | 4.6191 | 1 | 7.824 | 276 | 35.2761
4.5 | 3.814 | 1 | 7.824 | 276 | 35.2761
3.8 | 3.3478 | 1 | 7.824 | 276 | 35.2761
3.2 | 2.757 | 1 | 7.824 | 276 | 35.2761
3.1 | 2.6156 | 1 | 7.824 | 276 | 35.2761
3.2 | 2.6711 | 1 | 7.824 | 276 | 35.2761
3 | 2.5603 | 1 | 7.824 | 276 | 35.2761
3.5 | 3.0524 | 1 | 7.824 | 276 | 35.2761
5 | 4.2579 | 1 | 7.824 | 276 | 35.2761
5.3 | 4.461 | 1 | 7.824 | 276 | 35.2761
7.3 | 5.9416 | 1 | 7.824 | 276 | 35.2761
7 | 5.5194 | 1 | 7.824 | 276 | 35.2761
8.2 | 6.2126 | 1 | 7.824 | 276 | 35.2761
8.8 | 6.2519 | 1 | 7.824 | 276 | 35.2761
8.4 | 5.9659 | 1 | 7.824 | 276 | 35.2761
8.2 | 5.8218 | 1 | 7.824 | 276 | 35.2761
7.8 | 5.3686 | 1 | 7.824 | 276 | 35.2761
7.4 | 5.5004 | 1 | 7.824 | 276 | 35.2761
7.2 | 5.4853 | 1 | 7.824 | 276 | 35.2761
6.9 | 5.3314 | 1 | 7.824 | 276 | 35.2761
6.2 | 4.7956 | 1 | 7.824 | 276 | 35.2761
6.1 | 4.7428 | 1 | 7.824 | 276 | 35.2761
6.1 | 4.6561 | 1 | 7.824 | 276 | 35.2761
6.8 | 5.191 | 1 | 7.824 | 276 | 35.2761
6.3 | 5.1102 | 1 | 7.824 | 276 | 35.2761
7.1 | 5.7425 | 1 | 7.824 | 276 | 35.2761
7.3 | 5.9799 | 1 | 7.824 | 276 | 35.2761
7.1 | 5.9251 | 1 | 7.824 | 276 | 35.2761
6.1 | 4.6979 | 1 | 7.824 | 276 | 35.2761
5.9 | 4.6373 | 1 | 7.824 | 276 | 35.2761
5.8 | 4.3266 | 1 | 7.824 | 276 | 35.2761
6.8 | 3.6668 | 1 | 7.824 | 276 | 35.2761
7.7 | 4.345 | 1 | 7.824 | 276 | 35.2761
8.4 | 4.597 | 1 | 7.824 | 276 | 35.2761
8.1 | 3.6168 | 1 | 7.824 | 276 | 35.2761
8.7 | 3.6371 | 1 | 7.824 | 276 | 35.2761
8.6 | 3.4234 | 1 | 7.824 | 276 | 35.2761
8.6 | 3.3301 | 1 | 7.824 | 276 | 35.2761
8.4 | 3.605 | 1 | 7.824 | 276 | 35.2761
8 | 3.4229 | 1 | 7.824 | 276 | 35.2761
6.8 | 3.0156 | 1 | 7.824 | 276 | 35.2761
6.6 | 2.9772 | 1 | 7.824 | 276 | 35.2761
6 | 3.0315 | 1 | 7.824 | 276 | 35.2761
5.8 | 3.0426 | 1 | 7.824 | 276 | 35.2761
5.9 | 3.2613 | 1 | 7.824 | 276 | 35.2761
5.5 | 3.3161 | 1 | 7.824 | 276 | 35.2761
4.9 | 3.1066 | 1 | 7.824 | 276 | 35.2761
5.3 | 3.4026 | 1 | 7.824 | 276 | 35.2761
5.7 | 3.54 | 1 | 7.824 | 276 | 35.2761
5.7 | 3.6181 | 1 | 7.824 | 276 | 35.2761
6 | 3.474 | 1 | 7.824 | 276 | 35.2761
4.4 | 2.9941 | 1 | 7.824 | 276 | 35.2761
5.1 | 2.8254 | 1 | 7.824 | 276 | 35.2761
4.8 | 2.9368 | 1 | 7.824 | 276 | 35.2761
4.4 | 2.9957 | 1 | 7.824 | 276 | 35.2761
4.8 | 3.0549 | 1 | 7.824 | 276 | 35.2761
5.1 | 2.9124 | 1 | 7.824 | 276 | 35.2761
6 | 3.6675 | 1 | 7.824 | 276 | 35.2761
7.1 | 4.5621 | 1 | 7.824 | 276 | 35.2761
8.2 | 4.5728 | 1 | 7.824 | 276 | 35.2761
9 | 4.9889 | 1 | 7.824 | 276 | 35.2761
9 | 5.0604 | 1 | 7.824 | 276 | 35.2761
8.8 | 5.3232 | 1 | 7.824 | 276 | 35.2761
8.3 | 5.4975 | 1 | 7.824 | 276 | 35.2761
7.9 | 5.6243 | 1 | 7.824 | 276 | 35.2761
7.5 | 5.9451 | 1 | 7.824 | 276 | 35.2761
7.3 | 6.3075 | 1 | 7.824 | 276 | 35.2761
8 | 7.0347 | 1 | 7.824 | 276 | 35.2761
8 | 7.3806 | 1 | 7.824 | 276 | 35.2761
8.3 | 7.7771 | 1 | 7.824 | 276 | 35.2761
9.6 | 8.4371 | 1 | 7.824 | 276 | 35.2761
9.8 | 8.3799 | 1 | 7.824 | 276 | 35.2761
9.9 | 8.23 | 1 | 7.824 | 276 | 35.2761
9.9 | 8.134 | 1 | 7.824 | 276 | 35.2761
9.6 | 7.8013 | 1 | 7.824 | 276 | 35.2761
9.7 | 7.897 | 1 | 7.824 | 276 | 35.2761
9.6 | 7.7548 | 1 | 7.824 | 276 | 35.2761
9.8 | 7.7567 | 1 | 7.824 | 276 | 35.2761
9.3 | 7.4724 | 1 | 7.824 | 276 | 35.2761
9.7 | 7.7579 | 1 | 7.824 | 276 | 35.2761
9.8 | 7.8995 | 1 | 7.824 | 276 | 35.2761
10.1 | 8.1365 | 1 | 7.824 | 276 | 35.2761
11.2 | 8.3273 | 1 | 7.824 | 276 | 35.2761
11.3 | 8.2394 | 1 | 7.824 | 276 | 35.2761
11 | 8.3237 | 1 | 7.824 | 276 | 35.2761
11 | 8.4157 | 1 | 7.824 | 276 | 35.2761
10.9 | 8.3691 | 1 | 7.824 | 276 | 35.2761
10.7 | 8.3223 | 1 | 7.824 | 276 | 35.2761
9.9 | 7.9467 | 1 | 7.824 | 276 | 35.2761
9.5 | 7.7572 | 1 | 7.824 | 276 | 35.2761
9.4 | 7.8045 | 1 | 7.824 | 276 | 35.2761
9.5 | 8.193 | 1 | 7.824 | 276 | 35.2761
9.2 | 8.3035 | 1 | 7.824 | 276 | 35.2761
9.6 | 8.3885 | 1 | 7.824 | 276 | 35.2761
9.2 | 8.4566 | 1 | 7.824 | 276 | 35.2761
9.2 | 8.4563 | 1 | 7.824 | 276 | 35.2761
9.3 | 8.6057 | 1 | 7.824 | 276 | 35.2761
9.8 | 8.9388 | 1 | 7.824 | 276 | 35.2761
10 | 9.0819 | 1 | 7.824 | 276 | 35.2761
9.9 | 9.3001 | 1 | 7.824 | 276 | 35.2761
10.3 | 9.3741 | 1 | 7.824 | 276 | 35.2761
10.8 | 9.7561 | 1 | 7.824 | 276 | 35.2761
10.9 | 10.0132 | 1 | 7.824 | 276 | 35.2761
11.1 | 10.2627 | 1 | 7.824 | 276 | 35.2761
12 | 10.8148 | 1 | 7.824 | 276 | 35.2761
12.1 | 10.9118 | 1 | 7.824 | 276 | 35.2761
12.7 | 11.2206 | 1 | 7.824 | 276 | 35.2761
13 | 11.4559 | 1 | 7.824 | 276 | 35.2761
13 | 11.619 | 1 | 7.824 | 276 | 35.2761
12.8 | 11.2097 | 1 | 7.824 | 276 | 35.2761
12.9 | 11.1444 | 1 | 7.824 | 276 | 35.2761
12.4 | 10.8255 | 1 | 7.824 | 276 | 35.2761
12.1 | 10.6433 | 1 | 7.824 | 276 | 35.2761
12 | 10.5476 | 1 | 7.824 | 276 | 35.2761
11.4 | 10.3402 | 1 | 7.824 | 276 | 35.2761
9.8 | 9.044 | 1 | 7.824 | 276 | 35.2761
9 | 7.9569 | 1 | 7.824 | 276 | 35.2761
8.8 | 6.9054 | 1 | 7.824 | 276 | 35.2761
8.6 | 7.1338 | 1 | 7.824 | 276 | 35.2761
8.2 | 6.384 | 1 | 7.824 | 276 | 35.2761
7.8 | 6.6491 | 1 | 7.824 | 276 | 35.2761
7.9 | 6.938 | 1 | 7.824 | 276 | 35.2761
5.9 | 5.4612 | 1 | 7.824 | 276 | 35.2761
7.2 | 6.0698 | 1 | 7.824 | 276 | 35.2761
6.4 | 5.298 | 1 | 7.824 | 276 | 35.2761
6.3 | 5.2923 | 1 | 7.824 | 276 | 35.2761
4.6 | 3.8209 | 1 | 7.824 | 276 | 35.2761
6.9 | 4.903 | 1 | 7.824 | 276 | 35.2761
7.5 | 4.929 | 1 | 7.824 | 276 | 35.2761
8.4 | 4.8238 | 1 | 7.824 | 276 | 35.2761
8.8 | 5.1019 | 1 | 7.824 | 276 | 35.2761
9.5 | 5.5701 | 1 | 7.824 | 276 | 35.2761
9.8 | 5.6494 | 1 | 7.824 | 276 | 35.2761
9.1 | 5.2927 | 1 | 7.824 | 276 | 35.2761
8.6 | 4.9987 | 1 | 7.824 | 276 | 35.2761
8.2 | 4.6815 | 1 | 7.824 | 276 | 35.2761
7.7 | 4.6809 | 1 | 7.824 | 276 | 35.2761
7.5 | 4.3495 | 1 | 7.824 | 276 | 35.2761
7.1 | 4.1012 | 1 | 7.824 | 276 | 35.2761
6.8 | 4.1287 | 1 | 7.824 | 276 | 35.2761
6.4 | 4.3106 | 1 | 7.824 | 276 | 35.2761
6.4 | 4.6411 | 1 | 7.824 | 276 | 35.2761
6.7 | 4.8383 | 1 | 7.824 | 276 | 35.2761
6.6 | 4.8714 | 1 | 7.824 | 276 | 35.2761
6.8 | 5.1025 | 1 | 7.824 | 276 | 35.2761
6.7 | 5.2251 | 1 | 7.824 | 276 | 35.2761
6.8 | 5.3642 | 1 | 7.824 | 276 | 35.2761
7.1 | 5.5159 | 1 | 7.824 | 276 | 35.2761
7.2 | 6.0658 | 1 | 7.824 | 276 | 35.2761
8 | 7.0799 | 1 | 7.824 | 276 | 35.2761
8.3 | 7.5215 | 1 | 7.824 | 276 | 35.2761
8.9 | 6.8534 | 1 | 7.824 | 276 | 35.2761
9.7 | 7.2844 | 1 | 7.824 | 276 | 35.2761
9.5 | 6.9197 | 1 | 7.824 | 276 | 35.2761
10.4 | 7.8411 | 1 | 7.824 | 276 | 35.2761
10.7 | 8.0262 | 1 | 7.824 | 276 | 35.2761
11.2 | 7.8588 | 1 | 7.824 | 276 | 35.2761
9.4 | 7.5058 | 1 | 7.824 | 276 | 35.2761
9.4 | 6.8248 | 1 | 7.824 | 276 | 35.2761
9.2 | 5.73 | 1 | 7.824 | 276 | 35.2761
8.7 | 4.7205 | 1 | 7.824 | 276 | 35.2761
7.9 | 4.7591 | 1 | 7.824 | 276 | 35.2761
7.6 | 4.3397 | 1 | 7.824 | 276 | 35.2761
5.9 | 3.9111 | 1 | 7.824 | 276 | 35.2761
4.2 | 3.1244 | 1 | 7.824 | 276 | 35.2761
5 | 3.1887 | 1 | 7.824 | 276 | 35.2761
4.8 | 2.9606 | 1 | 7.824 | 276 | 35.2761
4.2 | 1.8543 | 1 | 7.824 | 276 | 35.2761
3.5 | 1.5821 | 1 | 7.824 | 276 | 35.2761
3.4 | 1.1635 | 1 | 7.824 | 276 | 35.2761
3.6 | 1.2003 | 1 | 7.824 | 276 | 35.2761
3.2 | 1.4131 | 1 | 7.824 | 276 | 35.2761
3.8 | 1.5105 | 1 | 7.824 | 276 | 35.2761
3.7 | 1.4935 | 1 | 7.824 | 276 | 35.2761
3.4 | 1.6952 | 1 | 7.824 | 276 | 35.2761
4.5 | 2.229 | 1 | 7.824 | 276 | 35.2761
5.5 | 2.5832 | 1 | 7.824 | 276 | 35.2761
6.1 | 2.6856 | 1 | 7.824 | 276 | 35.2761
6.7 | 2.7962 | 1 | 7.824 | 276 | 35.2761
7.5 | 3.4492 | 1 | 7.824 | 276 | 35.2761
7.9 | 3.3151 | 1 | 7.824 | 276 | 35.2761
7 | 3.22 | 1 | 7.824 | 276 | 35.2761
7.7 | 3.0749 | 1 | 7.824 | 276 | 35.2761
6.7 | 2.5622 | 1 | 7.824 | 276 | 35.2761
5.8 | 2.0957 | 1 | 7.824 | 276 | 35.2761
5.1 | 1.5657 | 1 | 7.824 | 276 | 35.2761
4.2 | 2.3658 | 1 | 7.824 | 276 | 35.2761
3.7 | 1.7899 | 1 | 7.824 | 276 | 35.2761
3.7 | 1.7899 | 1 | 7.824 | 276 | 35.2761
3.5 | 1.472 | 1 | 7.824 | 276 | 35.2761
3.5 | 1.2751 | 1 | 7.824 | 276 | 35.2761
3.5 | 1.0084 | 1 | 7.824 | 276 | 35.2761
3.1 | 0.9684 | 1 | 7.824 | 276 | 35.2761
2.9 | 0.8139 | 1 | 7.824 | 276 | 35.2761
2.7 | 0.73641 | 1 | 7.824 | 276 | 35.2761
2.8 | 0.60461 | 1 | 7.824 | 276 | 35.2761
2.7 | 0.66023 | 1 | 7.824 | 276 | 35.2761
2.5 | 0.46806 | 1 | 7.824 | 276 | 35.2761
2.7 | 0.58516 | 1 | 7.824 | 276 | 35.2761
3.9 | 1.4706 | 1 | 7.824 | 276 | 35.2761
5.2 | 2.4359 | 1 | 7.824 | 276 | 35.2761
6.1 | 2.6325 | 1 | 7.824 | 276 | 35.2761
6.8 | 2.8396 | 1 | 7.824 | 276 | 35.2761
7.3 | 2.9426 | 1 | 7.824 | 276 | 35.2761
7.5 | 2.9501 | 1 | 7.824 | 276 | 35.2761
7.1 | 2.9327 | 1 | 7.824 | 276 | 35.2761
6.7 | 2.9609 | 1 | 7.824 | 276 | 35.2761
6.5 | 2.5653 | 1 | 7.824 | 276 | 35.2761
5.2 | 2.2782 | 1 | 7.824 | 276 | 35.2761
5.5 | 2.3307 | 1 | 7.824 | 276 | 35.2761
5.5 | 2.404 | 1 | 7.824 | 276 | 35.2761
4.3 | 2.7772 | 1 | 7.824 | 276 | 35.2761
3.1 | 2.316 | 1 | 7.824 | 276 | 35.2761
2.8 | 2.1482 | 1 | 7.824 | 276 | 35.2761
2.6 | 2.1203 | 1 | 7.824 | 276 | 35.2761
2.6 | 2.1626 | 1 | 7.824 | 276 | 35.2761
2.8 | 2.3593 | 1 | 7.824 | 276 | 35.2761
2.9 | 2.6317 | 1 | 7.824 | 276 | 35.2761
3.3 | 3.0726 | 1 | 7.824 | 276 | 35.2761
3.8 | 3.4779 | 1 | 7.824 | 276 | 35.2761
4 | 3.7214 | 1 | 7.824 | 276 | 35.2761
4.4 | 4.0254 | 1 | 7.824 | 276 | 35.2761
4.8 | 4.3281 | 1 | 7.824 | 276 | 35.2761
5.2 | 4.6294 | 1 | 7.824 | 276 | 35.2761
5.5 | 4.7854 | 1 | 7.824 | 276 | 35.2761
5.5 | 4.7399 | 1 | 7.824 | 276 | 35.2761
5.7 | 4.7528 | 1 | 7.824 | 276 | 35.2761
5.7 | 4.3993 | 1 | 7.824 | 276 | 35.2761
5.8 | 4.0716 | 1 | 7.824 | 276 | 35.2761
6.3 | 4.2153 | 1 | 7.824 | 276 | 35.2761
6.1 | 3.9492 | 1 | 7.824 | 276 | 35.2761
6.1 | 3.8323 | 1 | 7.824 | 276 | 35.2761
6.2 | 3.8094 | 1 | 7.824 | 276 | 35.2761
4.5 | 2.6179 | 1 | 7.824 | 276 | 35.2761
2.5 | 0.58429 | 1 | 7.824 | 276 | 35.2761
1.3 | -0.40823 | 1 | 7.824 | 276 | 35.2761
2.3 | 0.62653 | 1 | 7.824 | 276 | 35.2761
2.1 | 0.54951 | 1 | 7.824 | 276 | 35.2761
1.1 | -0.037564 | 1 | 7.824 | 276 | 35.2761
0.5 | -0.456 | 1 | 7.824 | 276 | 35.2761
-0.6 | -1.2087 | 1 | 7.824 | 276 | 35.2761
-0.3 | -0.67695 | 1 | 7.824 | 276 | 35.2761
-0.8 | -1.3265 | 1 | 7.824 | 276 | 35.2761
-0.2 | -0.93697 | 1 | 7.824 | 276 | 35.2761
-0.2 | -0.70045 | 1 | 7.824 | 276 | 35.2761
0.9 | -0.49075 | 1 | 7.824 | 276 | 35.2761
2.2 | 1.1096 | 1 | 7.824 | 276 | 35.2761
3.3 | 1.7829 | 1 | 7.824 | 276 | 35.2761
4.6 | 2.639 | 1 | 7.824 | 276 | 35.2761
5.7 | 3.7035 | 1 | 7.824 | 276 | 35.2761
6.9 | 4.7818 | 1 | 7.824 | 276 | 35.2761
7.7 | 5.4839 | 1 | 7.824 | 276 | 35.2761
7.9 | 5.8401 | 1 | 7.824 | 276 | 35.2761
8.3 | 6.2585 | 1 | 7.824 | 276 | 35.2761
8.7 | 6.5881 | 1 | 7.824 | 276 | 35.2761
8.5 | 6.6694 | 1 | 7.824 | 276 | 35.2761
8.8 | 6.8164 | 1 | 7.824 | 276 | 35.2761
8.3 | 6.4803 | 1 | 7.824 | 276 | 35.2761
7.8 | 6.3697 | 1 | 7.824 | 276 | 35.2761
8 | 6.6536 | 1 | 7.824 | 276 | 35.2761
8.5 | 7.0388 | 1 | 7.824 | 276 | 35.2761
8.3 | 6.9416 | 1 | 7.824 | 276 | 35.2761
8.2 | 6.8923 | 1 | 7.824 | 276 | 35.2761
7.9 | 6.6982 | 1 | 7.824 | 276 | 35.2761
7.7 | 6.4116 | 1 | 7.824 | 276 | 35.2761
7.9 | 6.6032 | 1 | 7.824 | 276 | 35.2761
8.3 | 6.9403 | 1 | 7.824 | 276 | 35.2761
8.6 | 7.2276 | 1 | 7.824 | 276 | 35.2761
9.1 | 7.7563 | 1 | 7.824 | 276 | 35.2761
9.3 | 8.1467 | 1 | 7.824 | 276 | 35.2761
9.6 | 8.3373 | 1 | 7.824 | 276 | 35.2761
9.9 | 8.6267 | 1 | 7.824 | 276 | 35.2761
10 | 8.8242 | 1 | 7.824 | 276 | 35.2761
10 | 8.9781 | 1 | 7.824 | 276 | 35.2761
10.1 | 9.0749 | 1 | 7.824 | 276 | 35.2761
9.9 | 8.88 | 1 | 7.824 | 276 | 35.2761
9.7 | 8.7369 | 1 | 7.824 | 276 | 35.2761
9.6 | 8.3349 | 1 | 7.824 | 276 | 35.2761
9.1 | 8.1523 | 1 | 7.824 | 276 | 35.2761
8.7 | 7.9645 | 1 | 7.824 | 276 | 35.2761
8.4 | 7.7211 | 1 | 7.824 | 276 | 35.2761
8.3 | 7.623 | 1 | 7.824 | 276 | 35.2761
8.2 | 7.6263 | 1 | 7.824 | 276 | 35.2761
8.3 | 7.827 | 1 | 7.824 | 276 | 35.2761
8.4 | 7.8228 | 1 | 7.824 | 276 | 35.2761
8.4 | 7.8225 | 1 | 7.824 | 276 | 35.2761
8.4 | 7.8739 | 1 | 7.824 | 276 | 35.2761
8.3 | 7.9304 | 1 | 7.824 | 276 | 35.2761
8.4 | 7.8739 | 1 | 7.824 | 276 | 35.2761
8.1 | 7.7843 | 1 | 7.824 | 276 | 35.2761
8 | 7.7371 | 1 | 7.824 | 276 | 35.2761
7.9 | 7.5861 | 1 | 7.824 | 276 | 35.2761
7.6 | 7.2377 | 1 | 7.824 | 276 | 35.2761
7.3 | 6.691 | 1 | 7.824 | 276 | 35.2761
7.3 | 6.6913 | 1 | 7.824 | 276 | 35.2761
7.8 | 6.7891 | 1 | 7.824 | 276 | 35.2761
8.1 | 6.6973 | 1 | 7.824 | 276 | 35.2761
8.4 | 6.7512 | 1 | 7.824 | 276 | 35.2761
8.6 | 5.9681 | 1 | 7.824 | 276 | 35.2761
10 | 6.8263 | 1 | 7.824 | 276 | 35.2761
10.1 | 5.2258 | 1 | 7.824 | 276 | 35.2761
10 | 5.2504 | 1 | 7.824 | 276 | 35.2761
10.3 | 5.8842 | 1 | 7.824 | 276 | 35.2761
8.9 | 5.2137 | 1 | 7.824 | 276 | 35.2761
8.6 | 5.4815 | 1 | 7.824 | 276 | 35.2761
7.4 | 4.7882 | 1 | 7.824 | 276 | 35.2761
6.6 | 4.4936 | 1 | 7.824 | 276 | 35.2761
6.5 | 4.4005 | 1 | 7.824 | 276 | 35.2761
5.9 | 4.0852 | 1 | 7.824 | 276 | 35.2761
5.8 | 3.9504 | 1 | 7.824 | 276 | 35.2761
5.2 | 3.6718 | 1 | 7.824 | 276 | 35.2761
5 | 3.5652 | 1 | 7.824 | 276 | 35.2761
4.7 | 3.3619 | 1 | 7.824 | 276 | 35.2761
4.4 | 3.3675 | 1 | 7.824 | 276 | 35.2761
4.2 | 3.3017 | 1 | 7.824 | 276 | 35.2761
4.3 | 3.3991 | 1 | 7.824 | 276 | 35.2761
4.8 | 3.6687 | 1 | 7.824 | 276 | 35.2761
5.1 | 4.001 | 1 | 7.824 | 276 | 35.2761
5.2 | 4.0974 | 1 | 7.824 | 276 | 35.2761
7.1 | 5.3473 | 1 | 7.824 | 276 | 35.2761
8.6 | 6.277 | 1 | 7.824 | 276 | 35.2761
10.3 | 6.985 | 1 | 7.824 | 276 | 35.2761
11.8 | 7.1583 | 1 | 7.824 | 276 | 35.2761
12.1 | 7.0058 | 1 | 7.824 | 276 | 35.2761
11.8 | 7.7434 | 1 | 7.824 | 276 | 35.2761
10.9 | 7.3531 | 1 | 7.824 | 276 | 35.2761
11 | 7.6097 | 1 | 7.824 | 276 | 35.2761
10 | 7.6637 | 1 | 7.824 | 276 | 35.2761
9.5 | 8.0911 | 1 | 7.824 | 276 | 35.2761
9.7 | 8.3328 | 1 | 7.824 | 276 | 35.2761
8.7 | 7.6159 | 1 | 7.824 | 276 | 35.2761
7.8 | 6.6497 | 1 | 7.824 | 276 | 35.2761
6.5 | 5.7664 | 1 | 7.824 | 276 | 35.2761
5.5 | 4.7898 | 1 | 7.824 | 276 | 35.2761
4.3 | 3.5742 | 1 | 7.824 | 276 | 35.2761
2.8 | 2.2367 | 1 | 7.824 | 276 | 35.2761
1.4 | 0.78061 | 1 | 7.824 | 276 | 35.2761
-0.3 | -0.83509 | 1 | 7.824 | 276 | 35.2761
-1.5 | -2.1541 | 1 | 7.824 | 276 | 35.2761
-1.8 | -2.3725 | 1 | 7.824 | 276 | 35.2761
-1.7 | -2.3836 | 1 | 7.824 | 276 | 35.2761
-1.4 | -2.1648 | 1 | 7.824 | 276 | 35.2761
-1 | -1.7419 | 1 | 7.824 | 276 | 35.2761
0.8 | -0.35149 | 1 | 7.824 | 276 | 35.2761
2.9 | 1.1526 | 1 | 7.824 | 276 | 35.2761
5.1 | 1.9974 | 1 | 7.824 | 276 | 35.2761
5.5 | 1.6482 | 1 | 7.824 | 276 | 35.2761
5.9 | 1.8451 | 1 | 7.824 | 276 | 35.2761
5.7 | 1.7309 | 1 | 7.824 | 276 | 35.2761
6.2 | 1.892 | 1 | 7.824 | 276 | 35.2761
5.5 | 1.2803 | 1 | 7.824 | 276 | 35.2761
5.2 | 1.3514 | 1 | 7.824 | 276 | 35.2761
4 | 0.81302 | 1 | 7.824 | 276 | 35.2761
3.6 | 0.64446 | 1 | 7.824 | 276 | 35.2761
3.2 | 0.61503 | 1 | 7.824 | 276 | 35.2761
2.1 | 0.18046 | 1 | 7.824 | 276 | 35.2761
0.8 | -0.92171 | 1 | 7.824 | 276 | 35.2761
-0.2 | -1.3714 | 1 | 7.824 | 276 | 35.2761
-1.1 | -2.2242 | 1 | 7.824 | 276 | 35.2761
-1.8 | -2.7218 | 1 | 7.824 | 276 | 35.2761
-2.8 | -3.6136 | 1 | 7.824 | 276 | 35.2761
-3.2 | -3.9333 | 1 | 7.824 | 276 | 35.2761
-3.2 | -4.0297 | 1 | 7.824 | 276 | 35.2761
-3.2 | -3.8019 | 1 | 7.824 | 276 | 35.2761
-2.6 | -3.3219 | 1 | 7.824 | 276 | 35.2761
-2.6 | -3.422 | 1 | 7.824 | 276 | 35.2761
-1.4 | -2.4085 | 1 | 7.824 | 276 | 35.2761
0.6 | -1.0057 | 1 | 7.824 | 276 | 35.2761
2.7 | -0.053105 | 1 | 7.824 | 276 | 35.2761
5 | 1.7648 | 1 | 7.824 | 276 | 35.2761
5.9 | 1.9407 | 1 | 7.824 | 276 | 35.2761
7.4 | 3.4212 | 1 | 7.824 | 276 | 35.2761
7.5 | 3.655 | 1 | 7.824 | 276 | 35.2761
8.5 | 4.0826 | 1 | 7.824 | 276 | 35.2761
8.3 | 3.867 | 1 | 7.824 | 276 | 35.2761
7.2 | 3.5627 | 1 | 7.824 | 276 | 35.2761
5.7 | 2.7389 | 1 | 7.824 | 276 | 35.2761
5.7 | 2.7389 | 1 | 7.824 | 276 | 35.2761
4.2 | 2.2606 | 1 | 7.824 | 276 | 35.2761
3.4 | 1.8076 | 1 | 7.824 | 276 | 35.2761
2.3 | 1.048 | 1 | 7.824 | 276 | 35.2761
1.4 | 0.43565 | 1 | 7.824 | 276 | 35.2761
1.7 | 0.7826 | 1 | 7.824 | 276 | 35.2761
0.9 | 0.31155 | 1 | 7.824 | 276 | 35.2761
0.5 | 0.030096 | 1 | 7.824 | 276 | 35.2761
0.8 | 0.20836 | 1 | 7.824 | 276 | 35.2761
-1.1 | -1.8035 | 1 | 7.824 | 276 | 35.2761
-0.4 | -0.93275 | 1 | 7.824 | 276 | 35.2761
-0.9 | -1.4594 | 1 | 7.824 | 276 | 35.2761
0.7 | -0.022042 | 1 | 7.824 | 276 | 35.2761
1.5 | 0.79509 | 1 | 7.824 | 276 | 35.2761
3.4 | 2.1699 | 1 | 7.824 | 276 | 35.2761
5.4 | 3.3943 | 1 | 7.824 | 276 | 35.2761
8.1 | 4.7584 | 1 | 7.824 | 276 | 35.2761
9.5 | 5.5191 | 1 | 7.824 | 276 | 35.2761
10.2 | 5.0321 | 1 | 7.824 | 276 | 35.2761
10.8 | 5.7782 | 1 | 7.824 | 276 | 35.2761
9.2 | 5.0693 | 1 | 7.824 | 276 | 35.2761
8.5 | 4.7069 | 1 | 7.824 | 276 | 35.2761
7.9 | 4.4299 | 1 | 7.824 | 276 | 35.2761
7.1 | 4.1894 | 1 | 7.824 | 276 | 35.2761
6.9 | 4.2338 | 1 | 7.824 | 276 | 35.2761
7 | 4.4393 | 1 | 7.824 | 276 | 35.2761
7.2 | 4.8611 | 1 | 7.824 | 276 | 35.2761
6.7 | 5.2341 | 1 | 7.824 | 276 | 35.2761
6.4 | 5.624 | 1 | 7.824 | 276 | 35.2761
6 | 5.5617 | 1 | 7.824 | 276 | 35.2761
6.3 | 5.8576 | 1 | 7.824 | 276 | 35.2761
6.5 | 6.0546 | 1 | 7.824 | 276 | 35.2761
6.5 | 6.2997 | 1 | 7.824 | 276 | 35.2761
6.6 | 6.3991 | 1 | 7.824 | 276 | 35.2761
6.6 | 6.3991 | 1 | 7.824 | 276 | 35.2761
6.5 | 6.3994 | 1 | 7.824 | 276 | 35.2761
6.6 | 6.4991 | 1 | 7.824 | 276 | 35.2761
7 | 6.6466 | 1 | 7.824 | 276 | 35.2761
7.6 | 7.2908 | 1 | 7.824 | 276 | 35.2761
8 | 7.4328 | 1 | 7.824 | 276 | 35.2761
8.6 | 7.6205 | 1 | 7.824 | 276 | 35.2761
9.1 | 7.7608 | 1 | 7.824 | 276 | 35.2761
9.9 | 8.1381 | 1 | 7.824 | 276 | 35.2761
9.9 | 8.0425 | 1 | 7.824 | 276 | 35.2761
9.9 | 8.1381 | 1 | 7.824 | 276 | 35.2761
9.9 | 8.0416 | 1 | 7.824 | 276 | 35.2761
10 | 8.1363 | 1 | 7.824 | 276 | 35.2761
9.8 | 7.8053 | 1 | 7.824 | 276 | 35.2761
8.7 | 7.2792 | 1 | 7.824 | 276 | 35.2761
8.6 | 7.2794 | 1 | 7.824 | 276 | 35.2761
8.3 | 7.1825 | 1 | 7.824 | 276 | 35.2761
8 | 7.1345 | 1 | 7.824 | 276 | 35.2761
7.8 | 6.891 | 1 | 7.824 | 276 | 35.2761
7.7 | 6.7937 | 1 | 7.824 | 276 | 35.2761
7.2 | 6.4028 | 1 | 7.824 | 276 | 35.2761
6.3 | 5.6183 | 1 | 7.824 | 276 | 35.2761
6 | 5.6566 | 1 | 7.824 | 276 | 35.2761
5.6 | 5.2609 | 1 | 7.824 | 276 | 35.2761
5.6 | 5.2609 | 1 | 7.824 | 276 | 35.2761
5.4 | 5.063 | 1 | 7.824 | 276 | 35.2761
5.1 | 4.7662 | 1 | 7.824 | 276 | 35.2761
5.7 | 5.36 | 1 | 7.824 | 276 | 35.2761
6.4 | 5.9553 | 1 | 7.824 | 276 | 35.2761
7.2 | 6.4028 | 1 | 7.824 | 276 | 35.2761
8.6 | 7.1367 | 1 | 7.824 | 276 | 35.2761
9.4 | 7.3821 | 1 | 7.824 | 276 | 35.2761
9.7 | 7.3894 | 1 | 7.824 | 276 | 35.2761
9.2 | 6.7469 | 1 | 7.824 | 276 | 35.2761
9.6 | 7.0296 | 1 | 7.824 | 276 | 35.2761
9.3 | 6.8384 | 1 | 7.824 | 276 | 35.2761
9 | 6.5604 | 1 | 7.824 | 276 | 35.2761
8.3 | 6.3026 | 1 | 7.824 | 276 | 35.2761
7.4 | 5.5004 | 1 | 7.824 | 276 | 35.2761
7 | 5.2097 | 1 | 7.824 | 276 | 35.2761
5.4 | 4.3783 | 1 | 7.824 | 276 | 35.2761
6.1 | 4.8765 | 1 | 7.824 | 276 | 35.2761
5.4 | 4.5113 | 1 | 7.824 | 276 | 35.2761
4.9 | 4.114 | 1 | 7.824 | 276 | 35.2761
4.2 | 3.4325 | 1 | 7.824 | 276 | 35.2761
4.7 | 3.9195 | 1 | 7.824 | 276 | 35.2761
4.4 | 3.7149 | 1 | 7.824 | 276 | 35.2761
4.8 | 4.017 | 1 | 7.824 | 276 | 35.2761
4.9 | 4.1144 | 1 | 7.824 | 276 | 35.2761
4.7 | 4.0084 | 1 | 7.824 | 276 | 35.2761
4.8 | 4.0174 | 1 | 7.824 | 276 | 35.2761
5 | 4.4375 | 1 | 7.824 | 276 | 35.2761
6 | 5.0049 | 1 | 7.824 | 276 | 35.2761
6.7 | 5.591 | 1 | 7.824 | 276 | 35.2761
6.8 | 5.9193 | 1 | 7.824 | 276 | 35.2761
7.1 | 6.1169 | 1 | 7.824 | 276 | 35.2761
7.6 | 6.1363 | 1 | 7.824 | 276 | 35.2761
8.9 | 7.0062 | 1 | 7.824 | 276 | 35.2761
9.5 | 6.7271 | 1 | 7.824 | 276 | 35.2761
7.1 | 5.2221 | 1 | 7.824 | 276 | 35.2761
8.1 | 5.7747 | 1 | 7.824 | 276 | 35.2761
6.4 | 5.1667 | 1 | 7.824 | 276 | 35.2761
6.3 | 4.9822 | 1 | 7.824 | 276 | 35.2761
5.5 | 4.3894 | 1 | 7.824 | 276 | 35.2761
6 | 4.3126 | 1 | 7.824 | 276 | 35.2761
5.5 | 4.0472 | 1 | 7.824 | 276 | 35.2761
5.5 | 4.0472 | 1 | 7.824 | 276 | 35.2761
5.3 | 3.9405 | 1 | 7.824 | 276 | 35.2761
4.1 | 3.4228 | 1 | 7.824 | 276 | 35.2761
4.9 | 3.9838 | 1 | 7.824 | 276 | 35.2761
4.5 | 3.8133 | 1 | 7.824 | 276 | 35.2761
4.4 | 3.8485 | 1 | 7.824 | 276 | 35.2761
4.7 | 4.0091 | 1 | 7.824 | 276 | 35.2761
4.8 | 4.1065 | 1 | 7.824 | 276 | 35.2761
4.5 | 3.9469 | 1 | 7.824 | 276 | 35.2761
5.3 | 4.5053 | 1 | 7.824 | 276 | 35.2761
6 | 5.0054 | 1 | 7.824 | 276 | 35.2761
6.5 | 4.9559 | 1 | 7.824 | 276 | 35.2761
7 | 5.0877 | 1 | 7.824 | 276 | 35.2761
7 | 5.0037 | 1 | 7.824 | 276 | 35.2761
4.7 | 3.9216 | 1 | 7.824 | 276 | 35.2761
5.6 | 4.4869 | 1 | 7.824 | 276 | 35.2761
6 | 4.5674 | 1 | 7.824 | 276 | 35.2761
7.5 | 5.0585 | 1 | 7.824 | 276 | 35.2761
5.3 | 3.8591 | 1 | 7.824 | 276 | 35.2761
5 | 3.6569 | 1 | 7.824 | 276 | 35.2761
4.8 | 3.4667 | 1 | 7.824 | 276 | 35.2761
4.4 | 3.1664 | 1 | 7.824 | 276 | 35.2761
3.7 | 2.8231 | 1 | 7.824 | 276 | 35.2761
3.1 | 2.4482 | 1 | 7.824 | 276 | 35.2761
2.9 | 2.2114 | 1 | 7.824 | 276 | 35.2761
2.3 | 1.8309 | 1 | 7.824 | 276 | 35.2761
3.1 | 2.5326 | 1 | 7.824 | 276 | 35.2761
3.3 | 2.7289 | 1 | 7.824 | 276 | 35.2761
3.5 | 3.0544 | 1 | 7.824 | 276 | 35.2761
3.8 | 3.2627 | 1 | 7.824 | 276 | 35.2761
3.8 | 2.6755 | 1 | 7.824 | 276 | 35.2761
3.6 | 2.484 | 1 | 7.824 | 276 | 35.2761
3.8 | 2.6761 | 1 | 7.824 | 276 | 35.2761
4.1 | 2.883 | 1 | 7.824 | 276 | 35.2761
5.1 | 3.7581 | 1 | 7.824 | 276 | 35.2761
6.3 | 4.3193 | 1 | 7.824 | 276 | 35.2761
6.7 | 4.0278 | 1 | 7.824 | 276 | 35.2761
7.3 | 4.4225 | 1 | 7.824 | 276 | 35.2761
7.7 | 4.2614 | 1 | 7.824 | 276 | 35.2761
8.1 | 4.7704 | 1 | 7.824 | 276 | 35.2761
8.4 | 4.964 | 1 | 7.824 | 276 | 35.2761
8.5 | 5.277 | 1 | 7.824 | 276 | 35.2761
8.6 | 5.2908 | 1 | 7.824 | 276 | 35.2761
7.5 | 4.4927 | 1 | 7.824 | 276 | 35.2761
6.7 | 4.4925 | 1 | 7.824 | 276 | 35.2761
5.8 | 3.5812 | 1 | 7.824 | 276 | 35.2761
6.1 | 3.2801 | 1 | 7.824 | 276 | 35.2761
5.7 | 2.9785 | 1 | 7.824 | 276 | 35.2761
5.7 | 2.9785 | 1 | 7.824 | 276 | 35.2761
5.3 | 2.6771 | 1 | 7.824 | 276 | 35.2761
5 | 2.753 | 1 | 7.824 | 276 | 35.2761
4.8 | 2.8052 | 1 | 7.824 | 276 | 35.2761
4.8 | 2.3961 | 1 | 7.824 | 276 | 35.2761
4.8 | 2.3961 | 1 | 7.824 | 276 | 35.2761
4.6 | 2.3239 | 1 | 7.824 | 276 | 35.2761
3.7 | 2.2654 | 1 | 7.824 | 276 | 35.2761
2.8 | 1.6772 | 1 | 7.824 | 276 | 35.2761
3.4 | 1.9371 | 1 | 7.824 | 276 | 35.2761
5.1 | 2.9702 | 1 | 7.824 | 276 | 35.2761
5.8 | 2.9925 | 1 | 7.824 | 276 | 35.2761
5.5 | 2.9066 | 1 | 7.824 | 276 | 35.2761
7.3 | 3.6962 | 1 | 7.824 | 276 | 35.2761
6.5 | 2.7095 | 1 | 7.824 | 276 | 35.2761
6.6 | 2.2038 | 1 | 7.824 | 276 | 35.2761
6.6 | 2.94 | 1 | 7.824 | 276 | 35.2761
6 | 2.2896 | 1 | 7.824 | 276 | 35.2761
5.8 | 2.1088 | 1 | 7.824 | 276 | 35.2761
5 | 1.6195 | 1 | 7.824 | 276 | 35.2761
4.5 | 1.2301 | 1 | 7.824 | 276 | 35.2761
4.1 | 0.79692 | 1 | 7.824 | 276 | 35.2761
3.9 | 1.0874 | 1 | 7.824 | 276 | 35.2761
3.4 | 1.1645 | 1 | 7.824 | 276 | 35.2761
2.9 | 1.0292 | 1 | 7.824 | 276 | 35.2761
2.1 | 0.68198 | 1 | 7.824 | 276 | 35.2761
2 | 0.83031 | 1 | 7.824 | 276 | 35.2761
1.4 | 0.43509 | 1 | 7.824 | 276 | 35.2761
1.4 | 0.563 | 1 | 7.824 | 276 | 35.2761
1.3 | 0.46066 | 1 | 7.824 | 276 | 35.2761
1.7 | 0.78155 | 1 | 7.824 | 276 | 35.2761
1.9 | 0.72846 | 1 | 7.824 | 276 | 35.2761
1.8 | 0.75438 | 1 | 7.824 | 276 | 35.2761
2.1 | 1.0578 | 1 | 7.824 | 276 | 35.2761
3 | 1.4921 | 1 | 7.824 | 276 | 35.2761
3.8 | 1.8659 | 1 | 7.824 | 276 | 35.2761
4.4 | 1.7351 | 1 | 7.824 | 276 | 35.2761
4.1 | 1.5261 | 1 | 7.824 | 276 | 35.2761
5 | 2 | 1 | 7.824 | 276 | 35.2761
4.2 | 1.771 | 1 | 7.824 | 276 | 35.2761
4.5 | 1.9413 | 1 | 7.824 | 276 | 35.2761
3.8 | 1.8627 | 1 | 7.824 | 276 | 35.2761
3.2 | 1.9773 | 1 | 7.824 | 276 | 35.2761
2.9 | 1.6463 | 1 | 7.824 | 276 | 35.2761
3.2 | 1.8605 | 1 | 7.824 | 276 | 35.2761
3.1 | 1.504 | 1 | 7.824 | 276 | 35.2761
2.9 | 1.5162 | 1 | 7.824 | 276 | 35.2761
2.7 | 1.5751 | 1 | 7.824 | 276 | 35.2761
2.7 | 1.4438 | 1 | 7.824 | 276 | 35.2761
2.5 | 1.3724 | 1 | 7.824 | 276 | 35.2761
2.3 | 1.2567 | 1 | 7.824 | 276 | 35.2761
2.2 | 1.2867 | 1 | 7.824 | 276 | 35.2761
2.1 | 1.1848 | 1 | 7.824 | 276 | 35.2761
2.1 | 1.1843 | 1 | 7.824 | 276 | 35.2761
2.2 | 1.2856 | 1 | 7.824 | 276 | 35.2761
2 | 1.2104 | 1 | 7.824 | 276 | 35.2761
2 | 1.3295 | 1 | 7.824 | 276 | 35.2761
2.3 | 1.6222 | 1 | 7.824 | 276 | 35.2761
3.5 | 2.3793 | 1 | 7.824 | 276 | 35.2761
4.7 | 2.7696 | 1 | 7.824 | 276 | 35.2761
6 | 2.9186 | 1 | 7.824 | 276 | 35.2761
5.3 | 2.301 | 1 | 7.824 | 276 | 35.2761
4.6 | 1.9064 | 1 | 7.824 | 276 | 35.2761
5 | 2.092 | 1 | 7.824 | 276 | 35.2761
4.5 | 1.5482 | 1 | 7.824 | 276 | 35.2761
4.1 | 1.5042 | 1 | 7.824 | 276 | 35.2761
3.6 | 1.1048 | 1 | 7.824 | 276 | 35.2761
3.3 | 1.1615 | 1 | 7.824 | 276 | 35.2761
2.9 | 0.73603 | 1 | 7.824 | 276 | 35.2761
3.2 | 0.94812 | 1 | 7.824 | 276 | 35.2761
3.3 | 1.0428 | 1 | 7.824 | 276 | 35.2761
2.3 | 1.1621 | 1 | 7.824 | 276 | 35.2761
1.4 | 0.8196 | 1 | 7.824 | 276 | 35.2761
1.1 | 0.76693 | 1 | 7.824 | 276 | 35.2761
0.9 | 0.69161 | 1 | 7.824 | 276 | 35.2761
0.5 | 0.24836 | 1 | 7.824 | 276 | 35.2761
0.3 | 0.1764 | 1 | 7.824 | 276 | 35.2761
0.5 | 0.37594 | 1 | 7.824 | 276 | 35.2761
0.9 | 0.56861 | 1 | 7.824 | 276 | 35.2761
0.6 | 0.35223 | 1 | 7.824 | 276 | 35.2761
1.2 | 0.86454 | 1 | 7.824 | 276 | 35.2761
1.9 | 1.348 | 1 | 7.824 | 276 | 35.2761
2.4 | 1.9647 | 1 | 7.824 | 276 | 35.2761
3 | 2.5552 | 1 | 7.824 | 276 | 35.2761
4.5 | 3.8067 | 1 | 7.824 | 276 | 35.2761
5.4 | 4.3702 | 1 | 7.824 | 276 | 35.2761
5.7 | 4.5704 | 1 | 7.824 | 276 | 35.2761
6.1 | 4.9559 | 1 | 7.824 | 276 | 35.2761
6.4 | 5.1546 | 1 | 7.824 | 276 | 35.2761
5.7 | 4.7952 | 1 | 7.824 | 276 | 35.2761
5.3 | 4.8668 | 1 | 7.824 | 276 | 35.2761
5.2 | 4.8625 | 1 | 7.824 | 276 | 35.2761
5.3 | 5.0571 | 1 | 7.824 | 276 | 35.2761
5.4 | 5.1563 | 1 | 7.824 | 276 | 35.2761
5.6 | 5.2583 | 1 | 7.824 | 276 | 35.2761
5.8 | 5.4561 | 1 | 7.824 | 276 | 35.2761
5.8 | 5.4561 | 1 | 7.824 | 276 | 35.2761
5.9 | 5.6524 | 1 | 7.824 | 276 | 35.2761
6.1 | 5.8508 | 1 | 7.824 | 276 | 35.2761
6.4 | 6.1984 | 1 | 7.824 | 276 | 35.2761
6.5 | 6.2978 | 1 | 7.824 | 276 | 35.2761
6.6 | 6.2477 | 1 | 7.824 | 276 | 35.2761
5 | 4.665 | 1 | 7.824 | 276 | 35.2761
4.4 | 3.8441 | 1 | 7.824 | 276 | 35.2761
4.4 | 3.8444 | 1 | 7.824 | 276 | 35.2761
5.4 | 4.7339 | 1 | 7.824 | 276 | 35.2761
6.8 | 5.7734 | 1 | 7.824 | 276 | 35.2761
8.2 | 6.5167 | 1 | 7.824 | 276 | 35.2761
9.7 | 6.8955 | 1 | 7.824 | 276 | 35.2761
10.9 | 7.348 | 1 | 7.824 | 276 | 35.2761
11.6 | 7.1631 | 1 | 7.824 | 276 | 35.2761
11.6 | 7.1631 | 1 | 7.824 | 276 | 35.2761
11.2 | 7.089 | 1 | 7.824 | 276 | 35.2761
11 | 7.1117 | 1 | 7.824 | 276 | 35.2761
10 | 6.6263 | 1 | 7.824 | 276 | 35.2761
9 | 6.5556 | 1 | 7.824 | 276 | 35.2761
9 | 6.5556 | 1 | 7.824 | 276 | 35.2761
7.9 | 6.2344 | 1 | 7.824 | 276 | 35.2761
7.6 | 6.0396 | 1 | 7.824 | 276 | 35.2761
7.9 | 6.0996 | 1 | 7.824 | 276 | 35.2761
8.5 | 6.7123 | 1 | 7.824 | 276 | 35.2761
8.2 | 6.7503 | 1 | 7.824 | 276 | 35.2761
8 | 6.9861 | 1 | 7.824 | 276 | 35.2761
7.6 | 7.0375 | 1 | 7.824 | 276 | 35.2761
7.9 | 7.3326 | 1 | 7.824 | 276 | 35.2761
8.3 | 7.6246 | 1 | 7.824 | 276 | 35.2761
8.3 | 7.8801 | 1 | 7.824 | 276 | 35.2761
9.1 | 8.2047 | 1 | 7.824 | 276 | 35.2761
9.3 | 8.3997 | 1 | 7.824 | 276 | 35.2761
9.8 | 8.5806 | 1 | 7.824 | 276 | 35.2761
9.6 | 8.4886 | 1 | 7.824 | 276 | 35.2761
9.7 | 8.4845 | 1 | 7.824 | 276 | 35.2761
10.1 | 8.6694 | 1 | 7.824 | 276 | 35.2761
10 | 8.8758 | 1 | 7.824 | 276 | 35.2761
9.9 | 9.1416 | 1 | 7.824 | 276 | 35.2761
9.8 | 9.1487 | 1 | 7.824 | 276 | 35.2761
10.2 | 9.542 | 1 | 7.824 | 276 | 35.2761
10.5 | 9.7294 | 1 | 7.824 | 276 | 35.2761
10.8 | 9.8095 | 1 | 7.824 | 276 | 35.2761
10.7 | 9.6068 | 1 | 7.824 | 276 | 35.2761
11 | 9.689 | 1 | 7.824 | 276 | 35.2761
10.9 | 9.593 | 1 | 7.824 | 276 | 35.2761
10.9 | 9.6976 | 1 | 7.824 | 276 | 35.2761
10.9 | 9.6976 | 1 | 7.824 | 276 | 35.2761
10.9 | 9.4912 | 1 | 7.824 | 276 | 35.2761
10 | 8.9295 | 1 | 7.824 | 276 | 35.2761
9.6 | 8.4912 | 1 | 7.824 | 276 | 35.2761
9.3 | 8.4027 | 1 | 7.824 | 276 | 35.2761
9.1 | 8.2077 | 1 | 7.824 | 276 | 35.2761
9.3 | 8.2014 | 1 | 7.824 | 276 | 35.2761
9.9 | 8.5813 | 1 | 7.824 | 276 | 35.2761
9.7 | 8.4884 | 1 | 7.824 | 276 | 35.2761
8.9 | 8.0135 | 1 | 7.824 | 276 | 35.2761
9.6 | 8.5944 | 1 | 7.824 | 276 | 35.2761
10.8 | 9.3478 | 1 | 7.824 | 276 | 35.2761
11 | 9.4383 | 1 | 7.824 | 276 | 35.2761
11.3 | 9.6755 | 1 | 7.824 | 276 | 35.2761
12.3 | 10.2205 | 1 | 7.824 | 276 | 35.2761
12 | 10.1389 | 1 | 7.824 | 276 | 35.2761
12.4 | 10.4169 | 1 | 7.824 | 276 | 35.2761
13.2 | 10.9175 | 1 | 7.824 | 276 | 35.2761
12.5 | 11.089 | 1 | 7.824 | 276 | 35.2761
12.4 | 11.2085 | 1 | 7.824 | 276 | 35.2761
12.3 | 11.1114 | 1 | 7.824 | 276 | 35.2761
12.1 | 11.0258 | 1 | 7.824 | 276 | 35.2761
11.9 | 10.9403 | 1 | 7.824 | 276 | 35.2761
12 | 11.0379 | 1 | 7.824 | 276 | 35.2761
11.7 | 10.9093 | 1 | 7.824 | 276 | 35.2761
11.3 | 10.7365 | 1 | 7.824 | 276 | 35.2761
11.1 | 10.6497 | 1 | 7.824 | 276 | 35.2761
11.4 | 10.7248 | 1 | 7.824 | 276 | 35.2761
11.4 | 10.6153 | 1 | 7.824 | 276 | 35.2761
11.3 | 10.6265 | 1 | 7.824 | 276 | 35.2761
11.3 | 10.6265 | 1 | 7.824 | 276 | 35.2761
11.1 | 10.5394 | 1 | 7.824 | 276 | 35.2761
11.3 | 10.6265 | 1 | 7.824 | 276 | 35.2761
11.7 | 10.9097 | 1 | 7.824 | 276 | 35.2761
12.2 | 11.1245 | 1 | 7.824 | 276 | 35.2761
12.5 | 11.307 | 1 | 7.824 | 276 | 35.2761
13.7 | 12.0838 | 1 | 7.824 | 276 | 35.2761
14.7 | 11.3124 | 1 | 7.824 | 276 | 35.2761
15.7 | 11.2161 | 1 | 7.824 | 276 | 35.2761
16.2 | 11.6131 | 1 | 7.824 | 276 | 35.2761
16.5 | 11.4629 | 1 | 7.824 | 276 | 35.2761
16.9 | 12.2318 | 1 | 7.824 | 276 | 35.2761
16.4 | 11.5093 | 1 | 7.824 | 276 | 35.2761
16.1 | 11.4283 | 1 | 7.824 | 276 | 35.2761
15 | 11.1953 | 1 | 7.824 | 276 | 35.2761
13.7 | 11.0822 | 1 | 7.824 | 276 | 35.2761
13.3 | 10.9105 | 1 | 7.824 | 276 | 35.2761
12.7 | 10.5998 | 1 | 7.824 | 276 | 35.2761
12.2 | 10.2271 | 1 | 7.824 | 276 | 35.2761
11.4 | 9.7705 | 1 | 7.824 | 276 | 35.2761
10.8 | 9.2467 | 1 | 7.824 | 276 | 35.2761
10.6 | 9.155 | 1 | 7.824 | 276 | 35.2761
8.6 | 7.8215 | 1 | 7.824 | 276 | 35.2761
9.2 | 8.105 | 1 | 7.824 | 276 | 35.2761
8.5 | 7.6236 | 1 | 7.824 | 276 | 35.2761
7.8 | 7.0393 | 1 | 7.824 | 276 | 35.2761
7.7 | 7.0397 | 1 | 7.824 | 276 | 35.2761
8.5 | 7.724 | 1 | 7.824 | 276 | 35.2761
8.3 | 7.8822 | 1 | 7.824 | 276 | 35.2761
9.8 | 9.1522 | 1 | 7.824 | 276 | 35.2761
11.3 | 10.1953 | 1 | 7.824 | 276 | 35.2761
12.6 | 10.8679 | 1 | 7.824 | 276 | 35.2761
12.9 | 11.0495 | 1 | 7.824 | 276 | 35.2761
13.1 | 10.9276 | 1 | 7.824 | 276 | 35.2761
14.3 | 11.3393 | 1 | 7.824 | 276 | 35.2761
14.3 | 11.1404 | 1 | 7.824 | 276 | 35.2761
13.7 | 10.6369 | 1 | 7.824 | 276 | 35.2761
13.7 | 9.7955 | 1 | 7.824 | 276 | 35.2761
12.7 | 9.2997 | 1 | 7.824 | 276 | 35.2761
12 | 8.9358 | 1 | 7.824 | 276 | 35.2761
11.5 | 8.6592 | 1 | 7.824 | 276 | 35.2761
10.5 | 8.0537 | 1 | 7.824 | 276 | 35.2761
10.3 | 8.0049 | 1 | 7.824 | 276 | 35.2761
9.2 | 8.3076 | 1 | 7.824 | 276 | 35.2761
8.1 | 7.9948 | 1 | 7.824 | 276 | 35.2761
7.9 | 7.7954 | 1 | 7.824 | 276 | 35.2761
7.9 | 7.7954 | 1 | 7.824 | 276 | 35.2761
7.7 | 7.7 | 1 | 7.824 | 276 | 35.2761
8 | 7.895 | 1 | 7.824 | 276 | 35.2761
7.7 | 7.7 | 1 | 7.824 | 276 | 35.2761
7.9 | 7.7952 | 1 | 7.824 | 276 | 35.2761
8.6 | 8.3872 | 1 | 7.824 | 276 | 35.2761
8.9 | 8.4743 | 1 | 7.824 | 276 | 35.2761
9.4 | 8.7581 | 1 | 7.824 | 276 | 35.2761
10.4 | 9.4225 | 1 | 7.824 | 276 | 35.2761
11.3 | 9.981 | 1 | 7.824 | 276 | 35.2761
12.7 | 10.4913 | 1 | 7.824 | 276 | 35.2761
12.4 | 10.2074 | 1 | 7.824 | 276 | 35.2761
11.8 | 10.0451 | 1 | 7.824 | 276 | 35.2761
13.8 | 9.1703 | 1 | 7.824 | 276 | 35.2761
12.7 | 7.9321 | 1 | 7.824 | 276 | 35.2761
11.6 | 8.0694 | 1 | 7.824 | 276 | 35.2761
10.2 | 8.6663 | 1 | 7.824 | 276 | 35.2761
8.7 | 6.9042 | 1 | 7.824 | 276 | 35.2761
8.8 | 6.6828 | 1 | 7.824 | 276 | 35.2761
9 | 7.3291 | 1 | 7.824 | 276 | 35.2761
8.9 | 6.9115 | 1 | 7.824 | 276 | 35.2761
8.4 | 6.5297 | 1 | 7.824 | 276 | 35.2761
8.1 | 6.4276 | 1 | 7.824 | 276 | 35.2761
8 | 6.4228 | 1 | 7.824 | 276 | 35.2761
7.8 | 6.3697 | 1 | 7.824 | 276 | 35.2761
7.7 | 6.3657 | 1 | 7.824 | 276 | 35.2761
8 | 6.653 | 1 | 7.824 | 276 | 35.2761
8.9 | 6.9989 | 1 | 7.824 | 276 | 35.2761
9.3 | 7.2831 | 1 | 7.824 | 276 | 35.2761
9.1 | 7.7557 | 1 | 7.824 | 276 | 35.2761
9.4 | 8.1918 | 1 | 7.824 | 276 | 35.2761
9.5 | 8.5922 | 1 | 7.824 | 276 | 35.2761
10.1 | 9.229 | 1 | 7.824 | 276 | 35.2761
11.1 | 9.7797 | 1 | 7.824 | 276 | 35.2761
11.3 | 10.2926 | 1 | 7.824 | 276 | 35.2761
12.3 | 11.1566 | 1 | 7.824 | 276 | 35.2761
11.4 | 9.86 | 1 | 7.824 | 276 | 35.2761
12.2 | 8.862 | 1 | 7.824 | 276 | 35.2761
11.8 | 8.0198 | 1 | 7.824 | 276 | 35.2761
11.1 | 7.7778 | 1 | 7.824 | 276 | 35.2761
10.4 | 7.6232 | 1 | 7.824 | 276 | 35.2761
9 | 6.8619 | 1 | 7.824 | 276 | 35.2761
8.7 | 6.363 | 1 | 7.824 | 276 | 35.2761
8.2 | 6.0721 | 1 | 7.824 | 276 | 35.2761
8.4 | 6.3916 | 1 | 7.824 | 276 | 35.2761
8.2 | 6.2926 | 1 | 7.824 | 276 | 35.2761
8 | 6.1923 | 1 | 7.824 | 276 | 35.2761
8.3 | 6.2957 | 1 | 7.824 | 276 | 35.2761
8.7 | 6.8981 | 1 | 7.824 | 276 | 35.2761
8.9 | 8.1093 | 1 | 7.824 | 276 | 35.2761
9.7 | 9.2624 | 1 | 7.824 | 276 | 35.2761
10.7 | 10.2506 | 1 | 7.824 | 276 | 35.2761
11.3 | 10.7319 | 1 | 7.824 | 276 | 35.2761
11.8 | 11.1127 | 1 | 7.824 | 276 | 35.2761
12.1 | 11.0175 | 1 | 7.824 | 276 | 35.2761
12.5 | 11.0781 | 1 | 7.824 | 276 | 35.2761
12.5 | 11.0775 | 1 | 7.824 | 276 | 35.2761
12.9 | 11.4629 | 1 | 7.824 | 276 | 35.2761
13.1 | 11.5456 | 1 | 7.824 | 276 | 35.2761
13.4 | 11.724 | 1 | 7.824 | 276 | 35.2761
13.8 | 12.1625 | 1 | 7.824 | 276 | 35.2761
13.2 | 11.9727 | 1 | 7.824 | 276 | 35.2761
13 | 11.6673 | 1 | 7.824 | 276 | 35.2761
13.3 | 9.5274 | 1 | 7.824 | 276 | 35.2761
11.8 | 8.0091 | 1 | 7.824 | 276 | 35.2761
10.8 | 6.9964 | 1 | 7.824 | 276 | 35.2761
10.2 | 6.8307 | 1 | 7.824 | 276 | 35.2761
9.1 | 6.5057 | 1 | 7.824 | 276 | 35.2761
8.4 | 5.9463 | 1 | 7.824 | 276 | 35.2761
8.1 | 5.7536 | 1 | 7.824 | 276 | 35.2761
8 | 5.6185 | 1 | 7.824 | 276 | 35.2761
7.7 | 5.2164 | 1 | 7.824 | 276 | 35.2761
7.6 | 5.3318 | 1 | 7.824 | 276 | 35.2761
7.1 | 4.9494 | 1 | 7.824 | 276 | 35.2761
6.5 | 4.4738 | 1 | 7.824 | 276 | 35.2761
6.7 | 4.6596 | 1 | 7.824 | 276 | 35.2761
6.6 | 4.5661 | 1 | 7.824 | 276 | 35.2761
7.2 | 5.0426 | 1 | 7.824 | 276 | 35.2761
8.5 | 5.7848 | 1 | 7.824 | 276 | 35.2761
9.5 | 6.7012 | 1 | 7.824 | 276 | 35.2761
10.4 | 6.7235 | 1 | 7.824 | 276 | 35.2761
9.2 | 7.6519 | 1 | 7.824 | 276 | 35.2761
10.5 | 7.1443 | 1 | 7.824 | 276 | 35.2761
10.6 | 7.4898 | 1 | 7.824 | 276 | 35.2761
11.9 | 7.6453 | 1 | 7.824 | 276 | 35.2761
11.7 | 7.1169 | 1 | 7.824 | 276 | 35.2761
8.6 | 6.2608 | 1 | 7.824 | 276 | 35.2761
9.9 | 6.5624 | 1 | 7.824 | 276 | 35.2761
9.3 | 5.9428 | 1 | 7.824 | 276 | 35.2761
8.9 | 6.1121 | 1 | 7.824 | 276 | 35.2761
8.2 | 5.8475 | 1 | 7.824 | 276 | 35.2761
7.7 | 5.6827 | 1 | 7.824 | 276 | 35.2761
7.7 | 5.5533 | 1 | 7.824 | 276 | 35.2761
6.8 | 5.0973 | 1 | 7.824 | 276 | 35.2761
6.1 | 4.8689 | 1 | 7.824 | 276 | 35.2761
6.7 | 5.2221 | 1 | 7.824 | 276 | 35.2761
5.6 | 4.477 | 1 | 7.824 | 276 | 35.2761
5.2 | 4.179 | 1 | 7.824 | 276 | 35.2761
3.9 | 3.3535 | 1 | 7.824 | 276 | 35.2761
4 | 3.32 | 1 | 7.824 | 276 | 35.2761
3.4 | 2.8197 | 1 | 7.824 | 276 | 35.2761
4.3 | 3.5253 | 1 | 7.824 | 276 | 35.2761
6 | 4.643 | 1 | 7.824 | 276 | 35.2761
8.1 | 5.7619 | 1 | 7.824 | 276 | 35.2761
8.8 | 5.7835 | 1 | 7.824 | 276 | 35.2761
9.1 | 5.6196 | 1 | 7.824 | 276 | 35.2761
8.6 | 5.3658 | 1 | 7.824 | 276 | 35.2761
7.4 | 5.7136 | 1 | 7.824 | 276 | 35.2761
8.4 | 6.5251 | 1 | 7.824 | 276 | 35.2761
9.6 | 6.0278 | 1 | 7.824 | 276 | 35.2761
8 | 5.7552 | 1 | 7.824 | 276 | 35.2761
8.7 | 5.5749 | 1 | 7.824 | 276 | 35.2761
7.9 | 4.5176 | 1 | 7.824 | 276 | 35.2761
6.8 | 4.2041 | 1 | 7.824 | 276 | 35.2761
5.2 | 3.5085 | 1 | 7.824 | 276 | 35.2761
4.1 | 2.7487 | 1 | 7.824 | 276 | 35.2761
4.5 | 3.0488 | 1 | 7.824 | 276 | 35.2761
3.6 | 2.4723 | 1 | 7.824 | 276 | 35.2761
3.9 | 2.5581 | 1 | 7.824 | 276 | 35.2761
3.5 | 2.256 | 1 | 7.824 | 276 | 35.2761
3.6 | 2.4723 | 1 | 7.824 | 276 | 35.2761
3.6 | 2.4723 | 1 | 7.824 | 276 | 35.2761
3.3 | 2.3873 | 1 | 7.824 | 276 | 35.2761
3.3 | 2.5118 | 1 | 7.824 | 276 | 35.2761
3.5 | 2.8337 | 1 | 7.824 | 276 | 35.2761
4.7 | 3.5713 | 1 | 7.824 | 276 | 35.2761
5.4 | 4.159 | 1 | 7.824 | 276 | 35.2761
5.8 | 4.4559 | 1 | 7.824 | 276 | 35.2761
7.4 | 5.3699 | 1 | 7.824 | 276 | 35.2761
6.8 | 4.6843 | 1 | 7.824 | 276 | 35.2761
8.7 | 5.7004 | 1 | 7.824 | 276 | 35.2761
6.2 | 5.0605 | 1 | 7.824 | 276 | 35.2761
8.5 | 6.0535 | 1 | 7.824 | 276 | 35.2761
6.6 | 4.5809 | 1 | 7.824 | 276 | 35.2761
6.1 | 4.4017 | 1 | 7.824 | 276 | 35.2761
6.7 | 4.5922 | 1 | 7.824 | 276 | 35.2761
6.9 | 4.4166 | 1 | 7.824 | 276 | 35.2761
5.5 | 4.0434 | 1 | 7.824 | 276 | 35.2761
5.1 | 3.8732 | 1 | 7.824 | 276 | 35.2761
4.5 | 3.594 | 1 | 7.824 | 276 | 35.2761
4.4 | 3.3698 | 1 | 7.824 | 276 | 35.2761
4.3 | 3.2732 | 1 | 7.824 | 276 | 35.2761
4.2 | 3.4325 | 1 | 7.824 | 276 | 35.2761
3.8 | 3.0007 | 1 | 7.824 | 276 | 35.2761
4.4 | 3.6277 | 1 | 7.824 | 276 | 35.2761
4.6 | 3.9107 | 1 | 7.824 | 276 | 35.2761
4.5 | 3.595 | 1 | 7.824 | 276 | 35.2761
4.3 | 3.4016 | 1 | 7.824 | 276 | 35.2761
4.8 | 3.8869 | 1 | 7.824 | 276 | 35.2761
5.3 | 4.1966 | 1 | 7.824 | 276 | 35.2761
5.7 | 4.3652 | 1 | 7.824 | 276 | 35.2761
6.2 | 4.7574 | 1 | 7.824 | 276 | 35.2761
6.9 | 4.9938 | 1 | 7.824 | 276 | 35.2761
7.5 | 4.937 | 1 | 7.824 | 276 | 35.2761
8.5 | 5.7317 | 1 | 7.824 | 276 | 35.2761
8.7 | 6.6843 | 1 | 7.824 | 276 | 35.2761
6.8 | 5.112 | 1 | 7.824 | 276 | 35.2761
6.6 | 4.5883 | 1 | 7.824 | 276 | 35.2761
6.1 | 4.9682 | 1 | 7.824 | 276 | 35.2761
6.6 | 5.0525 | 1 | 7.824 | 276 | 35.2761
5.7 | 4.2391 | 1 | 7.824 | 276 | 35.2761
5.5 | 4.0487 | 1 | 7.824 | 276 | 35.2761
5 | 3.7818 | 1 | 7.824 | 276 | 35.2761
3.9 | 3.2285 | 1 | 7.824 | 276 | 35.2761
3.5 | 2.8376 | 1 | 7.824 | 276 | 35.2761
3 | 2.5606 | 1 | 7.824 | 276 | 35.2761
2.8 | 2.2367 | 1 | 7.824 | 276 | 35.2761
1.9 | 1.3546 | 1 | 7.824 | 276 | 35.2761
1.4 | 0.82393 | 1 | 7.824 | 276 | 35.2761
1.6 | 1.0202 | 1 | 7.824 | 276 | 35.2761
0.3 | -0.21042 | 1 | 7.824 | 276 | 35.2761
1 | 0.67045 | 1 | 7.824 | 276 | 35.2761
1.3 | 0.72014 | 1 | 7.824 | 276 | 35.2761
2.5 | 1.6964 | 1 | 7.824 | 276 | 35.2761
3.2 | 2.4171 | 1 | 7.824 | 276 | 35.2761
3.9 | 3.098 | 1 | 7.824 | 276 | 35.2761
4.1 | 3.5537 | 1 | 7.824 | 276 | 35.2761
4.8 | 3.8859 | 1 | 7.824 | 276 | 35.2761
6.7 | 5.0148 | 1 | 7.824 | 276 | 35.2761
8.3 | 5.6247 | 1 | 7.824 | 276 | 35.2761
8.2 | 4.8336 | 1 | 7.824 | 276 | 35.2761
7.2 | 4.6171 | 1 | 7.824 | 276 | 35.2761
7.9 | 4.6773 | 1 | 7.824 | 276 | 35.2761
7.4 | 4.3792 | 1 | 7.824 | 276 | 35.2761
6.6 | 4.2634 | 1 | 7.824 | 276 | 35.2761
6.3 | 4.0661 | 1 | 7.824 | 276 | 35.2761
5.9 | 4.0947 | 1 | 7.824 | 276 | 35.2761
5.8 | 4.1245 | 1 | 7.824 | 276 | 35.2761
5.3 | 3.6118 | 1 | 7.824 | 276 | 35.2761
4.2 | 2.9729 | 1 | 7.824 | 276 | 35.2761
3.4 | 2.6134 | 1 | 7.824 | 276 | 35.2761
3 | 2.307 | 1 | 7.824 | 276 | 35.2761
2.7 | 1.9734 | 1 | 7.824 | 276 | 35.2761
2.1 | 1.6327 | 1 | 7.824 | 276 | 35.2761
1.6 | 1.3882 | 1 | 7.824 | 276 | 35.2761
2.1 | 1.7575 | 1 | 7.824 | 276 | 35.2761
2.1 | 1.7575 | 1 | 7.824 | 276 | 35.2761
2.6 | 2.1664 | 1 | 7.824 | 276 | 35.2761
4.4 | 3.5 | 1 | 7.824 | 276 | 35.2761
5.1 | 3.6268 | 1 | 7.824 | 276 | 35.2761
6.9 | 4.5452 | 1 | 7.824 | 276 | 35.2761
6.7 | 3.9018 | 1 | 7.824 | 276 | 35.2761
8 | 4.5532 | 1 | 7.824 | 276 | 35.2761
8.2 | 4.7305 | 1 | 7.824 | 276 | 35.2761
8.3 | 5.0026 | 1 | 7.824 | 276 | 35.2761
8.3 | 4.7446 | 1 | 7.824 | 276 | 35.2761
9.2 | 5.063 | 1 | 7.824 | 276 | 35.2761
8.7 | 4.4171 | 1 | 7.824 | 276 | 35.2761
8.2 | 4.5018 | 1 | 7.824 | 276 | 35.2761
7.7 | 4.5742 | 1 | 7.824 | 276 | 35.2761
7.4 | 4.6066 | 1 | 7.824 | 276 | 35.2761
7.3 | 4.7495 | 1 | 7.824 | 276 | 35.2761
6.8 | 4.6898 | 1 | 7.824 | 276 | 35.2761
6.8 | 4.6887 | 1 | 7.824 | 276 | 35.2761
6.5 | 4.6143 | 1 | 7.824 | 276 | 35.2761
6.1 | 4.6583 | 1 | 7.824 | 276 | 35.2761
5.9 | 4.7726 | 1 | 7.824 | 276 | 35.2761
5.7 | 4.7123 | 1 | 7.824 | 276 | 35.2761
5.2 | 4.8651 | 1 | 7.824 | 276 | 35.2761
5.2 | 5.1032 | 1 | 7.824 | 276 | 35.2761
5.3 | 5.2029 | 1 | 7.824 | 276 | 35.2761
5.6 | 5.2609 | 1 | 7.824 | 276 | 35.2761
5.6 | 5.3566 | 1 | 7.824 | 276 | 35.2761
5.9 | 5.4619 | 1 | 7.824 | 276 | 35.2761
6.8 | 6.1554 | 1 | 7.824 | 276 | 35.2761
6.8 | 6.2521 | 1 | 7.824 | 276 | 35.2761
7.3 | 6.404 | 1 | 7.824 | 276 | 35.2761
7.5 | 6.7435 | 1 | 7.824 | 276 | 35.2761
7.7 | 6.6965 | 1 | 7.824 | 276 | 35.2761
8.2 | 7.1811 | 1 | 7.824 | 276 | 35.2761
8 | 6.9871 | 1 | 7.824 | 276 | 35.2761
8.1 | 6.7496 | 1 | 7.824 | 276 | 35.2761
8.1 | 6.8917 | 1 | 7.824 | 276 | 35.2761
7.8 | 6.7935 | 1 | 7.824 | 276 | 35.2761
7.7 | 6.7928 | 1 | 7.824 | 276 | 35.2761
7.5 | 6.7435 | 1 | 7.824 | 276 | 35.2761
7.5 | 6.7435 | 1 | 7.824 | 276 | 35.2761
7.3 | 6.6453 | 1 | 7.824 | 276 | 35.2761
7.1 | 6.4492 | 1 | 7.824 | 276 | 35.2761
6.9 | 6.2531 | 1 | 7.824 | 276 | 35.2761
6.8 | 6.1551 | 1 | 7.824 | 276 | 35.2761
6.7 | 6.1535 | 1 | 7.824 | 276 | 35.2761
6.6 | 6.1522 | 1 | 7.824 | 276 | 35.2761
6.8 | 6.2518 | 1 | 7.824 | 276 | 35.2761
6.7 | 6.2508 | 1 | 7.824 | 276 | 35.2761
7.1 | 6.4492 | 1 | 7.824 | 276 | 35.2761
7.4 | 6.5972 | 1 | 7.824 | 276 | 35.2761
7.6 | 7.0389 | 1 | 7.824 | 276 | 35.2761
8.3 | 7.2791 | 1 | 7.824 | 276 | 35.2761
9.1 | 7.5666 | 1 | 7.824 | 276 | 35.2761
9.5 | 7.7099 | 1 | 7.824 | 276 | 35.2761
10 | 8.1363 | 1 | 7.824 | 276 | 35.2761
9.5 | 7.8527 | 1 | 7.824 | 276 | 35.2761
9.7 | 7.9473 | 1 | 7.824 | 276 | 35.2761
9.2 | 7.4253 | 1 | 7.824 | 276 | 35.2761
9.2 | 7.4261 | 1 | 7.824 | 276 | 35.2761
9.1 | 7.3313 | 1 | 7.824 | 276 | 35.2761
8.9 | 7.2348 | 1 | 7.824 | 276 | 35.2761
8.7 | 7.1388 | 1 | 7.824 | 276 | 35.2761
8.7 | 7.1388 | 1 | 7.824 | 276 | 35.2761
8.7 | 7.1395 | 1 | 7.824 | 276 | 35.2761
8.2 | 6.7553 | 1 | 7.824 | 276 | 35.2761
7.7 | 6.462 | 1 | 7.824 | 276 | 35.2761
7.4 | 6.2663 | 1 | 7.824 | 276 | 35.2761
7.3 | 6.3104 | 1 | 7.824 | 276 | 35.2761
7.1 | 6.2108 | 1 | 7.824 | 276 | 35.2761
6.9 | 6.1108 | 1 | 7.824 | 276 | 35.2761
7.2 | 6.4036 | 1 | 7.824 | 276 | 35.2761
7.3 | 6.4058 | 1 | 7.824 | 276 | 35.2761
7.8 | 6.796 | 1 | 7.824 | 276 | 35.2761
8 | 6.99 | 1 | 7.824 | 276 | 35.2761
8.9 | 7.6673 | 1 | 7.824 | 276 | 35.2761
9.7 | 8.1438 | 1 | 7.824 | 276 | 35.2761
10.4 | 8.4236 | 1 | 7.824 | 276 | 35.2761
11.2 | 8.7945 | 1 | 7.824 | 276 | 35.2761
12.3 | 7.9941 | 1 | 7.824 | 276 | 35.2761
13.6 | 8.1791 | 1 | 7.824 | 276 | 35.2761
12.1 | 7.464 | 1 | 7.824 | 276 | 35.2761
12.3 | 7.6368 | 1 | 7.824 | 276 | 35.2761
12.1 | 7.35 | 1 | 7.824 | 276 | 35.2761
11.3 | 6.962 | 1 | 7.824 | 276 | 35.2761
9 | 5.5498 | 1 | 7.824 | 276 | 35.2761
7.8 | 4.8939 | 1 | 7.824 | 276 | 35.2761
8.4 | 5.166 | 1 | 7.824 | 276 | 35.2761
7.7 | 4.9197 | 1 | 7.824 | 276 | 35.2761
6.2 | 4.1721 | 1 | 7.824 | 276 | 35.2761
5.9 | 4.0938 | 1 | 7.824 | 276 | 35.2761
5.8 | 4.3313 | 1 | 7.824 | 276 | 35.2761
6 | 5.0039 | 1 | 7.824 | 276 | 35.2761
5.7 | 4.9394 | 1 | 7.824 | 276 | 35.2761
5.6 | 5.0257 | 1 | 7.824 | 276 | 35.2761
5.3 | 4.7312 | 1 | 7.824 | 276 | 35.2761
4.9 | 4.4298 | 1 | 7.824 | 276 | 35.2761
5.3 | 4.8703 | 1 | 7.824 | 276 | 35.2761
7.5 | 6.1751 | 1 | 7.824 | 276 | 35.2761
9.9 | 7.3511 | 1 | 7.824 | 276 | 35.2761
11.4 | 7.7642 | 1 | 7.824 | 276 | 35.2761
13.1 | 8.2399 | 1 | 7.824 | 276 | 35.2761
14.1 | 7.9986 | 1 | 7.824 | 276 | 35.2761
14.6 | 8.1954 | 1 | 7.824 | 276 | 35.2761
15 | 8.0091 | 1 | 7.824 | 276 | 35.2761
15.1 | 7.737 | 1 | 7.824 | 276 | 35.2761
14.2 | 7.1671 | 1 | 7.824 | 276 | 35.2761
12.9 | 6.2549 | 1 | 7.824 | 276 | 35.2761
12.1 | 6.7497 | 1 | 7.824 | 276 | 35.2761
10.8 | 6.4332 | 1 | 7.824 | 276 | 35.2761
9.9 | 6.454 | 1 | 7.824 | 276 | 35.2761
9.4 | 6.3701 | 1 | 7.824 | 276 | 35.2761
8.7 | 6.363 | 1 | 7.824 | 276 | 35.2761
8.2 | 6.2018 | 1 | 7.824 | 276 | 35.2761
8 | 6.1013 | 1 | 7.824 | 276 | 35.2761
7 | 5.5544 | 1 | 7.824 | 276 | 35.2761
6.4 | 5.1591 | 1 | 7.824 | 276 | 35.2761
6.3 | 5.0624 | 1 | 7.824 | 276 | 35.2761
6.1 | 4.9595 | 1 | 7.824 | 276 | 35.2761
5.8 | 4.8947 | 1 | 7.824 | 276 | 35.2761
5.9 | 4.9918 | 1 | 7.824 | 276 | 35.2761
7.3 | 5.9772 | 1 | 7.824 | 276 | 35.2761
9.2 | 7.1841 | 1 | 7.824 | 276 | 35.2761
12.1 | 8.5499 | 1 | 7.824 | 276 | 35.2761
14.2 | 9.6753 | 1 | 7.824 | 276 | 35.2761
15.9 | 10.8093 | 1 | 7.824 | 276 | 35.2761
17.7 | 11.656 | 1 | 7.824 | 276 | 35.2761
18.5 | 11.3596 | 1 | 7.824 | 276 | 35.2761
19.3 | 11.3817 | 1 | 7.824 | 276 | 35.2761
17.3 | 10.2227 | 1 | 7.824 | 276 | 35.2761
17.1 | 10.25 | 1 | 7.824 | 276 | 35.2761
16.6 | 10.0703 | 1 | 7.824 | 276 | 35.2761
15.7 | 10.2029 | 1 | 7.824 | 276 | 35.2761
15 | 9.8961 | 1 | 7.824 | 276 | 35.2761
13.2 | 9.4897 | 1 | 7.824 | 276 | 35.2761
11.5 | 8.8131 | 1 | 7.824 | 276 | 35.2761
9.8 | 7.7401 | 1 | 7.824 | 276 | 35.2761
7.8 | 6.3555 | 1 | 7.824 | 276 | 35.2761
7.1 | 5.776 | 1 | 7.824 | 276 | 35.2761
6.7 | 5.4822 | 1 | 7.824 | 276 | 35.2761
5.9 | 4.9833 | 1 | 7.824 | 276 | 35.2761
4.8 | 4.1394 | 1 | 7.824 | 276 | 35.2761
3.5 | 3.043 | 1 | 7.824 | 276 | 35.2761
2.1 | 1.8795 | 1 | 7.824 | 276 | 35.2761
2 | 1.7803 | 1 | 7.824 | 276 | 35.2761
4.6 | 4.0344 | 1 | 7.824 | 276 | 35.2761
7 | 5.8607 | 1 | 7.824 | 276 | 35.2761
8.5 | 6.5961 | 1 | 7.824 | 276 | 35.2761
9.5 | 6.4651 | 1 | 7.824 | 276 | 35.2761
10.8 | 6.9684 | 1 | 7.824 | 276 | 35.2761
10.2 | 6.3565 | 1 | 7.824 | 276 | 35.2761
10.6 | 6.5513 | 1 | 7.824 | 276 | 35.2761
11.1 | 6.1245 | 1 | 7.824 | 276 | 35.2761
11.8 | 5.734 | 1 | 7.824 | 276 | 35.2761
10.9 | 5.1414 | 1 | 7.824 | 276 | 35.2761
10.3 | 5.1611 | 1 | 7.824 | 276 | 35.2761
9.2 | 4.8697 | 1 | 7.824 | 276 | 35.2761
8.3 | 4.6792 | 1 | 7.824 | 276 | 35.2761
7.5 | 4.8887 | 1 | 7.824 | 276 | 35.2761
5.3 | 3.4563 | 1 | 7.824 | 276 | 35.2761
6.4 | 4.1179 | 1 | 7.824 | 276 | 35.2761
7.3 | 4.7053 | 1 | 7.824 | 276 | 35.2761
6.5 | 4.3326 | 1 | 7.824 | 276 | 35.2761
7 | 4.156 | 1 | 7.824 | 276 | 35.2761
6.8 | 4.2865 | 1 | 7.824 | 276 | 35.2761
5.7 | 3.5887 | 1 | 7.824 | 276 | 35.2761
4.7 | 2.973 | 1 | 7.824 | 276 | 35.2761
4.7 | 3.218 | 1 | 7.824 | 276 | 35.2761
4.8 | 3.7821 | 1 | 7.824 | 276 | 35.2761
5 | 3.844 | 1 | 7.824 | 276 | 35.2761
5.3 | 3.8312 | 1 | 7.824 | 276 | 35.2761
5.5 | 3.8953 | 1 | 7.824 | 276 | 35.2761
6.6 | 4.7646 | 1 | 7.824 | 276 | 35.2761
7.4 | 5.132 | 1 | 7.824 | 276 | 35.2761
7.9 | 5.4271 | 1 | 7.824 | 276 | 35.2761
8.1 | 5.2821 | 1 | 7.824 | 276 | 35.2761
7.9 | 5.0597 | 1 | 7.824 | 276 | 35.2761
8.3 | 5.3445 | 1 | 7.824 | 276 | 35.2761
8.6 | 5.5359 | 1 | 7.824 | 276 | 35.2761
9 | 5.0517 | 1 | 7.824 | 276 | 35.2761
7.9 | 5.4321 | 1 | 7.824 | 276 | 35.2761
7 | 5.3217 | 1 | 7.824 | 276 | 35.2761
6.6 | 5.3436 | 1 | 7.824 | 276 | 35.2761
5.9 | 4.7608 | 1 | 7.824 | 276 | 35.2761
5.6 | 4.3403 | 1 | 7.824 | 276 | 35.2761
5.5 | 4.245 | 1 | 7.824 | 276 | 35.2761
5.1 | 3.9476 | 1 | 7.824 | 276 | 35.2761
4.7 | 3.5634 | 1 | 7.824 | 276 | 35.2761
4.4 | 3.2747 | 1 | 7.824 | 276 | 35.2761
4 | 2.849 | 1 | 7.824 | 276 | 35.2761
4 | 2.9742 | 1 | 7.824 | 276 | 35.2761
4.1 | 2.8623 | 1 | 7.824 | 276 | 35.2761
3.9 | 2.6715 | 1 | 7.824 | 276 | 35.2761
4.1 | 2.8637 | 1 | 7.824 | 276 | 35.2761
4.6 | 3.1359 | 1 | 7.824 | 276 | 35.2761
5.1 | 3.6118 | 1 | 7.824 | 276 | 35.2761
5.6 | 3.7964 | 1 | 7.824 | 276 | 35.2761
6.3 | 3.9302 | 1 | 7.824 | 276 | 35.2761
7.9 | 4.7689 | 1 | 7.824 | 276 | 35.2761
8.5 | 4.166 | 1 | 7.824 | 276 | 35.2761
8.7 | 3.8783 | 1 | 7.824 | 276 | 35.2761
8.1 | 4.613 | 1 | 7.824 | 276 | 35.2761
7.7 | 4.6667 | 1 | 7.824 | 276 | 35.2761
7.9 | 4.7705 | 1 | 7.824 | 276 | 35.2761
7.1 | 4.6297 | 1 | 7.824 | 276 | 35.2761
6.5 | 3.5366 | 1 | 7.824 | 276 | 35.2761
6.1 | 3.4054 | 1 | 7.824 | 276 | 35.2761
5.4 | 2.7769 | 1 | 7.824 | 276 | 35.2761
4.4 | 2.4768 | 1 | 7.824 | 276 | 35.2761
3.5 | 2.1353 | 1 | 7.824 | 276 | 35.2761
3.2 | 1.967 | 1 | 7.824 | 276 | 35.2761
2.9 | 1.7585 | 1 | 7.824 | 276 | 35.2761
2.4 | 1.263 | 1 | 7.824 | 276 | 35.2761
1.9 | 0.97541 | 1 | 7.824 | 276 | 35.2761
1.9 | 0.97594 | 1 | 7.824 | 276 | 35.2761
2.2 | 1.2815 | 1 | 7.824 | 276 | 35.2761
2.4 | 1.2637 | 1 | 7.824 | 276 | 35.2761
2.9 | 1.6371 | 1 | 7.824 | 276 | 35.2761
3.9 | 2.3213 | 1 | 7.824 | 276 | 35.2761
5.9 | 3.6475 | 1 | 7.824 | 276 | 35.2761
7.5 | 4.1195 | 1 | 7.824 | 276 | 35.2761
7.8 | 4.0795 | 1 | 7.824 | 276 | 35.2761
9 | 4.4476 | 1 | 7.824 | 276 | 35.2761
9.1 | 4.0437 | 1 | 7.824 | 276 | 35.2761
9.4 | 4.6206 | 1 | 7.824 | 276 | 35.2761
10 | 4.756 | 1 | 7.824 | 276 | 35.2761
9.3 | 3.8887 | 1 | 7.824 | 276 | 35.2761
9.1 | 4.32 | 1 | 7.824 | 276 | 35.2761
8.9 | 4.1088 | 1 | 7.824 | 276 | 35.2761
8.4 | 4.2058 | 1 | 7.824 | 276 | 35.2761
8 | 4.1486 | 1 | 7.824 | 276 | 35.2761
7.3 | 4.2812 | 1 | 7.824 | 276 | 35.2761
6 | 3.5129 | 1 | 7.824 | 276 | 35.2761
4.7 | 2.5207 | 1 | 7.824 | 276 | 35.2761
3.8 | 1.9768 | 1 | 7.824 | 276 | 35.2761
3.4 | 1.6657 | 1 | 7.824 | 276 | 35.2761
2.6 | 0.95934 | 1 | 7.824 | 276 | 35.2761
0.5 | -0.34079 | 1 | 7.824 | 276 | 35.2761
1 | -0.096527 | 1 | 7.824 | 276 | 35.2761
1.2 | -0.022422 | 1 | 7.824 | 276 | 35.2761
1.1 | -0.0011675 | 1 | 7.824 | 276 | 35.2761
2 | 0.69329 | 1 | 7.824 | 276 | 35.2761
4 | 2.0464 | 1 | 7.824 | 276 | 35.2761
5.6 | 3.2212 | 1 | 7.824 | 276 | 35.2761
8.5 | 5.5991 | 1 | 7.824 | 276 | 35.2761
10.6 | 6.3781 | 1 | 7.824 | 276 | 35.2761
11.2 | 6.4181 | 1 | 7.824 | 276 | 35.2761
12 | 6.7761 | 1 | 7.824 | 276 | 35.2761
12.3 | 6.9551 | 1 | 7.824 | 276 | 35.2761
13 | 6.9835 | 1 | 7.824 | 276 | 35.2761
11.6 | 6.2578 | 1 | 7.824 | 276 | 35.2761
11.6 | 6.2578 | 1 | 7.824 | 276 | 35.2761
10.9 | 5.8697 | 1 | 7.824 | 276 | 35.2761
9.2 | 4.9256 | 1 | 7.824 | 276 | 35.2761
7.8 | 4.1922 | 1 | 7.824 | 276 | 35.2761
8 | 4.4181 | 1 | 7.824 | 276 | 35.2761
7.8 | 4.5372 | 1 | 7.824 | 276 | 35.2761
7.5 | 5.164 | 1 | 7.824 | 276 | 35.2761
7.4 | 5.4937 | 1 | 7.824 | 276 | 35.2761
6.5 | 5.0329 | 1 | 7.824 | 276 | 35.2761
5.2 | 3.9625 | 1 | 7.824 | 276 | 35.2761
5 | 3.9862 | 1 | 7.824 | 276 | 35.2761
4.9 | 3.7595 | 1 | 7.824 | 276 | 35.2761
5 | 3.8551 | 1 | 7.824 | 276 | 35.2761
5.5 | 4.3795 | 1 | 7.824 | 276 | 35.2761
6.5 | 4.6006 | 1 | 7.824 | 276 | 35.2761
7.3 | 5.2649 | 1 | 7.824 | 276 | 35.2761
7.6 | 6.3554 | 1 | 7.824 | 276 | 35.2761
7.5 | 6.7386 | 1 | 7.824 | 276 | 35.2761
7.8 | 6.5473 | 1 | 7.824 | 276 | 35.2761
7.9 | 6.4554 | 1 | 7.824 | 276 | 35.2761
7.8 | 6.5467 | 1 | 7.824 | 276 | 35.2761
7.5 | 6.7375 | 1 | 7.824 | 276 | 35.2761
7.6 | 6.3529 | 1 | 7.824 | 276 | 35.2761
7.5 | 6.4941 | 1 | 7.824 | 276 | 35.2761
7.7 | 6.3544 | 1 | 7.824 | 276 | 35.2761
7.6 | 6.3523 | 1 | 7.824 | 276 | 35.2761
7.4 | 6.4924 | 1 | 7.824 | 276 | 35.2761
7.4 | 6.5897 | 1 | 7.824 | 276 | 35.2761
7.8 | 7.1291 | 1 | 7.824 | 276 | 35.2761
8 | 7.2248 | 1 | 7.824 | 276 | 35.2761
7.5 | 6.9348 | 1 | 7.824 | 276 | 35.2761
7.7 | 7.2328 | 1 | 7.824 | 276 | 35.2761
7.4 | 6.7369 | 1 | 7.824 | 276 | 35.2761
6.8 | 6.1486 | 1 | 7.824 | 276 | 35.2761
6.9 | 6.1009 | 1 | 7.824 | 276 | 35.2761
5.9 | 5.5538 | 1 | 7.824 | 276 | 35.2761
5.7 | 5.356 | 1 | 7.824 | 276 | 35.2761
6.5 | 6.0488 | 1 | 7.824 | 276 | 35.2761
7.4 | 6.7366 | 1 | 7.824 | 276 | 35.2761
8.3 | 7.2682 | 1 | 7.824 | 276 | 35.2761
8.9 | 8.0017 | 1 | 7.824 | 276 | 35.2761
9.4 | 7.8372 | 1 | 7.824 | 276 | 35.2761
9.5 | 8.2805 | 1 | 7.824 | 276 | 35.2761
9.9 | 8.2159 | 1 | 7.824 | 276 | 35.2761
10.7 | 8.2496 | 1 | 7.824 | 276 | 35.2761
10.8 | 8.4374 | 1 | 7.824 | 276 | 35.2761
9.7 | 8.5751 | 1 | 7.824 | 276 | 35.2761
8 | 6.8793 | 1 | 7.824 | 276 | 35.2761
7.5 | 6.4916 | 1 | 7.824 | 276 | 35.2761
7.6 | 6.3504 | 1 | 7.824 | 276 | 35.2761
6.8 | 5.9078 | 1 | 7.824 | 276 | 35.2761
6.3 | 5.6106 | 1 | 7.824 | 276 | 35.2761
6.4 | 5.8532 | 1 | 7.824 | 276 | 35.2761
6.9 | 6.0059 | 1 | 7.824 | 276 | 35.2761
7 | 6.3453 | 1 | 7.824 | 276 | 35.2761
5.9 | 5.4577 | 1 | 7.824 | 276 | 35.2761
6 | 5.5565 | 1 | 7.824 | 276 | 35.2761
6 | 5.5567 | 1 | 7.824 | 276 | 35.2761
6.2 | 5.8517 | 1 | 7.824 | 276 | 35.2761
6.5 | 6.1487 | 1 | 7.824 | 276 | 35.2761
6.9 | 6.3463 | 1 | 7.824 | 276 | 35.2761
7.1 | 6.6427 | 1 | 7.824 | 276 | 35.2761
8.4 | 7.6193 | 1 | 7.824 | 276 | 35.2761
8.9 | 7.8066 | 1 | 7.824 | 276 | 35.2761
11 | 8.7822 | 1 | 7.824 | 276 | 35.2761
13.3 | 9.5427 | 1 | 7.824 | 276 | 35.2761
15.1 | 10.12 | 1 | 7.824 | 276 | 35.2761
16.1 | 10.3894 | 1 | 7.824 | 276 | 35.2761
15.7 | 10.5155 | 1 | 7.824 | 276 | 35.2761
16.5 | 10.5679 | 1 | 7.824 | 276 | 35.2761
17.2 | 10.8311 | 1 | 7.824 | 276 | 35.2761
17 | 10.6234 | 1 | 7.824 | 276 | 35.2761
16.7 | 10.0248 | 1 | 7.824 | 276 | 35.2761
15.2 | 9.9232 | 1 | 7.824 | 276 | 35.2761
13.6 | 8.6309 | 1 | 7.824 | 276 | 35.2761
12.5 | 7.8441 | 1 | 7.824 | 276 | 35.2761
11.5 | 7.61 | 1 | 7.824 | 276 | 35.2761
10.3 | 6.9914 | 1 | 7.824 | 276 | 35.2761
8.7 | 6.2445 | 1 | 7.824 | 276 | 35.2761
7.9 | 5.8874 | 1 | 7.824 | 276 | 35.2761
7 | 5.4304 | 1 | 7.824 | 276 | 35.2761
6.1 | 4.879 | 1 | 7.824 | 276 | 35.2761
6 | 4.783 | 1 | 7.824 | 276 | 35.2761
5.5 | 4.4771 | 1 | 7.824 | 276 | 35.2761
5.6 | 4.7078 | 1 | 7.824 | 276 | 35.2761
5 | 4.2138 | 1 | 7.824 | 276 | 35.2761
5.6 | 4.7083 | 1 | 7.824 | 276 | 35.2761
7.6 | 6.1392 | 1 | 7.824 | 276 | 35.2761
9.8 | 7.7199 | 1 | 7.824 | 276 | 35.2761
12.1 | 9.1178 | 1 | 7.824 | 276 | 35.2761
15.1 | 9.8192 | 1 | 7.824 | 276 | 35.2761
16.5 | 9.7067 | 1 | 7.824 | 276 | 35.2761
17.2 | 10.2029 | 1 | 7.824 | 276 | 35.2761
17 | 9.7469 | 1 | 7.824 | 276 | 35.2761
16.9 | 9.4232 | 1 | 7.824 | 276 | 35.2761
16.4 | 9.1619 | 1 | 7.824 | 276 | 35.2761
15.7 | 8.8756 | 1 | 7.824 | 276 | 35.2761
14 | 7.4659 | 1 | 7.824 | 276 | 35.2761
11 | 5.6191 | 1 | 7.824 | 276 | 35.2761
8.9 | 4.759 | 1 | 7.824 | 276 | 35.2761
8 | 4.4441 | 1 | 7.824 | 276 | 35.2761
8.9 | 4.9932 | 1 | 7.824 | 276 | 35.2761
7.7 | 4.4732 | 1 | 7.824 | 276 | 35.2761
6.9 | 4.1218 | 1 | 7.824 | 276 | 35.2761
6.2 | 3.6343 | 1 | 7.824 | 276 | 35.2761
5.1 | 3.1888 | 1 | 7.824 | 276 | 35.2761
4 | 2.8634 | 1 | 7.824 | 276 | 35.2761
3.6 | 2.601 | 1 | 7.824 | 276 | 35.2761
3.6 | 2.4785 | 1 | 7.824 | 276 | 35.2761
3.4 | 2.287 | 1 | 7.824 | 276 | 35.2761
4.5 | 2.8202 | 1 | 7.824 | 276 | 35.2761
7.8 | 5.2538 | 1 | 7.824 | 276 | 35.2761
10.7 | 6.3743 | 1 | 7.824 | 276 | 35.2761
13 | 8.1328 | 1 | 7.824 | 276 | 35.2761
15.7 | 9.3402 | 1 | 7.824 | 276 | 35.2761
16.1 | 9.3025 | 1 | 7.824 | 276 | 35.2761
16.2 | 9.2735 | 1 | 7.824 | 276 | 35.2761
16.5 | 9.3742 | 1 | 7.824 | 276 | 35.2761
16.8 | 9.6478 | 1 | 7.824 | 276 | 35.2761
16.6 | 9.6663 | 1 | 7.824 | 276 | 35.2761
16.3 | 9.8298 | 1 | 7.824 | 276 | 35.2761
15.9 | 9.842 | 1 | 7.824 | 276 | 35.2761
14.6 | 9.1019 | 1 | 7.824 | 276 | 35.2761
13.2 | 9.1222 | 1 | 7.824 | 276 | 35.2761
11.6 | 7.6208 | 1 | 7.824 | 276 | 35.2761
10.7 | 7.0246 | 1 | 7.824 | 276 | 35.2761
10.9 | 7.2434 | 1 | 7.824 | 276 | 35.2761
9.4 | 6.5093 | 1 | 7.824 | 276 | 35.2761
7.2 | 5.8444 | 1 | 7.824 | 276 | 35.2761
7 | 5.0847 | 1 | 7.824 | 276 | 35.2761
6.8 | 5.2395 | 1 | 7.824 | 276 | 35.2761
6.2 | 4.7544 | 1 | 7.824 | 276 | 35.2761
5.7 | 4.5804 | 1 | 7.824 | 276 | 35.2761
4.3 | 3.6172 | 1 | 7.824 | 276 | 35.2761
6.2 | 4.8413 | 1 | 7.824 | 276 | 35.2761
8.3 | 6.3046 | 1 | 7.824 | 276 | 35.2761
10.1 | 6.8922 | 1 | 7.824 | 276 | 35.2761
13.1 | 8.8166 | 1 | 7.824 | 276 | 35.2761
14.6 | 9.5379 | 1 | 7.824 | 276 | 35.2761
16.3 | 10.3731 | 1 | 7.824 | 276 | 35.2761
16.8 | 9.89 | 1 | 7.824 | 276 | 35.2761
17.4 | 9.5868 | 1 | 7.824 | 276 | 35.2761
18 | 10.5248 | 1 | 7.824 | 276 | 35.2761
17.8 | 10.2151 | 1 | 7.824 | 276 | 35.2761
17.9 | 10.3312 | 1 | 7.824 | 276 | 35.2761
15.7 | 9.8588 | 1 | 7.824 | 276 | 35.2761
14.9 | 8.9539 | 1 | 7.824 | 276 | 35.2761
12.8 | 7.8248 | 1 | 7.824 | 276 | 35.2761
12.1 | 7.5691 | 1 | 7.824 | 276 | 35.2761
11.5 | 7.852 | 1 | 7.824 | 276 | 35.2761
11.2 | 7.6658 | 1 | 7.824 | 276 | 35.2761
10.2 | 7.6702 | 1 | 7.824 | 276 | 35.2761
9 | 7.0942 | 1 | 7.824 | 276 | 35.2761
10.3 | 8.9625 | 1 | 7.824 | 276 | 35.2761
10 | 8.7739 | 1 | 7.824 | 276 | 35.2761
9.3 | 8.2476 | 1 | 7.824 | 276 | 35.2761
9.9 | 8.8814 | 1 | 7.824 | 276 | 35.2761
10.1 | 9.2322 | 1 | 7.824 | 276 | 35.2761
10.6 | 9.6147 | 1 | 7.824 | 276 | 35.2761
11.6 | 10.2677 | 1 | 7.824 | 276 | 35.2761
12.2 | 10.4253 | 1 | 7.824 | 276 | 35.2761
13.1 | 10.1166 | 1 | 7.824 | 276 | 35.2761
13.6 | 10.0985 | 1 | 7.824 | 276 | 35.2761
14 | 9.8182 | 1 | 7.824 | 276 | 35.2761
12.4 | 10.6162 | 1 | 7.824 | 276 | 35.2761
11.1 | 9.3255 | 1 | 7.824 | 276 | 35.2761
12.4 | 7.9866 | 1 | 7.824 | 276 | 35.2761
12.5 | 6.3416 | 1 | 7.824 | 276 | 35.2761
12.6 | 5.5456 | 1 | 7.824 | 276 | 35.2761
11.5 | 5.1392 | 1 | 7.824 | 276 | 35.2761
8.3 | 5.0681 | 1 | 7.824 | 276 | 35.2761
6.5 | 3.9339 | 1 | 7.824 | 276 | 35.2761
5.9 | 3.8869 | 1 | 7.824 | 276 | 35.2761
6 | 4.2242 | 1 | 7.824 | 276 | 35.2761
5.2 | 3.5121 | 1 | 7.824 | 276 | 35.2761
5.1 | 3.6205 | 1 | 7.824 | 276 | 35.2761
5.2 | 3.7571 | 1 | 7.824 | 276 | 35.2761
5 | 3.649 | 1 | 7.824 | 276 | 35.2761
5.8 | 4.242 | 1 | 7.824 | 276 | 35.2761
6.2 | 4.5366 | 1 | 7.824 | 276 | 35.2761
6.4 | 4.5971 | 1 | 7.824 | 276 | 35.2761
6.4 | 4.8097 | 1 | 7.824 | 276 | 35.2761
7 | 4.9924 | 1 | 7.824 | 276 | 35.2761
8.5 | 5.9219 | 1 | 7.824 | 276 | 35.2761
9.1 | 6.0977 | 1 | 7.824 | 276 | 35.2761
10 | 6.6263 | 1 | 7.824 | 276 | 35.2761
10.3 | 7.3177 | 1 | 7.824 | 276 | 35.2761
11.7 | 7.3734 | 1 | 7.824 | 276 | 35.2761
13 | 7.9529 | 1 | 7.824 | 276 | 35.2761
13 | 6.9893 | 1 | 7.824 | 276 | 35.2761
12.7 | 7.2578 | 1 | 7.824 | 276 | 35.2761
12 | 6.6048 | 1 | 7.824 | 276 | 35.2761
11 | 7.1192 | 1 | 7.824 | 276 | 35.2761
10.5 | 6.7163 | 1 | 7.824 | 276 | 35.2761
9.7 | 6.485 | 1 | 7.824 | 276 | 35.2761
9 | 6.1373 | 1 | 7.824 | 276 | 35.2761
8.3 | 5.9544 | 1 | 7.824 | 276 | 35.2761
8.7 | 5.5828 | 1 | 7.824 | 276 | 35.2761
8 | 5.2254 | 1 | 7.824 | 276 | 35.2761
7.9 | 5.3353 | 1 | 7.824 | 276 | 35.2761
8 | 5.1053 | 1 | 7.824 | 276 | 35.2761
8 | 4.8354 | 1 | 7.824 | 276 | 35.2761
7.6 | 5.0168 | 1 | 7.824 | 276 | 35.2761
7.7 | 5.4794 | 1 | 7.824 | 276 | 35.2761
7 | 5.5574 | 1 | 7.824 | 276 | 35.2761
7.6 | 5.597 | 1 | 7.824 | 276 | 35.2761
8 | 5.6282 | 1 | 7.824 | 276 | 35.2761
9 | 6.1287 | 1 | 7.824 | 276 | 35.2761
9.1 | 6.0947 | 1 | 7.824 | 276 | 35.2761
9 | 5.7216 | 1 | 7.824 | 276 | 35.2761
9 | 6.1244 | 1 | 7.824 | 276 | 35.2761
9.4 | 6.1579 | 1 | 7.824 | 276 | 35.2761
9.3 | 6.5633 | 1 | 7.824 | 276 | 35.2761
7.9 | 6.7875 | 1 | 7.824 | 276 | 35.2761
7.6 | 6.9346 | 1 | 7.824 | 276 | 35.2761
7.8 | 7.1301 | 1 | 7.824 | 276 | 35.2761
8 | 7.3256 | 1 | 7.824 | 276 | 35.2761
8.2 | 7.987 | 1 | 7.824 | 276 | 35.2761
9.1 | 8.4553 | 1 | 7.824 | 276 | 35.2761
9.1 | 8.1959 | 1 | 7.824 | 276 | 35.2761
7.9 | 6.9763 | 1 | 7.824 | 276 | 35.2761
6.3 | 5.6089 | 1 | 7.824 | 276 | 35.2761
6.3 | 5.5133 | 1 | 7.824 | 276 | 35.2761
6.2 | 5.4158 | 1 | 7.824 | 276 | 35.2761
6.1 | 5.178 | 1 | 7.824 | 276 | 35.2761
6 | 5.0804 | 1 | 7.824 | 276 | 35.2761
4.9 | 4.4228 | 1 | 7.824 | 276 | 35.2761
5.1 | 4.7615 | 1 | 7.824 | 276 | 35.2761
6.4 | 5.949 | 1 | 7.824 | 276 | 35.2761
6 | 4.9899 | 1 | 7.824 | 276 | 35.2761
5.6 | 4.4693 | 1 | 7.824 | 276 | 35.2761
5.1 | 3.858 | 1 | 7.824 | 276 | 35.2761
3.6 | 2.9251 | 1 | 7.824 | 276 | 35.2761
4.5 | 3.8056 | 1 | 7.824 | 276 | 35.2761
5 | 3.7668 | 1 | 7.824 | 276 | 35.2761
5.9 | 4.3286 | 1 | 7.824 | 276 | 35.2761
5.9 | 3.7555 | 1 | 7.824 | 276 | 35.2761
9 | 3.8029 | 1 | 7.824 | 276 | 35.2761
8.1 | 3.8457 | 1 | 7.824 | 276 | 35.2761
5.7 | 3.7728 | 1 | 7.824 | 276 | 35.2761
3.9 | 2.758 | 1 | 7.824 | 276 | 35.2761
5.2 | 3.1509 | 1 | 7.824 | 276 | 35.2761
4.9 | 3.2247 | 1 | 7.824 | 276 | 35.2761
2.4 | 1.9669 | 1 | 7.824 | 276 | 35.2761
3.4 | 2.1603 | 1 | 7.824 | 276 | 35.2761
3.3 | 1.7786 | 1 | 7.824 | 276 | 35.2761
3.8 | 1.7292 | 1 | 7.824 | 276 | 35.2761
4 | 1.9248 | 1 | 7.824 | 276 | 35.2761
3.4 | 1.3035 | 1 | 7.824 | 276 | 35.2761
3.2 | 1.1896 | 1 | 7.824 | 276 | 35.2761
3.2 | 1.1896 | 1 | 7.824 | 276 | 35.2761
3 | 1.2368 | 1 | 7.824 | 276 | 35.2761
2.5 | 0.9888 | 1 | 7.824 | 276 | 35.2761
2.7 | 1.0655 | 1 | 7.824 | 276 | 35.2761
3.5 | 1.6489 | 1 | 7.824 | 276 | 35.2761
5.2 | 2.5674 | 1 | 7.824 | 276 | 35.2761
6.4 | 3.3469 | 1 | 7.824 | 276 | 35.2761
7.2 | 3.4391 | 1 | 7.824 | 276 | 35.2761
7.6 | 3.998 | 1 | 7.824 | 276 | 35.2761
7.8 | 4.1049 | 1 | 7.824 | 276 | 35.2761
8.3 | 4.2561 | 1 | 7.824 | 276 | 35.2761
9.4 | 5.2913 | 1 | 7.824 | 276 | 35.2761
9.2 | 4.6959 | 1 | 7.824 | 276 | 35.2761
9.7 | 4.7413 | 1 | 7.824 | 276 | 35.2761
9.4 | 4.4094 | 1 | 7.824 | 276 | 35.2761
8.9 | 4.6507 | 1 | 7.824 | 276 | 35.2761
8.3 | 4.2582 | 1 | 7.824 | 276 | 35.2761
8 | 3.8052 | 1 | 7.824 | 276 | 35.2761
7 | 3.8784 | 1 | 7.824 | 276 | 35.2761
6 | 3.5301 | 1 | 7.824 | 276 | 35.2761
4.5 | 2.8229 | 1 | 7.824 | 276 | 35.2761
4.5 | 2.9404 | 1 | 7.824 | 276 | 35.2761
5 | 3.3325 | 1 | 7.824 | 276 | 35.2761
4.7 | 3.3712 | 1 | 7.824 | 276 | 35.2761
5.2 | 3.9743 | 1 | 7.824 | 276 | 35.2761
4.9 | 4.1168 | 1 | 7.824 | 276 | 35.2761
5 | 4.576 | 1 | 7.824 | 276 | 35.2761
5.2 | 4.9605 | 1 | 7.824 | 276 | 35.2761
5.9 | 5.6551 | 1 | 7.824 | 276 | 35.2761
6.6 | 6.2513 | 1 | 7.824 | 276 | 35.2761
7.4 | 6.9429 | 1 | 7.824 | 276 | 35.2761
8.4 | 8.0843 | 1 | 7.824 | 276 | 35.2761
10 | 9.3481 | 1 | 7.824 | 276 | 35.2761
11.9 | 10.5627 | 1 | 7.824 | 276 | 35.2761
13.3 | 11.5352 | 1 | 7.824 | 276 | 35.2761
14.5 | 12.518 | 1 | 7.824 | 276 | 35.2761
14.1 | 12.6881 | 1 | 7.824 | 276 | 35.2761
14.9 | 13.0658 | 1 | 7.824 | 276 | 35.2761
16 | 13.176 | 1 | 7.824 | 276 | 35.2761
14.6 | 12.0767 | 1 | 7.824 | 276 | 35.2761
14.2 | 11.8066 | 1 | 7.824 | 276 | 35.2761
13.9 | 11.6286 | 1 | 7.824 | 276 | 35.2761
13.5 | 11.4075 | 1 | 7.824 | 276 | 35.2761
13 | 11.1424 | 1 | 7.824 | 276 | 35.2761
12.6 | 10.9712 | 1 | 7.824 | 276 | 35.2761
11.5 | 10.3881 | 1 | 7.824 | 276 | 35.2761
10.2 | 9.5446 | 1 | 7.824 | 276 | 35.2761
9.7 | 9.0534 | 1 | 7.824 | 276 | 35.2761
9 | 8.6788 | 1 | 7.824 | 276 | 35.2761
10.6 | 9.9377 | 1 | 7.824 | 276 | 35.2761
11.1 | 10.3203 | 1 | 7.824 | 276 | 35.2761
11.5 | 10.4953 | 1 | 7.824 | 276 | 35.2761
12.2 | 10.906 | 1 | 7.824 | 276 | 35.2761
13.9 | 11.7339 | 1 | 7.824 | 276 | 35.2761
14 | 11.8286 | 1 | 7.824 | 276 | 35.2761
14.7 | 11.7582 | 1 | 7.824 | 276 | 35.2761
16 | 12.3975 | 1 | 7.824 | 276 | 35.2761
17.3 | 13.1736 | 1 | 7.824 | 276 | 35.2761
17.1 | 13.4022 | 1 | 7.824 | 276 | 35.2761
17.8 | 14.0964 | 1 | 7.824 | 276 | 35.2761
17.5 | 13.716 | 1 | 7.824 | 276 | 35.2761
16.5 | 13.4826 | 1 | 7.824 | 276 | 35.2761
16.3 | 13.5663 | 1 | 7.824 | 276 | 35.2761
16 | 13.2849 | 1 | 7.824 | 276 | 35.2761
14.9 | 12.5195 | 1 | 7.824 | 276 | 35.2761
12.6 | 11.4025 | 1 | 7.824 | 276 | 35.2761
12.1 | 11.0258 | 1 | 7.824 | 276 | 35.2761
11.1 | 10.3207 | 1 | 7.824 | 276 | 35.2761
10.1 | 9.5536 | 1 | 7.824 | 276 | 35.2761
9.8 | 9.3645 | 1 | 7.824 | 276 | 35.2761
9.7 | 9.1594 | 1 | 7.824 | 276 | 35.2761
9.8 | 9.3645 | 1 | 7.824 | 276 | 35.2761
9.3 | 8.7653 | 1 | 7.824 | 276 | 35.2761
9.2 | 8.8773 | 1 | 7.824 | 276 | 35.2761
10 | 9.5622 | 1 | 7.824 | 276 | 35.2761
10 | 9.455 | 1 | 7.824 | 276 | 35.2761
10.9 | 10.0179 | 1 | 7.824 | 276 | 35.2761
12 | 10.5551 | 1 | 7.824 | 276 | 35.2761
13 | 10.8331 | 1 | 7.824 | 276 | 35.2761
14.1 | 11.3552 | 1 | 7.824 | 276 | 35.2761
14.8 | 11.5509 | 1 | 7.824 | 276 | 35.2761
13 | 10.937 | 1 | 7.824 | 276 | 35.2761
14.1 | 11.3552 | 1 | 7.824 | 276 | 35.2761
16.2 | 12.634 | 1 | 7.824 | 276 | 35.2761
16.1 | 12.1923 | 1 | 7.824 | 276 | 35.2761
15 | 11.6351 | 1 | 7.824 | 276 | 35.2761
15.1 | 11.4805 | 1 | 7.824 | 276 | 35.2761
15.2 | 11.6205 | 1 | 7.824 | 276 | 35.2761
14.5 | 11.6767 | 1 | 7.824 | 276 | 35.2761
13.9 | 11.2702 | 1 | 7.824 | 276 | 35.2761
14 | 11.262 | 1 | 7.824 | 276 | 35.2761
13.6 | 11.0923 | 1 | 7.824 | 276 | 35.2761
13 | 11.2512 | 1 | 7.824 | 276 | 35.2761
12.7 | 11.0699 | 1 | 7.824 | 276 | 35.2761
12.5 | 10.9834 | 1 | 7.824 | 276 | 35.2761
11.7 | 10.4771 | 1 | 7.824 | 276 | 35.2761
10.8 | 9.7097 | 1 | 7.824 | 276 | 35.2761
10.7 | 9.7173 | 1 | 7.824 | 276 | 35.2761
10.4 | 9.7417 | 1 | 7.824 | 276 | 35.2761
9.9 | 9.3565 | 1 | 7.824 | 276 | 35.2761
11.2 | 10.2043 | 1 | 7.824 | 276 | 35.2761
12.3 | 10.791 | 1 | 7.824 | 276 | 35.2761
13.5 | 11.4093 | 1 | 7.824 | 276 | 35.2761
14.2 | 11.8086 | 1 | 7.824 | 276 | 35.2761
16.1 | 12.7459 | 1 | 7.824 | 276 | 35.2761
16.4 | 12.2651 | 1 | 7.824 | 276 | 35.2761
17.2 | 12.0708 | 1 | 7.824 | 276 | 35.2761
17.8 | 12.2271 | 1 | 7.824 | 276 | 35.2761
17.1 | 11.6197 | 1 | 7.824 | 276 | 35.2761
16.7 | 11.5861 | 1 | 7.824 | 276 | 35.2761
16.4 | 11.2774 | 1 | 7.824 | 276 | 35.2761
15.2 | 10.9467 | 1 | 7.824 | 276 | 35.2761
14.6 | 10.6414 | 1 | 7.824 | 276 | 35.2761
13.1 | 10.8213 | 1 | 7.824 | 276 | 35.2761
12.2 | 10.1231 | 1 | 7.824 | 276 | 35.2761
11.5 | 9.3138 | 1 | 7.824 | 276 | 35.2761
11.1 | 9.3303 | 1 | 7.824 | 276 | 35.2761
11.1 | 8.6508 | 1 | 7.824 | 276 | 35.2761
11.2 | 8.5573 | 1 | 7.824 | 276 | 35.2761
11.5 | 8.5122 | 1 | 7.824 | 276 | 35.2761
11 | 8.3696 | 1 | 7.824 | 276 | 35.2761
10.9 | 8.2312 | 1 | 7.824 | 276 | 35.2761
11.1 | 8.3234 | 1 | 7.824 | 276 | 35.2761
11 | 8.1408 | 1 | 7.824 | 276 | 35.2761
11.4 | 8.4178 | 1 | 7.824 | 276 | 35.2761
12 | 8.7854 | 1 | 7.824 | 276 | 35.2761
12.5 | 9.2871 | 1 | 7.824 | 276 | 35.2761
13.3 | 10.1127 | 1 | 7.824 | 276 | 35.2761
14.5 | 11.4111 | 1 | 7.824 | 276 | 35.2761
15.1 | 11.2712 | 1 | 7.824 | 276 | 35.2761
15 | 10.8501 | 1 | 7.824 | 276 | 35.2761
15.5 | 10.7906 | 1 | 7.824 | 276 | 35.2761
16.9 | 11.5176 | 1 | 7.824 | 276 | 35.2761
15.6 | 10.4356 | 1 | 7.824 | 276 | 35.2761
15.8 | 10.6523 | 1 | 7.824 | 276 | 35.2761
15.1 | 10.4813 | 1 | 7.824 | 276 | 35.2761
13.4 | 9.6444 | 1 | 7.824 | 276 | 35.2761
12.6 | 9.1937 | 1 | 7.824 | 276 | 35.2761
12.6 | 9.1937 | 1 | 7.824 | 276 | 35.2761
11.8 | 9.0612 | 1 | 7.824 | 276 | 35.2761
10.9 | 8.6012 | 1 | 7.824 | 276 | 35.2761
8.7 | 7.3736 | 1 | 7.824 | 276 | 35.2761
8 | 6.8902 | 1 | 7.824 | 276 | 35.2761
8.1 | 7.0836 | 1 | 7.824 | 276 | 35.2761
7.7 | 6.7919 | 1 | 7.824 | 276 | 35.2761
8.6 | 7.4706 | 1 | 7.824 | 276 | 35.2761
8.7 | 7.5673 | 1 | 7.824 | 276 | 35.2761
8.4 | 7.4238 | 1 | 7.824 | 276 | 35.2761
9.4 | 7.9475 | 1 | 7.824 | 276 | 35.2761
10.4 | 8.2722 | 1 | 7.824 | 276 | 35.2761
10.7 | 8.2701 | 1 | 7.824 | 276 | 35.2761
12.4 | 8.7402 | 1 | 7.824 | 276 | 35.2761
12.6 | 9.189 | 1 | 7.824 | 276 | 35.2761
13.5 | 9.637 | 1 | 7.824 | 276 | 35.2761
13.6 | 9.4132 | 1 | 7.824 | 276 | 35.2761
14.6 | 9.5198 | 1 | 7.824 | 276 | 35.2761
14.4 | 9.554 | 1 | 7.824 | 276 | 35.2761
14.5 | 9.9852 | 1 | 7.824 | 276 | 35.2761
13.3 | 8.7605 | 1 | 7.824 | 276 | 35.2761
12.5 | 8.7337 | 1 | 7.824 | 276 | 35.2761
11.4 | 8.4964 | 1 | 7.824 | 276 | 35.2761
10.5 | 7.8489 | 1 | 7.824 | 276 | 35.2761
10 | 7.8901 | 1 | 7.824 | 276 | 35.2761
9.6 | 7.7954 | 1 | 7.824 | 276 | 35.2761
9.6 | 7.9394 | 1 | 7.824 | 276 | 35.2761
9.6 | 8.2832 | 1 | 7.824 | 276 | 35.2761
8.7 | 7.9126 | 1 | 7.824 | 276 | 35.2761
9 | 8.2059 | 1 | 7.824 | 276 | 35.2761
9.1 | 8.5633 | 1 | 7.824 | 276 | 35.2761
9.3 | 8.7603 | 1 | 7.824 | 276 | 35.2761
8.8 | 8.2677 | 1 | 7.824 | 276 | 35.2761
8.4 | 7.9773 | 1 | 7.824 | 276 | 35.2761
9.4 | 8.4939 | 1 | 7.824 | 276 | 35.2761
10.2 | 8.8613 | 1 | 7.824 | 276 | 35.2761
11.7 | 9.3897 | 1 | 7.824 | 276 | 35.2761
12.2 | 9.0909 | 1 | 7.824 | 276 | 35.2761
13.2 | 9.678 | 1 | 7.824 | 276 | 35.2761
14 | 9.3665 | 1 | 7.824 | 276 | 35.2761
15.1 | 9.3267 | 1 | 7.824 | 276 | 35.2761
14.6 | 9.6343 | 1 | 7.824 | 276 | 35.2761
15.9 | 9.2667 | 1 | 7.824 | 276 | 35.2761
14.3 | 9.3324 | 1 | 7.824 | 276 | 35.2761
14 | 8.9907 | 1 | 7.824 | 276 | 35.2761
13.3 | 9.0942 | 1 | 7.824 | 276 | 35.2761
12 | 8.1115 | 1 | 7.824 | 276 | 35.2761
11.1 | 7.5187 | 1 | 7.824 | 276 | 35.2761
10 | 7.2087 | 1 | 7.824 | 276 | 35.2761
9.5 | 6.9222 | 1 | 7.824 | 276 | 35.2761
8.7 | 7.319 | 1 | 7.824 | 276 | 35.2761
8.1 | 7.0792 | 1 | 7.824 | 276 | 35.2761
7.7 | 6.4516 | 1 | 7.824 | 276 | 35.2761
8.1 | 6.5542 | 1 | 7.824 | 276 | 35.2761
8.1 | 6.324 | 1 | 7.824 | 276 | 35.2761
7.3 | 6.1595 | 1 | 7.824 | 276 | 35.2761
7.5 | 6.592 | 1 | 7.824 | 276 | 35.2761
8.1 | 7.2249 | 1 | 7.824 | 276 | 35.2761
10 | 8.2191 | 1 | 7.824 | 276 | 35.2761
10.4 | 8.5013 | 1 | 7.824 | 276 | 35.2761
11.5 | 9.0502 | 1 | 7.824 | 276 | 35.2761
12.4 | 9.7434 | 1 | 7.824 | 276 | 35.2761
13.8 | 10.596 | 1 | 7.824 | 276 | 35.2761
14.9 | 10.5927 | 1 | 7.824 | 276 | 35.2761
12.5 | 10.7536 | 1 | 7.824 | 276 | 35.2761
12 | 10.9174 | 1 | 7.824 | 276 | 35.2761
11.8 | 10.6683 | 1 | 7.824 | 276 | 35.2761
12 | 10.6458 | 1 | 7.824 | 276 | 35.2761
12.2 | 11.0022 | 1 | 7.824 | 276 | 35.2761
12.2 | 11.0022 | 1 | 7.824 | 276 | 35.2761
11.9 | 11.1525 | 1 | 7.824 | 276 | 35.2761
11.8 | 11.0546 | 1 | 7.824 | 276 | 35.2761
11.3 | 10.5088 | 1 | 7.824 | 276 | 35.2761
10.8 | 9.9112 | 1 | 7.824 | 276 | 35.2761
10.5 | 9.512 | 1 | 7.824 | 276 | 35.2761
10.3 | 9.2129 | 1 | 7.824 | 276 | 35.2761
10 | 8.7677 | 1 | 7.824 | 276 | 35.2761
9.9 | 8.47 | 1 | 7.824 | 276 | 35.2761
9.4 | 8.3911 | 1 | 7.824 | 276 | 35.2761
8.7 | 7.8114 | 1 | 7.824 | 276 | 35.2761
8.4 | 7.519 | 1 | 7.824 | 276 | 35.2761
8.9 | 7.8061 | 1 | 7.824 | 276 | 35.2761
9.9 | 8.2261 | 1 | 7.824 | 276 | 35.2761
11.3 | 8.9683 | 1 | 7.824 | 276 | 35.2761
12.7 | 9.1374 | 1 | 7.824 | 276 | 35.2761
13 | 9.1391 | 1 | 7.824 | 276 | 35.2761
14.1 | 8.7651 | 1 | 7.824 | 276 | 35.2761
14 | 9.8108 | 1 | 7.824 | 276 | 35.2761
14.9 | 10.7035 | 1 | 7.824 | 276 | 35.2761
15.3 | 10.1243 | 1 | 7.824 | 276 | 35.2761
14.6 | 10.2108 | 1 | 7.824 | 276 | 35.2761
14.9 | 10.0344 | 1 | 7.824 | 276 | 35.2761
14.8 | 9.9472 | 1 | 7.824 | 276 | 35.2761
14.1 | 10.0367 | 1 | 7.824 | 276 | 35.2761
13 | 9.1444 | 1 | 7.824 | 276 | 35.2761
12 | 9.147 | 1 | 7.824 | 276 | 35.2761
11 | 9.0304 | 1 | 7.824 | 276 | 35.2761
10.8 | 9.1374 | 1 | 7.824 | 276 | 35.2761
10.5 | 8.9509 | 1 | 7.824 | 276 | 35.2761
10.4 | 9.3145 | 1 | 7.824 | 276 | 35.2761
10.9 | 9.6944 | 1 | 7.824 | 276 | 35.2761
11.5 | 9.8553 | 1 | 7.824 | 276 | 35.2761
11.5 | 9.8553 | 1 | 7.824 | 276 | 35.2761
10.8 | 9.9136 | 1 | 7.824 | 276 | 35.2761
11.5 | 10.3808 | 1 | 7.824 | 276 | 35.2761
11.8 | 9.8347 | 1 | 7.824 | 276 | 35.2761
12 | 9.7726 | 1 | 7.824 | 276 | 35.2761
12.6 | 10.0384 | 1 | 7.824 | 276 | 35.2761
12.8 | 10.2748 | 1 | 7.824 | 276 | 35.2761
12.6 | 10.5937 | 1 | 7.824 | 276 | 35.2761
12 | 10.6511 | 1 | 7.824 | 276 | 35.2761
12.5 | 11.2979 | 1 | 7.824 | 276 | 35.2761
14 | 11.7087 | 1 | 7.824 | 276 | 35.2761
13.1 | 11.12 | 1 | 7.824 | 276 | 35.2761
12.3 | 10.3081 | 1 | 7.824 | 276 | 35.2761
13 | 10.1134 | 1 | 7.824 | 276 | 35.2761
13 | 9.7778 | 1 | 7.824 | 276 | 35.2761
12.7 | 10.1791 | 1 | 7.824 | 276 | 35.2761
12.1 | 9.7662 | 1 | 7.824 | 276 | 35.2761
11.1 | 9.3207 | 1 | 7.824 | 276 | 35.2761
10.9 | 9.2314 | 1 | 7.824 | 276 | 35.2761
10.2 | 8.6621 | 1 | 7.824 | 276 | 35.2761
9.5 | 7.8472 | 1 | 7.824 | 276 | 35.2761
9.2 | 7.5138 | 1 | 7.824 | 276 | 35.2761
8.8 | 7.3703 | 1 | 7.824 | 276 | 35.2761
8.7 | 7.3704 | 1 | 7.824 | 276 | 35.2761
8.6 | 7.131 | 1 | 7.824 | 276 | 35.2761
8.4 | 6.9396 | 1 | 7.824 | 276 | 35.2761
8.2 | 6.8423 | 1 | 7.824 | 276 | 35.2761
8.9 | 7.3236 | 1 | 7.824 | 276 | 35.2761
9.9 | 8.1324 | 1 | 7.824 | 276 | 35.2761
10.9 | 8.1325 | 1 | 7.824 | 276 | 35.2761
11.7 | 7.9394 | 1 | 7.824 | 276 | 35.2761
12 | 7.671 | 1 | 7.824 | 276 | 35.2761
10.6 | 8.847 | 1 | 7.824 | 276 | 35.2761
10.1 | 8.9717 | 1 | 7.824 | 276 | 35.2761
13 | 9.6897 | 1 | 7.824 | 276 | 35.2761
13.6 | 8.498 | 1 | 7.824 | 276 | 35.2761
15.3 | 9.3516 | 1 | 7.824 | 276 | 35.2761
13.1 | 9.4565 | 1 | 7.824 | 276 | 35.2761
11.5 | 9.4025 | 1 | 7.824 | 276 | 35.2761
11.3 | 8.7314 | 1 | 7.824 | 276 | 35.2761
11.1 | 9.3215 | 1 | 7.824 | 276 | 35.2761
10.3 | 8.08 | 1 | 7.824 | 276 | 35.2761
9.9 | 7.6588 | 1 | 7.824 | 276 | 35.2761
8.7 | 7.0373 | 1 | 7.824 | 276 | 35.2761
8.4 | 7.1768 | 1 | 7.824 | 276 | 35.2761
8.2 | 7.5249 | 1 | 7.824 | 276 | 35.2761
8.2 | 7.5246 | 1 | 7.824 | 276 | 35.2761
8.1 | 7.5274 | 1 | 7.824 | 276 | 35.2761
8.1 | 7.6292 | 1 | 7.824 | 276 | 35.2761
8 | 7.5304 | 1 | 7.824 | 276 | 35.2761
8 | 7.6847 | 1 | 7.824 | 276 | 35.2761
8.3 | 7.982 | 1 | 7.824 | 276 | 35.2761
8.3 | 7.8777 | 1 | 7.824 | 276 | 35.2761
7.7 | 6.9334 | 1 | 7.824 | 276 | 35.2761
7.5 | 6.9361 | 1 | 7.824 | 276 | 35.2761
7.2 | 6.3965 | 1 | 7.824 | 276 | 35.2761
7.4 | 6.8383 | 1 | 7.824 | 276 | 35.2761
8.5 | 7.7167 | 1 | 7.824 | 276 | 35.2761
10.7 | 8.123 | 1 | 7.824 | 276 | 35.2761
11.8 | 8.4525 | 1 | 7.824 | 276 | 35.2761
12.6 | 7.8255 | 1 | 7.824 | 276 | 35.2761
12.2 | 8.2914 | 1 | 7.824 | 276 | 35.2761
11.3 | 7.2887 | 1 | 7.824 | 276 | 35.2761
11.7 | 7.4821 | 1 | 7.824 | 276 | 35.2761
11.3 | 7.5375 | 1 | 7.824 | 276 | 35.2761
9.8 | 7.4749 | 1 | 7.824 | 276 | 35.2761
9.7 | 7.0268 | 1 | 7.824 | 276 | 35.2761
8 | 6.3285 | 1 | 7.824 | 276 | 35.2761
7.6 | 6.0396 | 1 | 7.824 | 276 | 35.2761
7.1 | 5.431 | 1 | 7.824 | 276 | 35.2761
4.7 | 3.9175 | 1 | 7.824 | 276 | 35.2761
5.6 | 4.3502 | 1 | 7.824 | 276 | 35.2761
3.8 | 3.1271 | 1 | 7.824 | 276 | 35.2761
5.2 | 4.3157 | 1 | 7.824 | 276 | 35.2761
5 | 4.1219 | 1 | 7.824 | 276 | 35.2761
4.8 | 4.105 | 1 | 7.824 | 276 | 35.2761
7 | 5.428 | 1 | 7.824 | 276 | 35.2761
8.9 | 6.5569 | 1 | 7.824 | 276 | 35.2761
10.3 | 7.3263 | 1 | 7.824 | 276 | 35.2761
10.7 | 7.3925 | 1 | 7.824 | 276 | 35.2761
11.9 | 7.8006 | 1 | 7.824 | 276 | 35.2761
12 | 7.4523 | 1 | 7.824 | 276 | 35.2761
12.4 | 7.7598 | 1 | 7.824 | 276 | 35.2761
12.9 | 7.6937 | 1 | 7.824 | 276 | 35.2761
12.9 | 7.5832 | 1 | 7.824 | 276 | 35.2761
12 | 7.5689 | 1 | 7.824 | 276 | 35.2761
11.8 | 8.0428 | 1 | 7.824 | 276 | 35.2761
11.5 | 7.8589 | 1 | 7.824 | 276 | 35.2761
10.4 | 7.5072 | 1 | 7.824 | 276 | 35.2761
9.6 | 7.2546 | 1 | 7.824 | 276 | 35.2761
8.5 | 6.405 | 1 | 7.824 | 276 | 35.2761
8 | 6.1117 | 1 | 7.824 | 276 | 35.2761
6.7 | 5.1444 | 1 | 7.824 | 276 | 35.2761
6.2 | 4.9739 | 1 | 7.824 | 276 | 35.2761
7 | 5.4296 | 1 | 7.824 | 276 | 35.2761
6.9 | 5.4669 | 1 | 7.824 | 276 | 35.2761
6.9 | 5.5556 | 1 | 7.824 | 276 | 35.2761
7.3 | 5.8483 | 1 | 7.824 | 276 | 35.2761
7.7 | 6.3677 | 1 | 7.824 | 276 | 35.2761
8 | 7.1345 | 1 | 7.824 | 276 | 35.2761
8.6 | 8.1775 | 1 | 7.824 | 276 | 35.2761
9.3 | 8.7635 | 1 | 7.824 | 276 | 35.2761
10 | 8.929 | 1 | 7.824 | 276 | 35.2761
10.2 | 9.4365 | 1 | 7.824 | 276 | 35.2761
11 | 9.8996 | 1 | 7.824 | 276 | 35.2761
11.1 | 9.8907 | 1 | 7.824 | 276 | 35.2761
11 | 10.0052 | 1 | 7.824 | 276 | 35.2761
11 | 10.3284 | 1 | 7.824 | 276 | 35.2761
11.5 | 10.9307 | 1 | 7.824 | 276 | 35.2761
12.4 | 11.4238 | 1 | 7.824 | 276 | 35.2761
12.5 | 11.7456 | 1 | 7.824 | 276 | 35.2761
13.2 | 12.2039 | 1 | 7.824 | 276 | 35.2761
12.6 | 12.0723 | 1 | 7.824 | 276 | 35.2761
12.2 | 11.3388 | 1 | 7.824 | 276 | 35.2761
11.4 | 10.1262 | 1 | 7.824 | 276 | 35.2761
10.9 | 9.436 | 1 | 7.824 | 276 | 35.2761
10.6 | 8.6996 | 1 | 7.824 | 276 | 35.2761
10.5 | 8.2706 | 1 | 7.824 | 276 | 35.2761
9.6 | 7.1128 | 1 | 7.824 | 276 | 35.2761
8.2 | 6.25 | 1 | 7.824 | 276 | 35.2761
7.6 | 5.8621 | 1 | 7.824 | 276 | 35.2761
6.9 | 5.2876 | 1 | 7.824 | 276 | 35.2761
6.9 | 5.4203 | 1 | 7.824 | 276 | 35.2761
7 | 5.3833 | 1 | 7.824 | 276 | 35.2761
7.3 | 5.4064 | 1 | 7.824 | 276 | 35.2761
7.8 | 5.833 | 1 | 7.824 | 276 | 35.2761
8.7 | 6.1983 | 1 | 7.824 | 276 | 35.2761
9.6 | 6.3186 | 1 | 7.824 | 276 | 35.2761
10.2 | 6.6557 | 1 | 7.824 | 276 | 35.2761
10.6 | 6.5801 | 1 | 7.824 | 276 | 35.2761
8.7 | 7.188 | 1 | 7.824 | 276 | 35.2761
8.1 | 6.9434 | 1 | 7.824 | 276 | 35.2761
8.4 | 6.4015 | 1 | 7.824 | 276 | 35.2761
8.4 | 6.4895 | 1 | 7.824 | 276 | 35.2761
9.2 | 6.7083 | 1 | 7.824 | 276 | 35.2761
9.7 | 6.956 | 1 | 7.824 | 276 | 35.2761
9.4 | 6.5959 | 1 | 7.824 | 276 | 35.2761
9.3 | 6.8044 | 1 | 7.824 | 276 | 35.2761
9.1 | 6.706 | 1 | 7.824 | 276 | 35.2761
8.9 | 6.6951 | 1 | 7.824 | 276 | 35.2761
8.8 | 6.69 | 1 | 7.824 | 276 | 35.2761
8.6 | 6.5913 | 1 | 7.824 | 276 | 35.2761
8.4 | 6.4478 | 1 | 7.824 | 276 | 35.2761
8.1 | 6.3881 | 1 | 7.824 | 276 | 35.2761
7.7 | 6.1878 | 1 | 7.824 | 276 | 35.2761
6.9 | 5.6484 | 1 | 7.824 | 276 | 35.2761
7.1 | 5.7945 | 1 | 7.824 | 276 | 35.2761
7.8 | 6.3281 | 1 | 7.824 | 276 | 35.2761
8.4 | 6.7165 | 1 | 7.824 | 276 | 35.2761
8.9 | 7.1906 | 1 | 7.824 | 276 | 35.2761
8.9 | 7.1442 | 1 | 7.824 | 276 | 35.2761
8.6 | 7.3292 | 1 | 7.824 | 276 | 35.2761
8.4 | 7.6248 | 1 | 7.824 | 276 | 35.2761
8.6 | 7.5221 | 1 | 7.824 | 276 | 35.2761
8.5 | 7.5723 | 1 | 7.824 | 276 | 35.2761
9.4 | 8.3972 | 1 | 7.824 | 276 | 35.2761
12 | 9.9303 | 1 | 7.824 | 276 | 35.2761
14.8 | 9.2962 | 1 | 7.824 | 276 | 35.2761
14 | 9.1754 | 1 | 7.824 | 276 | 35.2761
13.1 | 9.3281 | 1 | 7.824 | 276 | 35.2761
11.9 | 8.3376 | 1 | 7.824 | 276 | 35.2761
10.4 | 7.5869 | 1 | 7.824 | 276 | 35.2761
9.6 | 6.9821 | 1 | 7.824 | 276 | 35.2761
8.7 | 6.3665 | 1 | 7.824 | 276 | 35.2761
8.2 | 6.3382 | 1 | 7.824 | 276 | 35.2761
7.9 | 6.3703 | 1 | 7.824 | 276 | 35.2761
7.3 | 5.8885 | 1 | 7.824 | 276 | 35.2761
7.2 | 5.7019 | 1 | 7.824 | 276 | 35.2761
6.9 | 5.3274 | 1 | 7.824 | 276 | 35.2761
6.9 | 4.8968 | 1 | 7.824 | 276 | 35.2761
7.2 | 4.372 | 1 | 7.824 | 276 | 35.2761
7.5 | 4.3026 | 1 | 7.824 | 276 | 35.2761
9.7 | 5.3333 | 1 | 7.824 | 276 | 35.2761
10.8 | 5.5106 | 1 | 7.824 | 276 | 35.2761
12.9 | 7.096 | 1 | 7.824 | 276 | 35.2761
13.9 | 7.7469 | 1 | 7.824 | 276 | 35.2761
15.4 | 8.9028 | 1 | 7.824 | 276 | 35.2761
16.9 | 9.5052 | 1 | 7.824 | 276 | 35.2761
16.5 | 10.1105 | 1 | 7.824 | 276 | 35.2761
15.4 | 10.7768 | 1 | 7.824 | 276 | 35.2761
14.1 | 10.0786 | 1 | 7.824 | 276 | 35.2761
13.5 | 9.5401 | 1 | 7.824 | 276 | 35.2761
13.3 | 9.5864 | 1 | 7.824 | 276 | 35.2761
13.4 | 9.8609 | 1 | 7.824 | 276 | 35.2761
11.2 | 9.3156 | 1 | 7.824 | 276 | 35.2761
9.8 | 7.8923 | 1 | 7.824 | 276 | 35.2761
8.8 | 7.04 | 1 | 7.824 | 276 | 35.2761
8.6 | 6.943 | 1 | 7.824 | 276 | 35.2761
8.1 | 6.6059 | 1 | 7.824 | 276 | 35.2761
7.6 | 6.3597 | 1 | 7.824 | 276 | 35.2761
7.6 | 5.9928 | 1 | 7.824 | 276 | 35.2761
6.9 | 5.8247 | 1 | 7.824 | 276 | 35.2761
6.8 | 5.4095 | 1 | 7.824 | 276 | 35.2761
6.7 | 5.007 | 1 | 7.824 | 276 | 35.2761
6.3 | 4.757 | 1 | 7.824 | 276 | 35.2761
5.8 | 4.5407 | 1 | 7.824 | 276 | 35.2761
6.5 | 4.8615 | 1 | 7.824 | 276 | 35.2761
8.1 | 5.7654 | 1 | 7.824 | 276 | 35.2761
9.2 | 5.7527 | 1 | 7.824 | 276 | 35.2761
10.3 | 5.7175 | 1 | 7.824 | 276 | 35.2761
10.4 | 5.9454 | 1 | 7.824 | 276 | 35.2761
12.3 | 7.2436 | 1 | 7.824 | 276 | 35.2761
11.9 | 6.7246 | 1 | 7.824 | 276 | 35.2761
12.4 | 6.9336 | 1 | 7.824 | 276 | 35.2761
12.5 | 6.7453 | 1 | 7.824 | 276 | 35.2761
12.3 | 6.4967 | 1 | 7.824 | 276 | 35.2761
12.5 | 7.1613 | 1 | 7.824 | 276 | 35.2761
12 | 6.7409 | 1 | 7.824 | 276 | 35.2761
11.4 | 6.6638 | 1 | 7.824 | 276 | 35.2761
10.3 | 5.9357 | 1 | 7.824 | 276 | 35.2761
9.1 | 5.5538 | 1 | 7.824 | 276 | 35.2761
7.9 | 4.8628 | 1 | 7.824 | 276 | 35.2761
6.9 | 4.4179 | 1 | 7.824 | 276 | 35.2761
6.1 | 4.0344 | 1 | 7.824 | 276 | 35.2761
5.2 | 3.6759 | 1 | 7.824 | 276 | 35.2761
4.7 | 3.3648 | 1 | 7.824 | 276 | 35.2761
4 | 3.025 | 1 | 7.824 | 276 | 35.2761
3.8 | 3.0003 | 1 | 7.824 | 276 | 35.2761
3.7 | 2.903 | 1 | 7.824 | 276 | 35.2761
5 | 4.0361 | 1 | 7.824 | 276 | 35.2761
6.8 | 5.3272 | 1 | 7.824 | 276 | 35.2761
8.7 | 6.034 | 1 | 7.824 | 276 | 35.2761
9.7 | 6.2918 | 1 | 7.824 | 276 | 35.2761
10.6 | 6.3553 | 1 | 7.824 | 276 | 35.2761
11.7 | 6.7172 | 1 | 7.824 | 276 | 35.2761
11.8 | 6.9103 | 1 | 7.824 | 276 | 35.2761
12.3 | 7.1539 | 1 | 7.824 | 276 | 35.2761
12.2 | 6.7877 | 1 | 7.824 | 276 | 35.2761
12.2 | 6.6172 | 1 | 7.824 | 276 | 35.2761
12.2 | 7.1053 | 1 | 7.824 | 276 | 35.2761
11.7 | 6.6463 | 1 | 7.824 | 276 | 35.2761
11.4 | 6.0707 | 1 | 7.824 | 276 | 35.2761
9.9 | 5.195 | 1 | 7.824 | 276 | 35.2761
8.2 | 4.5859 | 1 | 7.824 | 276 | 35.2761
7.5 | 3.937 | 1 | 7.824 | 276 | 35.2761
6.5 | 3.5603 | 1 | 7.824 | 276 | 35.2761
5.7 | 3.3621 | 1 | 7.824 | 276 | 35.2761
5.7 | 3.7088 | 1 | 7.824 | 276 | 35.2761
4.8 | 3.2609 | 1 | 7.824 | 276 | 35.2761
4.3 | 2.9872 | 1 | 7.824 | 276 | 35.2761
5.1 | 3.5859 | 1 | 7.824 | 276 | 35.2761
5.3 | 3.7346 | 1 | 7.824 | 276 | 35.2761
5.5 | 3.8013 | 1 | 7.824 | 276 | 35.2761
5.7 | 4.031 | 1 | 7.824 | 276 | 35.2761
6.5 | 4.4551 | 1 | 7.824 | 276 | 35.2761
7.3 | 4.8342 | 1 | 7.824 | 276 | 35.2761
8.2 | 5.4605 | 1 | 7.824 | 276 | 35.2761
9.4 | 5.9519 | 1 | 7.824 | 276 | 35.2761
9.9 | 6.2417 | 1 | 7.824 | 276 | 35.2761
9.9 | 6.4378 | 1 | 7.824 | 276 | 35.2761
10.9 | 6.8147 | 1 | 7.824 | 276 | 35.2761
11.1 | 6.5385 | 1 | 7.824 | 276 | 35.2761
11.9 | 6.579 | 1 | 7.824 | 276 | 35.2761
11.7 | 6.6186 | 1 | 7.824 | 276 | 35.2761
12 | 6.1934 | 1 | 7.824 | 276 | 35.2761
12.1 | 5.7959 | 1 | 7.824 | 276 | 35.2761
11.1 | 5.1561 | 1 | 7.824 | 276 | 35.2761
10.2 | 4.7907 | 1 | 7.824 | 276 | 35.2761
9.2 | 4.9951 | 1 | 7.824 | 276 | 35.2761
7.8 | 5.3388 | 1 | 7.824 | 276 | 35.2761
6.9 | 5.1245 | 1 | 7.824 | 276 | 35.2761
6 | 5.0079 | 1 | 7.824 | 276 | 35.2761
5.8 | 4.7255 | 1 | 7.824 | 276 | 35.2761
5.6 | 4.5764 | 1 | 7.824 | 276 | 35.2761
5.3 | 4.4183 | 1 | 7.824 | 276 | 35.2761
5.3 | 4.3736 | 1 | 7.824 | 276 | 35.2761
5.6 | 4.5759 | 1 | 7.824 | 276 | 35.2761
6.2 | 5.1116 | 1 | 7.824 | 276 | 35.2761
6.9 | 5.6509 | 1 | 7.824 | 276 | 35.2761
8.1 | 6.4357 | 1 | 7.824 | 276 | 35.2761
10.4 | 7.5168 | 1 | 7.824 | 276 | 35.2761
12.3 | 8.4607 | 1 | 7.824 | 276 | 35.2761
13.3 | 8.5562 | 1 | 7.824 | 276 | 35.2761
14.3 | 8.6716 | 1 | 7.824 | 276 | 35.2761
14.3 | 8.6716 | 1 | 7.824 | 276 | 35.2761
14.4 | 8.7936 | 1 | 7.824 | 276 | 35.2761
15.2 | 9.0097 | 1 | 7.824 | 276 | 35.2761
14.7 | 9.008 | 1 | 7.824 | 276 | 35.2761
14.4 | 8.87 | 1 | 7.824 | 276 | 35.2761
13.9 | 8.6386 | 1 | 7.824 | 276 | 35.2761
13.3 | 8.2424 | 1 | 7.824 | 276 | 35.2761
12.2 | 7.4918 | 1 | 7.824 | 276 | 35.2761
11 | 6.5688 | 1 | 7.824 | 276 | 35.2761
9.6 | 6.0596 | 1 | 7.824 | 276 | 35.2761
8.2 | 5.3467 | 1 | 7.824 | 276 | 35.2761
7.1 | 5.0203 | 1 | 7.824 | 276 | 35.2761
6.4 | 4.613 | 1 | 7.824 | 276 | 35.2761
5.7 | 4.37 | 1 | 7.824 | 276 | 35.2761
5.4 | 4.428 | 1 | 7.824 | 276 | 35.2761
5 | 4.1279 | 1 | 7.824 | 276 | 35.2761
5 | 4.1279 | 1 | 7.824 | 276 | 35.2761
6.4 | 4.9959 | 1 | 7.824 | 276 | 35.2761
8.4 | 5.9779 | 1 | 7.824 | 276 | 35.2761
10.8 | 6.4716 | 1 | 7.824 | 276 | 35.2761
12.7 | 7.2265 | 1 | 7.824 | 276 | 35.2761
13.9 | 7.9057 | 1 | 7.824 | 276 | 35.2761
14.6 | 8.1683 | 1 | 7.824 | 276 | 35.2761
15.1 | 8.1377 | 1 | 7.824 | 276 | 35.2761
15.7 | 8.4488 | 1 | 7.824 | 276 | 35.2761
16.5 | 9.0158 | 1 | 7.824 | 276 | 35.2761
16.8 | 8.7934 | 1 | 7.824 | 276 | 35.2761
16.7 | 9.0711 | 1 | 7.824 | 276 | 35.2761
17 | 9.0434 | 1 | 7.824 | 276 | 35.2761
15.5 | 8.7865 | 1 | 7.824 | 276 | 35.2761
13.7 | 7.9438 | 1 | 7.824 | 276 | 35.2761
12.3 | 6.8157 | 1 | 7.824 | 276 | 35.2761
10.2 | 5.3218 | 1 | 7.824 | 276 | 35.2761
9.4 | 5.2519 | 1 | 7.824 | 276 | 35.2761
9 | 4.9697 | 1 | 7.824 | 276 | 35.2761
9 | 5.0785 | 1 | 7.824 | 276 | 35.2761
8.2 | 4.7341 | 1 | 7.824 | 276 | 35.2761
7.1 | 4.7711 | 1 | 7.824 | 276 | 35.2761
6.3 | 4.7246 | 1 | 7.824 | 276 | 35.2761
5.7 | 4.4526 | 1 | 7.824 | 276 | 35.2761
5.5 | 4.5666 | 1 | 7.824 | 276 | 35.2761
6.1 | 4.7926 | 1 | 7.824 | 276 | 35.2761
6.6 | 5.2716 | 1 | 7.824 | 276 | 35.2761
7.7 | 5.9637 | 1 | 7.824 | 276 | 35.2761
9.1 | 7.0601 | 1 | 7.824 | 276 | 35.2761
10.4 | 7.5536 | 1 | 7.824 | 276 | 35.2761
12.2 | 8.7084 | 1 | 7.824 | 276 | 35.2761
14.3 | 9.7914 | 1 | 7.824 | 276 | 35.2761
14.6 | 9.9228 | 1 | 7.824 | 276 | 35.2761
13.4 | 10.8985 | 1 | 7.824 | 276 | 35.2761
14.8 | 11.247 | 1 | 7.824 | 276 | 35.2761
16.9 | 12.0295 | 1 | 7.824 | 276 | 35.2761
17.2 | 12.294 | 1 | 7.824 | 276 | 35.2761
17.4 | 12.564 | 1 | 7.824 | 276 | 35.2761
17.2 | 12.7259 | 1 | 7.824 | 276 | 35.2761
17.1 | 13.3429 | 1 | 7.824 | 276 | 35.2761
16.4 | 13.2766 | 1 | 7.824 | 276 | 35.2761
15.6 | 12.7434 | 1 | 7.824 | 276 | 35.2761
15 | 11.4739 | 1 | 7.824 | 276 | 35.2761
13.6 | 10.9799 | 1 | 7.824 | 276 | 35.2761
12.3 | 11.2172 | 1 | 7.824 | 276 | 35.2761
12.3 | 11.4385 | 1 | 7.824 | 276 | 35.2761
11.2 | 10.6357 | 1 | 7.824 | 276 | 35.2761
10.3 | 9.6411 | 1 | 7.824 | 276 | 35.2761
9.8 | 9.0972 | 1 | 7.824 | 276 | 35.2761
10.2 | 9.4896 | 1 | 7.824 | 276 | 35.2761
12.3 | 10.9994 | 1 | 7.824 | 276 | 35.2761
13.8 | 11.9008 | 1 | 7.824 | 276 | 35.2761
16.1 | 13.5364 | 1 | 7.824 | 276 | 35.2761
17.9 | 14.6695 | 1 | 7.824 | 276 | 35.2761
19.8 | 15.7592 | 1 | 7.824 | 276 | 35.2761
21.9 | 16.4557 | 1 | 7.824 | 276 | 35.2761
21.8 | 16.8577 | 1 | 7.824 | 276 | 35.2761
22.4 | 16.0051 | 1 | 7.824 | 276 | 35.2761
22.1 | 16.1036 | 1 | 7.824 | 276 | 35.2761
21.9 | 15.7738 | 1 | 7.824 | 276 | 35.2761
21.9 | 15.4707 | 1 | 7.824 | 276 | 35.2761
20.5 | 15.1071 | 1 | 7.824 | 276 | 35.2761
19.5 | 14.6319 | 1 | 7.824 | 276 | 35.2761
18.9 | 14.6678 | 1 | 7.824 | 276 | 35.2761
18.5 | 14.3588 | 1 | 7.824 | 276 | 35.2761
17.5 | 13.8154 | 1 | 7.824 | 276 | 35.2761
16.4 | 13.0665 | 1 | 7.824 | 276 | 35.2761
15.7 | 12.4208 | 1 | 7.824 | 276 | 35.2761
15 | 11.9791 | 1 | 7.824 | 276 | 35.2761
14.4 | 11.6266 | 1 | 7.824 | 276 | 35.2761
13.7 | 11.3319 | 1 | 7.824 | 276 | 35.2761
13.2 | 11.1196 | 1 | 7.824 | 276 | 35.2761
13 | 11.0875 | 1 | 7.824 | 276 | 35.2761
13.8 | 11.5838 | 1 | 7.824 | 276 | 35.2761
15.1 | 12.1763 | 1 | 7.824 | 276 | 35.2761
15.8 | 12.7747 | 1 | 7.824 | 276 | 35.2761
18 | 14.0121 | 1 | 7.824 | 276 | 35.2761
21.1 | 15.2334 | 1 | 7.824 | 276 | 35.2761
23.6 | 15.3847 | 1 | 7.824 | 276 | 35.2761
24.6 | 16.2117 | 1 | 7.824 | 276 | 35.2761
25.9 | 15.7402 | 1 | 7.824 | 276 | 35.2761
25.8 | 14.5516 | 1 | 7.824 | 276 | 35.2761
25.7 | 14.7357 | 1 | 7.824 | 276 | 35.2761
25.5 | 14.4378 | 1 | 7.824 | 276 | 35.2761
24.3 | 13.7173 | 1 | 7.824 | 276 | 35.2761
22.5 | 13.671 | 1 | 7.824 | 276 | 35.2761
20.7 | 13.9233 | 1 | 7.824 | 276 | 35.2761
19 | 12.8895 | 1 | 7.824 | 276 | 35.2761
16.9 | 12.0823 | 1 | 7.824 | 276 | 35.2761
17 | 12.3129 | 1 | 7.824 | 276 | 35.2761
15.5 | 11.5943 | 1 | 7.824 | 276 | 35.2761
14.8 | 11.1532 | 1 | 7.824 | 276 | 35.2761
13.8 | 10.675 | 1 | 7.824 | 276 | 35.2761
12.8 | 10.1893 | 1 | 7.824 | 276 | 35.2761
12.4 | 9.9142 | 1 | 7.824 | 276 | 35.2761
11.6 | 9.5072 | 1 | 7.824 | 276 | 35.2761
11.1 | 9.2317 | 1 | 7.824 | 276 | 35.2761
12.6 | 10.0029 | 1 | 7.824 | 276 | 35.2761
14.4 | 10.5546 | 1 | 7.824 | 276 | 35.2761
16.8 | 11.7146 | 1 | 7.824 | 276 | 35.2761
18.9 | 11.8144 | 1 | 7.824 | 276 | 35.2761
20.9 | 11.9891 | 1 | 7.824 | 276 | 35.2761
22 | 12.9238 | 1 | 7.824 | 276 | 35.2761
23.3 | 13.0336 | 1 | 7.824 | 276 | 35.2761
24 | 13.6329 | 1 | 7.824 | 276 | 35.2761
24.6 | 13.9401 | 1 | 7.824 | 276 | 35.2761
24.4 | 14.2 | 1 | 7.824 | 276 | 35.2761
23.8 | 15.4489 | 1 | 7.824 | 276 | 35.2761
22.2 | 14.8569 | 1 | 7.824 | 276 | 35.2761
21.5 | 14.0872 | 1 | 7.824 | 276 | 35.2761
19.8 | 13.612 | 1 | 7.824 | 276 | 35.2761
17.5 | 12.7472 | 1 | 7.824 | 276 | 35.2761
17.8 | 12.9143 | 1 | 7.824 | 276 | 35.2761
17.3 | 12.7135 | 1 | 7.824 | 276 | 35.2761
16 | 12.3843 | 1 | 7.824 | 276 | 35.2761
14.7 | 11.8499 | 1 | 7.824 | 276 | 35.2761
13.7 | 11.2751 | 1 | 7.824 | 276 | 35.2761
13.1 | 10.8125 | 1 | 7.824 | 276 | 35.2761
12.4 | 10.4065 | 1 | 7.824 | 276 | 35.2761
12 | 10.1291 | 1 | 7.824 | 276 | 35.2761
11.9 | 10.0844 | 1 | 7.824 | 276 | 35.2761
12.3 | 10.3108 | 1 | 7.824 | 276 | 35.2761
13.6 | 11.1254 | 1 | 7.824 | 276 | 35.2761
15.3 | 12.2472 | 1 | 7.824 | 276 | 35.2761
17.7 | 13.6176 | 1 | 7.824 | 276 | 35.2761
19.8 | 14.676 | 1 | 7.824 | 276 | 35.2761
21.9 | 15.756 | 1 | 7.824 | 276 | 35.2761
23 | 16.3534 | 1 | 7.824 | 276 | 35.2761
24.7 | 15.8384 | 1 | 7.824 | 276 | 35.2761
24 | 16.1063 | 1 | 7.824 | 276 | 35.2761
23.8 | 15.4182 | 1 | 7.824 | 276 | 35.2761
22.6 | 14.5206 | 1 | 7.824 | 276 | 35.2761
21.5 | 14.6152 | 1 | 7.824 | 276 | 35.2761
20.3 | 14.7587 | 1 | 7.824 | 276 | 35.2761
18.8 | 14.6679 | 1 | 7.824 | 276 | 35.2761
15.9 | 13.4492 | 1 | 7.824 | 276 | 35.2761
15.1 | 12.4251 | 1 | 7.824 | 276 | 35.2761
14.4 | 11.5124 | 1 | 7.824 | 276 | 35.2761
13.6 | 10.5222 | 1 | 7.824 | 276 | 35.2761
13.1 | 10.0136 | 1 | 7.824 | 276 | 35.2761
12.9 | 10.1185 | 1 | 7.824 | 276 | 35.2761
12.8 | 10.3729 | 1 | 7.824 | 276 | 35.2761
12.6 | 10.2859 | 1 | 7.824 | 276 | 35.2761
12 | 9.9727 | 1 | 7.824 | 276 | 35.2761
11.7 | 9.9427 | 1 | 7.824 | 276 | 35.2761
12.2 | 10.1112 | 1 | 7.824 | 276 | 35.2761
12.3 | 10.3073 | 1 | 7.824 | 276 | 35.2761
12.4 | 10.61 | 1 | 7.824 | 276 | 35.2761
12.5 | 10.7055 | 1 | 7.824 | 276 | 35.2761
12.3 | 10.8858 | 1 | 7.824 | 276 | 35.2761
12.6 | 11.4491 | 1 | 7.824 | 276 | 35.2761
13.1 | 11.8235 | 1 | 7.824 | 276 | 35.2761
13.5 | 12.0994 | 1 | 7.824 | 276 | 35.2761
13.9 | 12.4861 | 1 | 7.824 | 276 | 35.2761
14.4 | 12.5753 | 1 | 7.824 | 276 | 35.2761
14.6 | 12.5454 | 1 | 7.824 | 276 | 35.2761
14.8 | 12.5713 | 1 | 7.824 | 276 | 35.2761
14.7 | 12.3671 | 1 | 7.824 | 276 | 35.2761
13.9 | 12.0967 | 1 | 7.824 | 276 | 35.2761
13.3 | 11.9049 | 1 | 7.824 | 276 | 35.2761
12.8 | 11.6983 | 1 | 7.824 | 276 | 35.2761
12.6 | 11.7278 | 1 | 7.824 | 276 | 35.2761
12.6 | 11.7844 | 1 | 7.824 | 276 | 35.2761
13.1 | 10.0136 | 1 | 7.824 | 276 | 35.2761
12.5 | 11.6299 | 1 | 7.824 | 276 | 35.2761
12.4 | 11.309 | 1 | 7.824 | 276 | 35.2761
11 | 10.3255 | 1 | 7.824 | 276 | 35.2761
10.4 | 9.7897 | 1 | 7.824 | 276 | 35.2761
11.1 | 10.4786 | 1 | 7.824 | 276 | 35.2761
10.9 | 9.7966 | 1 | 7.824 | 276 | 35.2761
11.2 | 9.9288 | 1 | 7.824 | 276 | 35.2761
12.6 | 10.9054 | 1 | 7.824 | 276 | 35.2761
13.7 | 11.5281 | 1 | 7.824 | 276 | 35.2761
15.4 | 12.1768 | 1 | 7.824 | 276 | 35.2761
15.8 | 12.0342 | 1 | 7.824 | 276 | 35.2761
16.8 | 11.9581 | 1 | 7.824 | 276 | 35.2761
18.7 | 12.6821 | 1 | 7.824 | 276 | 35.2761
18.5 | 12.2827 | 1 | 7.824 | 276 | 35.2761
18.5 | 11.8899 | 1 | 7.824 | 276 | 35.2761
18.1 | 12.2075 | 1 | 7.824 | 276 | 35.2761
15.8 | 11.9314 | 1 | 7.824 | 276 | 35.2761
15.6 | 12.6197 | 1 | 7.824 | 276 | 35.2761
15.3 | 12.0805 | 1 | 7.824 | 276 | 35.2761
14.7 | 11.5776 | 1 | 7.824 | 276 | 35.2761
14.4 | 11.8164 | 1 | 7.824 | 276 | 35.2761
13.5 | 11.1265 | 1 | 7.824 | 276 | 35.2761
12.6 | 11.2267 | 1 | 7.824 | 276 | 35.2761
12.1 | 11.0157 | 1 | 7.824 | 276 | 35.2761
11.9 | 11.0412 | 1 | 7.824 | 276 | 35.2761
11.8 | 10.6683 | 1 | 7.824 | 276 | 35.2761
11.8 | 10.6141 | 1 | 7.824 | 276 | 35.2761
11.2 | 10.6872 | 1 | 7.824 | 276 | 35.2761
11.3 | 10.5081 | 1 | 7.824 | 276 | 35.2761
11.1 | 10.3666 | 1 | 7.824 | 276 | 35.2761
11.4 | 10.8282 | 1 | 7.824 | 276 | 35.2761
11.7 | 10.9555 | 1 | 7.824 | 276 | 35.2761
13.4 | 12.109 | 1 | 7.824 | 276 | 35.2761
13.3 | 12.1814 | 1 | 7.824 | 276 | 35.2761
14.1 | 12.5605 | 1 | 7.824 | 276 | 35.2761
15.2 | 12.7228 | 1 | 7.824 | 276 | 35.2761
14.9 | 13.1614 | 1 | 7.824 | 276 | 35.2761
14.7 | 12.5248 | 1 | 7.824 | 276 | 35.2761
13.4 | 11.6129 | 1 | 7.824 | 276 | 35.2761
14.9 | 12.442 | 1 | 7.824 | 276 | 35.2761
14.3 | 11.4597 | 1 | 7.824 | 276 | 35.2761
13.8 | 11.199 | 1 | 7.824 | 276 | 35.2761
13.2 | 10.4879 | 1 | 7.824 | 276 | 35.2761
12.6 | 9.6864 | 1 | 7.824 | 276 | 35.2761
11.6 | 9.7395 | 1 | 7.824 | 276 | 35.2761
11.2 | 9.7171 | 1 | 7.824 | 276 | 35.2761
10.9 | 9.4804 | 1 | 7.824 | 276 | 35.2761
10.9 | 9.3774 | 1 | 7.824 | 276 | 35.2761
10.5 | 9.2492 | 1 | 7.824 | 276 | 35.2761
10.5 | 9.0431 | 1 | 7.824 | 276 | 35.2761
10.6 | 8.9358 | 1 | 7.824 | 276 | 35.2761
10.4 | 9.1509 | 1 | 7.824 | 276 | 35.2761
9 | 7.3598 | 1 | 7.824 | 276 | 35.2761
8.6 | 6.6999 | 1 | 7.824 | 276 | 35.2761
8.4 | 6.4658 | 1 | 7.824 | 276 | 35.2761
8.3 | 6.4177 | 1 | 7.824 | 276 | 35.2761
7.4 | 6.021 | 1 | 7.824 | 276 | 35.2761
7.3 | 6.2056 | 1 | 7.824 | 276 | 35.2761
7.6 | 5.849 | 1 | 7.824 | 276 | 35.2761
7.4 | 6.3503 | 1 | 7.824 | 276 | 35.2761
7.8 | 6.4531 | 1 | 7.824 | 276 | 35.2761
7.7 | 6.594 | 1 | 7.824 | 276 | 35.2761
7 | 6.0589 | 1 | 7.824 | 276 | 35.2761
7.7 | 6.6425 | 1 | 7.824 | 276 | 35.2761
8.2 | 7.1274 | 1 | 7.824 | 276 | 35.2761
8.6 | 7.9166 | 1 | 7.824 | 276 | 35.2761
9 | 8.3092 | 1 | 7.824 | 276 | 35.2761
9.2 | 8.4539 | 1 | 7.824 | 276 | 35.2761
8.9 | 8.1093 | 1 | 7.824 | 276 | 35.2761
8.7 | 8.0156 | 1 | 7.824 | 276 | 35.2761
9.4 | 8.4956 | 1 | 7.824 | 276 | 35.2761
9.6 | 8.5368 | 1 | 7.824 | 276 | 35.2761
9.7 | 8.6855 | 1 | 7.824 | 276 | 35.2761
10 | 8.5714 | 1 | 7.824 | 276 | 35.2761
9.8 | 7.2525 | 1 | 7.824 | 276 | 35.2761
9.3 | 6.9218 | 1 | 7.824 | 276 | 35.2761
8.6 | 7.0388 | 1 | 7.824 | 276 | 35.2761
8.7 | 6.5417 | 1 | 7.824 | 276 | 35.2761
9.1 | 6.7834 | 1 | 7.824 | 276 | 35.2761
10.1 | 7.314 | 1 | 7.824 | 276 | 35.2761
11.3 | 8.1053 | 1 | 7.824 | 276 | 35.2761
11.5 | 8.3329 | 1 | 7.824 | 276 | 35.2761
12.3 | 8.5752 | 1 | 7.824 | 276 | 35.2761
13.4 | 8.9963 | 1 | 7.824 | 276 | 35.2761
15 | 9.2011 | 1 | 7.824 | 276 | 35.2761
14.9 | 8.9647 | 1 | 7.824 | 276 | 35.2761
15.3 | 9.2606 | 1 | 7.824 | 276 | 35.2761
14.2 | 9.1973 | 1 | 7.824 | 276 | 35.2761
14.1 | 9.1518 | 1 | 7.824 | 276 | 35.2761
14.7 | 9.5874 | 1 | 7.824 | 276 | 35.2761
13.9 | 9.4397 | 1 | 7.824 | 276 | 35.2761
13.3 | 8.9545 | 1 | 7.824 | 276 | 35.2761
11.4 | 8.3364 | 1 | 7.824 | 276 | 35.2761
10.2 | 7.9997 | 1 | 7.824 | 276 | 35.2761
9.1 | 7.6667 | 1 | 7.824 | 276 | 35.2761
7.7 | 6.7959 | 1 | 7.824 | 276 | 35.2761
7.9 | 7.1371 | 1 | 7.824 | 276 | 35.2761
9.4 | 8.3999 | 1 | 7.824 | 276 | 35.2761
7.9 | 7.3356 | 1 | 7.824 | 276 | 35.2761
7.1 | 6.6469 | 1 | 7.824 | 276 | 35.2761
8.3 | 7.7798 | 1 | 7.824 | 276 | 35.2761
8.9 | 8.3711 | 1 | 7.824 | 276 | 35.2761
10.3 | 9.4844 | 1 | 7.824 | 276 | 35.2761
12.1 | 10.3892 | 1 | 7.824 | 276 | 35.2761
13.7 | 11.1838 | 1 | 7.824 | 276 | 35.2761
14.5 | 11.5738 | 1 | 7.824 | 276 | 35.2761
15.4 | 11.8014 | 1 | 7.824 | 276 | 35.2761
15.4 | 11.318 | 1 | 7.824 | 276 | 35.2761
15.5 | 10.8986 | 1 | 7.824 | 276 | 35.2761
15.5 | 11.1732 | 1 | 7.824 | 276 | 35.2761
15.6 | 11.309 | 1 | 7.824 | 276 | 35.2761
15.8 | 11.5346 | 1 | 7.824 | 276 | 35.2761
15.2 | 11.4727 | 1 | 7.824 | 276 | 35.2761
15.5 | 11.4078 | 1 | 7.824 | 276 | 35.2761
15.5 | 11.4078 | 1 | 7.824 | 276 | 35.2761
14.8 | 11.4011 | 1 | 7.824 | 276 | 35.2761
14.8 | 11.1098 | 1 | 7.824 | 276 | 35.2761
13.5 | 10.9965 | 1 | 7.824 | 276 | 35.2761
13.6 | 10.7887 | 1 | 7.824 | 276 | 35.2761
12.8 | 10.4911 | 1 | 7.824 | 276 | 35.2761
11.7 | 10.059 | 1 | 7.824 | 276 | 35.2761
11.5 | 10.0737 | 1 | 7.824 | 276 | 35.2761
11.5 | 10.0737 | 1 | 7.824 | 276 | 35.2761
11 | 9.8515 | 1 | 7.824 | 276 | 35.2761
11.3 | 10.1424 | 1 | 7.824 | 276 | 35.2761
12.2 | 10.7477 | 1 | 7.824 | 276 | 35.2761
13.6 | 11.4525 | 1 | 7.824 | 276 | 35.2761
15.3 | 12.2157 | 1 | 7.824 | 276 | 35.2761
15.9 | 12.4114 | 1 | 7.824 | 276 | 35.2761
16 | 12.1033 | 1 | 7.824 | 276 | 35.2761
16.9 | 11.9525 | 1 | 7.824 | 276 | 35.2761
18.1 | 12.4934 | 1 | 7.824 | 276 | 35.2761
17.4 | 12.3453 | 1 | 7.824 | 276 | 35.2761
17.8 | 12.2792 | 1 | 7.824 | 276 | 35.2761
17.5 | 12.2934 | 1 | 7.824 | 276 | 35.2761
17.6 | 12.568 | 1 | 7.824 | 276 | 35.2761
17.4 | 12.1578 | 1 | 7.824 | 276 | 35.2761
17.3 | 11.8912 | 1 | 7.824 | 276 | 35.2761
16.2 | 11.7517 | 1 | 7.824 | 276 | 35.2761
16.5 | 11.6012 | 1 | 7.824 | 276 | 35.2761
13.7 | 10.4933 | 1 | 7.824 | 276 | 35.2761
12.5 | 9.2558 | 1 | 7.824 | 276 | 35.2761
11.5 | 8.8449 | 1 | 7.824 | 276 | 35.2761
10.6 | 8.5215 | 1 | 7.824 | 276 | 35.2761
10.5 | 8.6671 | 1 | 7.824 | 276 | 35.2761
9.8 | 8.5884 | 1 | 7.824 | 276 | 35.2761
9.1 | 8.0598 | 1 | 7.824 | 276 | 35.2761
8.4 | 7.627 | 1 | 7.824 | 276 | 35.2761
9 | 8.0125 | 1 | 7.824 | 276 | 35.2761
10.3 | 8.7698 | 1 | 7.824 | 276 | 35.2761
12.3 | 9.3961 | 1 | 7.824 | 276 | 35.2761
14.6 | 10.1529 | 1 | 7.824 | 276 | 35.2761
16.3 | 10.2301 | 1 | 7.824 | 276 | 35.2761
16.4 | 10.5575 | 1 | 7.824 | 276 | 35.2761
17 | 10.9413 | 1 | 7.824 | 276 | 35.2761
17.7 | 11.4484 | 1 | 7.824 | 276 | 35.2761
17.6 | 11.7461 | 1 | 7.824 | 276 | 35.2761
17.3 | 11.1921 | 1 | 7.824 | 276 | 35.2761
17.8 | 11.4436 | 1 | 7.824 | 276 | 35.2761
17.4 | 11.1904 | 1 | 7.824 | 276 | 35.2761
17.2 | 11.1468 | 1 | 7.824 | 276 | 35.2761
16.8 | 10.6447 | 1 | 7.824 | 276 | 35.2761
15.4 | 9.7857 | 1 | 7.824 | 276 | 35.2761
13.9 | 8.5518 | 1 | 7.824 | 276 | 35.2761
12.9 | 8.4035 | 1 | 7.824 | 276 | 35.2761
12.3 | 7.8801 | 1 | 7.824 | 276 | 35.2761
11.5 | 7.7424 | 1 | 7.824 | 276 | 35.2761
10.9 | 7.006 | 1 | 7.824 | 276 | 35.2761
10.3 | 6.6324 | 1 | 7.824 | 276 | 35.2761
9.5 | 6.3967 | 1 | 7.824 | 276 | 35.2761
8.9 | 6.1384 | 1 | 7.824 | 276 | 35.2761
8.7 | 6.2057 | 1 | 7.824 | 276 | 35.2761
8.8 | 6.5132 | 1 | 7.824 | 276 | 35.2761
10.5 | 7.6029 | 1 | 7.824 | 276 | 35.2761
12.4 | 8.8906 | 1 | 7.824 | 276 | 35.2761
14.4 | 9.9706 | 1 | 7.824 | 276 | 35.2761
16.1 | 10.8888 | 1 | 7.824 | 276 | 35.2761
16.5 | 10.9315 | 1 | 7.824 | 276 | 35.2761
17.6 | 11.443 | 1 | 7.824 | 276 | 35.2761
17.9 | 11.3206 | 1 | 7.824 | 276 | 35.2761
18.5 | 11.6558 | 1 | 7.824 | 276 | 35.2761
19 | 12.2784 | 1 | 7.824 | 276 | 35.2761
18.7 | 11.9434 | 1 | 7.824 | 276 | 35.2761
18.5 | 11.7352 | 1 | 7.824 | 276 | 35.2761
18.4 | 11.4484 | 1 | 7.824 | 276 | 35.2761
17.4 | 10.9416 | 1 | 7.824 | 276 | 35.2761
16.2 | 10.5042 | 1 | 7.824 | 276 | 35.2761
15.6 | 9.6741 | 1 | 7.824 | 276 | 35.2761
14.3 | 9.9261 | 1 | 7.824 | 276 | 35.2761
13.1 | 9.2548 | 1 | 7.824 | 276 | 35.2761
12.4 | 8.8906 | 1 | 7.824 | 276 | 35.2761
11.7 | 8.5671 | 1 | 7.824 | 276 | 35.2761
11 | 8.4228 | 1 | 7.824 | 276 | 35.2761
10.4 | 8.2821 | 1 | 7.824 | 276 | 35.2761
9.6 | 7.9526 | 1 | 7.824 | 276 | 35.2761
9.1 | 7.7149 | 1 | 7.824 | 276 | 35.2761
9 | 7.8132 | 1 | 7.824 | 276 | 35.2761
11 | 9.2874 | 1 | 7.824 | 276 | 35.2761
12.3 | 10.4759 | 1 | 7.824 | 276 | 35.2761
14.6 | 11.7175 | 1 | 7.824 | 276 | 35.2761
16.7 | 12.8335 | 1 | 7.824 | 276 | 35.2761
18.9 | 13.5609 | 1 | 7.824 | 276 | 35.2761
20 | 13.8007 | 1 | 7.824 | 276 | 35.2761
21.3 | 14.2571 | 1 | 7.824 | 276 | 35.2761
22 | 13.6533 | 1 | 7.824 | 276 | 35.2761
22.2 | 13.9383 | 1 | 7.824 | 276 | 35.2761
22.5 | 13.4806 | 1 | 7.824 | 276 | 35.2761
22.3 | 13.2052 | 1 | 7.824 | 276 | 35.2761
21.8 | 13.0056 | 1 | 7.824 | 276 | 35.2761
21 | 12.8029 | 1 | 7.824 | 276 | 35.2761
19.3 | 12.0272 | 1 | 7.824 | 276 | 35.2761
17.4 | 11.4864 | 1 | 7.824 | 276 | 35.2761
15.3 | 10.4545 | 1 | 7.824 | 276 | 35.2761
13.9 | 9.9712 | 1 | 7.824 | 276 | 35.2761
13.9 | 10.1552 | 1 | 7.824 | 276 | 35.2761
13.8 | 10.297 | 1 | 7.824 | 276 | 35.2761
13.1 | 9.752 | 1 | 7.824 | 276 | 35.2761
12.2 | 9.394 | 1 | 7.824 | 276 | 35.2761
11.1 | 8.9887 | 1 | 7.824 | 276 | 35.2761
10.7 | 8.9518 | 1 | 7.824 | 276 | 35.2761
10.8 | 9.0966 | 1 | 7.824 | 276 | 35.2761
12.3 | 9.823 | 1 | 7.824 | 276 | 35.2761
15.2 | 10.7672 | 1 | 7.824 | 276 | 35.2761
17.6 | 11.8755 | 1 | 7.824 | 276 | 35.2761
18 | 11.7412 | 1 | 7.824 | 276 | 35.2761
19.5 | 12.8332 | 1 | 7.824 | 276 | 35.2761
20.2 | 13.1549 | 1 | 7.824 | 276 | 35.2761
21.7 | 14.0509 | 1 | 7.824 | 276 | 35.2761
22.3 | 14.1514 | 1 | 7.824 | 276 | 35.2761
22.7 | 14.1315 | 1 | 7.824 | 276 | 35.2761
23.3 | 14.2783 | 1 | 7.824 | 276 | 35.2761
22.6 | 14.0088 | 1 | 7.824 | 276 | 35.2761
21 | 14.4645 | 1 | 7.824 | 276 | 35.2761
19.4 | 13.283 | 1 | 7.824 | 276 | 35.2761
18.2 | 12.5709 | 1 | 7.824 | 276 | 35.2761
16.3 | 10.9725 | 1 | 7.824 | 276 | 35.2761
14.6 | 10.738 | 1 | 7.824 | 276 | 35.2761
13.2 | 10.1259 | 1 | 7.824 | 276 | 35.2761
11.9 | 9.7923 | 1 | 7.824 | 276 | 35.2761
11.3 | 9.8799 | 1 | 7.824 | 276 | 35.2761
12.1 | 10.6502 | 1 | 7.824 | 276 | 35.2761
11.8 | 10.4139 | 1 | 7.824 | 276 | 35.2761
11.5 | 10.124 | 1 | 7.824 | 276 | 35.2761
11.3 | 9.725 | 1 | 7.824 | 276 | 35.2761
10.9 | 9.4432 | 1 | 7.824 | 276 | 35.2761
10.5 | 8.8592 | 1 | 7.824 | 276 | 35.2761
10.8 | 8.9969 | 1 | 7.824 | 276 | 35.2761
11.4 | 9.3194 | 1 | 7.824 | 276 | 35.2761
12.2 | 9.7772 | 1 | 7.824 | 276 | 35.2761
14.2 | 10.9953 | 1 | 7.824 | 276 | 35.2761
16 | 12.0478 | 1 | 7.824 | 276 | 35.2761
16.6 | 12.1966 | 1 | 7.824 | 276 | 35.2761
18.2 | 12.9404 | 1 | 7.824 | 276 | 35.2761
19.3 | 13.1464 | 1 | 7.824 | 276 | 35.2761
20.1 | 13.83 | 1 | 7.824 | 276 | 35.2761
20.4 | 14.2306 | 1 | 7.824 | 276 | 35.2761
20.3 | 14.0966 | 1 | 7.824 | 276 | 35.2761
19.4 | 13.9918 | 1 | 7.824 | 276 | 35.2761
18.1 | 13.5857 | 1 | 7.824 | 276 | 35.2761
16.6 | 12.9918 | 1 | 7.824 | 276 | 35.2761
15.5 | 12.6008 | 1 | 7.824 | 276 | 35.2761
15 | 12.7191 | 1 | 7.824 | 276 | 35.2761
14.5 | 12.7367 | 1 | 7.824 | 276 | 35.2761
15.1 | 13.0331 | 1 | 7.824 | 276 | 35.2761
14.4 | 12.6964 | 1 | 7.824 | 276 | 35.2761
14.2 | 12.5043 | 1 | 7.824 | 276 | 35.2761
13.4 | 12.0102 | 1 | 7.824 | 276 | 35.2761
12.5 | 11.5235 | 1 | 7.824 | 276 | 35.2761
12.3 | 11.0551 | 1 | 7.824 | 276 | 35.2761
13.1 | 11.4487 | 1 | 7.824 | 276 | 35.2761
14.2 | 12.2848 | 1 | 7.824 | 276 | 35.2761
15.2 | 13.073 | 1 | 7.824 | 276 | 35.2761
16.9 | 13.6896 | 1 | 7.824 | 276 | 35.2761
18.6 | 14.2413 | 1 | 7.824 | 276 | 35.2761
20.4 | 15.1275 | 1 | 7.824 | 276 | 35.2761
21.5 | 15.0337 | 1 | 7.824 | 276 | 35.2761
21.3 | 14.7646 | 1 | 7.824 | 276 | 35.2761
22.3 | 15.976 | 1 | 7.824 | 276 | 35.2761
22.7 | 16.3736 | 1 | 7.824 | 276 | 35.2761
22.8 | 16.7759 | 1 | 7.824 | 276 | 35.2761
22.1 | 16.5302 | 1 | 7.824 | 276 | 35.2761
21.2 | 16.3745 | 1 | 7.824 | 276 | 35.2761
20.2 | 15.9621 | 1 | 7.824 | 276 | 35.2761
19.4 | 16.0702 | 1 | 7.824 | 276 | 35.2761
17.8 | 15.1424 | 1 | 7.824 | 276 | 35.2761
16.4 | 14.3298 | 1 | 7.824 | 276 | 35.2761
15.6 | 13.4543 | 1 | 7.824 | 276 | 35.2761
14.5 | 12.9049 | 1 | 7.824 | 276 | 35.2761
14.3 | 12.7683 | 1 | 7.824 | 276 | 35.2761
14.2 | 12.7842 | 1 | 7.824 | 276 | 35.2761
14.4 | 12.9205 | 1 | 7.824 | 276 | 35.2761
14.4 | 13.0908 | 1 | 7.824 | 276 | 35.2761
14.2 | 13.0114 | 1 | 7.824 | 276 | 35.2761
14 | 12.5908 | 1 | 7.824 | 276 | 35.2761
14.3 | 12.7683 | 1 | 7.824 | 276 | 35.2761
14.9 | 13.0651 | 1 | 7.824 | 276 | 35.2761
16.2 | 13.6356 | 1 | 7.824 | 276 | 35.2761
17.7 | 14.4347 | 1 | 7.824 | 276 | 35.2761
19.2 | 15.5464 | 1 | 7.824 | 276 | 35.2761
19.7 | 15.9522 | 1 | 7.824 | 276 | 35.2761
19.7 | 15.9535 | 1 | 7.824 | 276 | 35.2761
20.8 | 16.5149 | 1 | 7.824 | 276 | 35.2761
19.8 | 16.3304 | 1 | 7.824 | 276 | 35.2761
19.8 | 16.3879 | 1 | 7.824 | 276 | 35.2761
20.5 | 16.8643 | 1 | 7.824 | 276 | 35.2761
20.2 | 16.8177 | 1 | 7.824 | 276 | 35.2761
19.6 | 16.4899 | 1 | 7.824 | 276 | 35.2761
19 | 16.2779 | 1 | 7.824 | 276 | 35.2761
18.3 | 15.9087 | 1 | 7.824 | 276 | 35.2761
17.4 | 15.2858 | 1 | 7.824 | 276 | 35.2761
16.9 | 15.0414 | 1 | 7.824 | 276 | 35.2761
16.7 | 14.8493 | 1 | 7.824 | 276 | 35.2761
16.8 | 15.0041 | 1 | 7.824 | 276 | 35.2761
16.2 | 14.8381 | 1 | 7.824 | 276 | 35.2761
15.8 | 14.5682 | 1 | 7.824 | 276 | 35.2761
15.7 | 14.4709 | 1 | 7.824 | 276 | 35.2761
15.7 | 14.4709 | 1 | 7.824 | 276 | 35.2761
15.9 | 14.6656 | 1 | 7.824 | 276 | 35.2761
16.4 | 14.9131 | 1 | 7.824 | 276 | 35.2761
17.1 | 15.2329 | 1 | 7.824 | 276 | 35.2761
18.4 | 15.8265 | 1 | 7.824 | 276 | 35.2761
19 | 16.2181 | 1 | 7.824 | 276 | 35.2761
20.6 | 16.6693 | 1 | 7.824 | 276 | 35.2761
21.1 | 16.7878 | 1 | 7.824 | 276 | 35.2761
22.8 | 17.4872 | 1 | 7.824 | 276 | 35.2761
23.1 | 17.813 | 1 | 7.824 | 276 | 35.2761
23.4 | 18.0265 | 1 | 7.824 | 276 | 35.2761
23.3 | 17.8224 | 1 | 7.824 | 276 | 35.2761
23.5 | 18.1146 | 1 | 7.824 | 276 | 35.2761
22.6 | 17.6991 | 1 | 7.824 | 276 | 35.2761
21.1 | 17.0141 | 1 | 7.824 | 276 | 35.2761
19.3 | 16.1507 | 1 | 7.824 | 276 | 35.2761
17.9 | 15.4109 | 1 | 7.824 | 276 | 35.2761
17.3 | 15.3658 | 1 | 7.824 | 276 | 35.2761
15.9 | 14.6656 | 1 | 7.824 | 276 | 35.2761
15.4 | 14.2379 | 1 | 7.824 | 276 | 35.2761
14.4 | 12.9776 | 1 | 7.824 | 276 | 35.2761
13.3 | 11.9699 | 1 | 7.824 | 276 | 35.2761
12.2 | 11.0134 | 1 | 7.824 | 276 | 35.2761
11.4 | 10.397 | 1 | 7.824 | 276 | 35.2761
12.1 | 10.8624 | 1 | 7.824 | 276 | 35.2761
13.2 | 11.3855 | 1 | 7.824 | 276 | 35.2761
14.6 | 11.972 | 1 | 7.824 | 276 | 35.2761
15.8 | 12.517 | 1 | 7.824 | 276 | 35.2761
17.4 | 13.111 | 1 | 7.824 | 276 | 35.2761
18.7 | 13.1425 | 1 | 7.824 | 276 | 35.2761
19.6 | 13.8303 | 1 | 7.824 | 276 | 35.2761
21 | 14.0445 | 1 | 7.824 | 276 | 35.2761
21 | 14.0445 | 1 | 7.824 | 276 | 35.2761
21.7 | 14.4937 | 1 | 7.824 | 276 | 35.2761
22.2 | 14.4115 | 1 | 7.824 | 276 | 35.2761
22.2 | 14.5917 | 1 | 7.824 | 276 | 35.2761
22 | 14.3772 | 1 | 7.824 | 276 | 35.2761
21.1 | 14.309 | 1 | 7.824 | 276 | 35.2761
19.8 | 13.7132 | 1 | 7.824 | 276 | 35.2761
18.8 | 13.4668 | 1 | 7.824 | 276 | 35.2761
17.7 | 13.3795 | 1 | 7.824 | 276 | 35.2761
17.5 | 13.6086 | 1 | 7.824 | 276 | 35.2761
16.4 | 13.3336 | 1 | 7.824 | 276 | 35.2761
14.9 | 12.7886 | 1 | 7.824 | 276 | 35.2761
14.2 | 12.1764 | 1 | 7.824 | 276 | 35.2761
13.1 | 11.3416 | 1 | 7.824 | 276 | 35.2761
12 | 10.8183 | 1 | 7.824 | 276 | 35.2761
12.6 | 11.075 | 1 | 7.824 | 276 | 35.2761
12.4 | 11.0973 | 1 | 7.824 | 276 | 35.2761
13.1 | 11.448 | 1 | 7.824 | 276 | 35.2761
14.5 | 12.1382 | 1 | 7.824 | 276 | 35.2761
16.1 | 12.8418 | 1 | 7.824 | 276 | 35.2761
18.2 | 13.7246 | 1 | 7.824 | 276 | 35.2761
19.1 | 13.152 | 1 | 7.824 | 276 | 35.2761
20.6 | 12.9128 | 1 | 7.824 | 276 | 35.2761
21.4 | 11.7916 | 1 | 7.824 | 276 | 35.2761
21.7 | 13.1032 | 1 | 7.824 | 276 | 35.2761
23 | 12.8616 | 1 | 7.824 | 276 | 35.2761
23.1 | 13.3048 | 1 | 7.824 | 276 | 35.2761
21.4 | 12.9803 | 1 | 7.824 | 276 | 35.2761
22.2 | 13.4181 | 1 | 7.824 | 276 | 35.2761
21.4 | 13.0173 | 1 | 7.824 | 276 | 35.2761
19.8 | 12.6242 | 1 | 7.824 | 276 | 35.2761
18.5 | 13.1451 | 1 | 7.824 | 276 | 35.2761
16.9 | 12.6506 | 1 | 7.824 | 276 | 35.2761
15.5 | 12.0292 | 1 | 7.824 | 276 | 35.2761
14.1 | 11.4985 | 1 | 7.824 | 276 | 35.2761
13 | 11.085 | 1 | 7.824 | 276 | 35.2761
12.5 | 10.8712 | 1 | 7.824 | 276 | 35.2761
12.1 | 10.6458 | 1 | 7.824 | 276 | 35.2761
12 | 10.7092 | 1 | 7.824 | 276 | 35.2761
11.7 | 10.5795 | 1 | 7.824 | 276 | 35.2761
11.6 | 9.9575 | 1 | 7.824 | 276 | 35.2761
12.6 | 9.8042 | 1 | 7.824 | 276 | 35.2761
13.2 | 9.8357 | 1 | 7.824 | 276 | 35.2761
14.5 | 10.5465 | 1 | 7.824 | 276 | 35.2761
15.5 | 11.0236 | 1 | 7.824 | 276 | 35.2761
15.7 | 11.2028 | 1 | 7.824 | 276 | 35.2761
15.9 | 10.6633 | 1 | 7.824 | 276 | 35.2761
15.9 | 10.2828 | 1 | 7.824 | 276 | 35.2761
16.8 | 10.2759 | 1 | 7.824 | 276 | 35.2761
18.4 | 10.6019 | 1 | 7.824 | 276 | 35.2761
18.4 | 11.0492 | 1 | 7.824 | 276 | 35.2761
18.4 | 10.9727 | 1 | 7.824 | 276 | 35.2761
16.9 | 10.6396 | 1 | 7.824 | 276 | 35.2761
16.9 | 10.7207 | 1 | 7.824 | 276 | 35.2761
16.8 | 10.8866 | 1 | 7.824 | 276 | 35.2761
15.9 | 10.5393 | 1 | 7.824 | 276 | 35.2761
14.3 | 10.0551 | 1 | 7.824 | 276 | 35.2761
13 | 9.7044 | 1 | 7.824 | 276 | 35.2761
12 | 9.301 | 1 | 7.824 | 276 | 35.2761
11.9 | 9.3032 | 1 | 7.824 | 276 | 35.2761
10.6 | 9.003 | 1 | 7.824 | 276 | 35.2761
10 | 8.3795 | 1 | 7.824 | 276 | 35.2761
8.5 | 7.376 | 1 | 7.824 | 276 | 35.2761
8.3 | 6.9903 | 1 | 7.824 | 276 | 35.2761
8.8 | 7.375 | 1 | 7.824 | 276 | 35.2761
11.2 | 8.9802 | 1 | 7.824 | 276 | 35.2761
13.4 | 9.4223 | 1 | 7.824 | 276 | 35.2761
15.5 | 11.3465 | 1 | 7.824 | 276 | 35.2761
18 | 13.4385 | 1 | 7.824 | 276 | 35.2761
20.7 | 14.3812 | 1 | 7.824 | 276 | 35.2761
22.1 | 15.048 | 1 | 7.824 | 276 | 35.2761
23.2 | 14.8533 | 1 | 7.824 | 276 | 35.2761
24.3 | 15.349 | 1 | 7.824 | 276 | 35.2761
24.8 | 16.0251 | 1 | 7.824 | 276 | 35.2761
24.5 | 16.4858 | 1 | 7.824 | 276 | 35.2761
24.7 | 17.0499 | 1 | 7.824 | 276 | 35.2761
24.3 | 17.0632 | 1 | 7.824 | 276 | 35.2761
23.5 | 16.9969 | 1 | 7.824 | 276 | 35.2761
22.4 | 17.2175 | 1 | 7.824 | 276 | 35.2761
21.9 | 17.159 | 1 | 7.824 | 276 | 35.2761
19.8 | 15.9153 | 1 | 7.824 | 276 | 35.2761
19 | 15.7413 | 1 | 7.824 | 276 | 35.2761
17.8 | 14.734 | 1 | 7.824 | 276 | 35.2761
16 | 13.8248 | 1 | 7.824 | 276 | 35.2761
15.4 | 12.7621 | 1 | 7.824 | 276 | 35.2761
14.6 | 12.4932 | 1 | 7.824 | 276 | 35.2761
16 | 13.8248 | 1 | 7.824 | 276 | 35.2761
12.9 | 11.4653 | 1 | 7.824 | 276 | 35.2761
12.2 | 11.2261 | 1 | 7.824 | 276 | 35.2761
12.4 | 11.0912 | 1 | 7.824 | 276 | 35.2761
12.5 | 11.4077 | 1 | 7.824 | 276 | 35.2761
13 | 11.4527 | 1 | 7.824 | 276 | 35.2761
13.7 | 11.7443 | 1 | 7.824 | 276 | 35.2761
14.8 | 12.4096 | 1 | 7.824 | 276 | 35.2761
14.9 | 12.3964 | 1 | 7.824 | 276 | 35.2761
16.6 | 13.6657 | 1 | 7.824 | 276 | 35.2761
17.3 | 13.5619 | 1 | 7.824 | 276 | 35.2761
16.8 | 13.5268 | 1 | 7.824 | 276 | 35.2761
18.4 | 14.5703 | 1 | 7.824 | 276 | 35.2761
18.3 | 13.9467 | 1 | 7.824 | 276 | 35.2761
18.5 | 13.5652 | 1 | 7.824 | 276 | 35.2761
18.3 | 13.1415 | 1 | 7.824 | 276 | 35.2761
17 | 12.7234 | 1 | 7.824 | 276 | 35.2761
16 | 12.7323 | 1 | 7.824 | 276 | 35.2761
15 | 12.3835 | 1 | 7.824 | 276 | 35.2761
14.6 | 12.7119 | 1 | 7.824 | 276 | 35.2761
13.6 | 12.9408 | 1 | 7.824 | 276 | 35.2761
13.5 | 12.6098 | 1 | 7.824 | 276 | 35.2761
12.2 | 10.5231 | 1 | 7.824 | 276 | 35.2761
11.9 | 10.6602 | 1 | 7.824 | 276 | 35.2761
12.2 | 11.0047 | 1 | 7.824 | 276 | 35.2761
12.6 | 11.5037 | 1 | 7.824 | 276 | 35.2761
12.9 | 10.9265 | 1 | 7.824 | 276 | 35.2761
13 | 10.4552 | 1 | 7.824 | 276 | 35.2761
13.3 | 10.5345 | 1 | 7.824 | 276 | 35.2761
13.9 | 10.5959 | 1 | 7.824 | 276 | 35.2761
15.4 | 11.234 | 1 | 7.824 | 276 | 35.2761
15 | 11.4545 | 1 | 7.824 | 276 | 35.2761
15 | 11.6026 | 1 | 7.824 | 276 | 35.2761
17 | 11.6222 | 1 | 7.824 | 276 | 35.2761
17.2 | 11.9334 | 1 | 7.824 | 276 | 35.2761
17.2 | 11.1376 | 1 | 7.824 | 276 | 35.2761
15.1 | 10.9163 | 1 | 7.824 | 276 | 35.2761
15.5 | 10.3219 | 1 | 7.824 | 276 | 35.2761
14.7 | 9.5044 | 1 | 7.824 | 276 | 35.2761
11.7 | 9.5837 | 1 | 7.824 | 276 | 35.2761
12.3 | 9.7505 | 1 | 7.824 | 276 | 35.2761
12.6 | 10.3835 | 1 | 7.824 | 276 | 35.2761
12 | 10.8107 | 1 | 7.824 | 276 | 35.2761
12.3 | 10.778 | 1 | 7.824 | 276 | 35.2761
11.5 | 10.7065 | 1 | 7.824 | 276 | 35.2761
11.1 | 10.2063 | 1 | 7.824 | 276 | 35.2761
10.9 | 9.7976 | 1 | 7.824 | 276 | 35.2761
10.6 | 9.0438 | 1 | 7.824 | 276 | 35.2761
9.6 | 8.2838 | 1 | 7.824 | 276 | 35.2761
9.4 | 7.8461 | 1 | 7.824 | 276 | 35.2761
9.1 | 7.7532 | 1 | 7.824 | 276 | 35.2761
9.9 | 8.2261 | 1 | 7.824 | 276 | 35.2761
10.5 | 8.8479 | 1 | 7.824 | 276 | 35.2761
11.2 | 9.773 | 1 | 7.824 | 276 | 35.2761
12 | 9.9212 | 1 | 7.824 | 276 | 35.2761
12 | 9.7696 | 1 | 7.824 | 276 | 35.2761
11.7 | 10.148 | 1 | 7.824 | 276 | 35.2761
11.8 | 10.3487 | 1 | 7.824 | 276 | 35.2761
11.6 | 10.4755 | 1 | 7.824 | 276 | 35.2761
11.9 | 11.0415 | 1 | 7.824 | 276 | 35.2761
11.4 | 10.7174 | 1 | 7.824 | 276 | 35.2761
11.6 | 10.914 | 1 | 7.824 | 276 | 35.2761
11.3 | 10.5642 | 1 | 7.824 | 276 | 35.2761
10.6 | 9.8236 | 1 | 7.824 | 276 | 35.2761
10.5 | 9.6193 | 1 | 7.824 | 276 | 35.2761
10.3 | 9.0593 | 1 | 7.824 | 276 | 35.2761
9.1 | 8.1009 | 1 | 7.824 | 276 | 35.2761
8.8 | 7.9106 | 1 | 7.824 | 276 | 35.2761
8.7 | 7.7135 | 1 | 7.824 | 276 | 35.2761
8.5 | 7.0367 | 1 | 7.824 | 276 | 35.2761
8 | 6.3293 | 1 | 7.824 | 276 | 35.2761
7.2 | 6.3054 | 1 | 7.824 | 276 | 35.2761
6.9 | 6.014 | 1 | 7.824 | 276 | 35.2761
6 | 5.3239 | 1 | 7.824 | 276 | 35.2761
6.1 | 5.4218 | 1 | 7.824 | 276 | 35.2761
8.1 | 6.9885 | 1 | 7.824 | 276 | 35.2761
9.8 | 7.9004 | 1 | 7.824 | 276 | 35.2761
11.7 | 8.6063 | 1 | 7.824 | 276 | 35.2761
12.8 | 8.5941 | 1 | 7.824 | 276 | 35.2761
13.6 | 9.0876 | 1 | 7.824 | 276 | 35.2761
14.4 | 8.4399 | 1 | 7.824 | 276 | 35.2761
15.5 | 9.4685 | 1 | 7.824 | 276 | 35.2761
16.1 | 9.7349 | 1 | 7.824 | 276 | 35.2761
15.3 | 9.5712 | 1 | 7.824 | 276 | 35.2761
15.5 | 9.6608 | 1 | 7.824 | 276 | 35.2761
16.5 | 10.5858 | 1 | 7.824 | 276 | 35.2761
15.6 | 10.2345 | 1 | 7.824 | 276 | 35.2761
15 | 9.1626 | 1 | 7.824 | 276 | 35.2761
13.9 | 8.8159 | 1 | 7.824 | 276 | 35.2761
12.9 | 9.6102 | 1 | 7.824 | 276 | 35.2761
12.5 | 9.2914 | 1 | 7.824 | 276 | 35.2761
12.6 | 9.6161 | 1 | 7.824 | 276 | 35.2761
12.4 | 10.7767 | 1 | 7.824 | 276 | 35.2761
11.9 | 10.9379 | 1 | 7.824 | 276 | 35.2761
11.4 | 11.0572 | 1 | 7.824 | 276 | 35.2761
11.4 | 11.1706 | 1 | 7.824 | 276 | 35.2761
11.7 | 11.4688 | 1 | 7.824 | 276 | 35.2761
12.1 | 11.7511 | 1 | 7.824 | 276 | 35.2761
12.5 | 12.1477 | 1 | 7.824 | 276 | 35.2761
13.1 | 12.5671 | 1 | 7.824 | 276 | 35.2761
13.5 | 12.9623 | 1 | 7.824 | 276 | 35.2761
14.8 | 13.7104 | 1 | 7.824 | 276 | 35.2761
15.3 | 14.0215 | 1 | 7.824 | 276 | 35.2761
16.4 | 14.6752 | 1 | 7.824 | 276 | 35.2761
16.5 | 14.3084 | 1 | 7.824 | 276 | 35.2761
17.8 | 15.0842 | 1 | 7.824 | 276 | 35.2761
19.3 | 15.6361 | 1 | 7.824 | 276 | 35.2761
19.6 | 16.2555 | 1 | 7.824 | 276 | 35.2761
20.4 | 16.2005 | 1 | 7.824 | 276 | 35.2761
20.9 | 16.6019 | 1 | 7.824 | 276 | 35.2761
21.4 | 16.5551 | 1 | 7.824 | 276 | 35.2761
20.9 | 16.2662 | 1 | 7.824 | 276 | 35.2761
20.4 | 16.0877 | 1 | 7.824 | 276 | 35.2761
18.8 | 15.4522 | 1 | 7.824 | 276 | 35.2761
17.5 | 15.6757 | 1 | 7.824 | 276 | 35.2761
16.1 | 14.7996 | 1 | 7.824 | 276 | 35.2761
15.2 | 13.9834 | 1 | 7.824 | 276 | 35.2761
14.5 | 13.0732 | 1 | 7.824 | 276 | 35.2761
13.5 | 12.1063 | 1 | 7.824 | 276 | 35.2761
13 | 11.7882 | 1 | 7.824 | 276 | 35.2761
13 | 11.8994 | 1 | 7.824 | 276 | 35.2761
12.9 | 11.9139 | 1 | 7.824 | 276 | 35.2761
13 | 12.0115 | 1 | 7.824 | 276 | 35.2761
13.4 | 12.2893 | 1 | 7.824 | 276 | 35.2761
14.1 | 12.9137 | 1 | 7.824 | 276 | 35.2761
14.9 | 12.8427 | 1 | 7.824 | 276 | 35.2761
15.4 | 13.2079 | 1 | 7.824 | 276 | 35.2761
16.4 | 13.7668 | 1 | 7.824 | 276 | 35.2761
17.3 | 14.1698 | 1 | 7.824 | 276 | 35.2761
18.5 | 14.6808 | 1 | 7.824 | 276 | 35.2761
18.8 | 14.6865 | 1 | 7.824 | 276 | 35.2761
19.4 | 14.9649 | 1 | 7.824 | 276 | 35.2761
19.7 | 15.2349 | 1 | 7.824 | 276 | 35.2761
21.1 | 15.695 | 1 | 7.824 | 276 | 35.2761
20.6 | 15.7254 | 1 | 7.824 | 276 | 35.2761
19.6 | 15.3599 | 1 | 7.824 | 276 | 35.2761
19 | 14.975 | 1 | 7.824 | 276 | 35.2761
17 | 13.7274 | 1 | 7.824 | 276 | 35.2761
16.2 | 13.2532 | 1 | 7.824 | 276 | 35.2761
15.3 | 13.2236 | 1 | 7.824 | 276 | 35.2761
13.8 | 12.3963 | 1 | 7.824 | 276 | 35.2761
13 | 12.0119 | 1 | 7.824 | 276 | 35.2761
12.6 | 11.8457 | 1 | 7.824 | 276 | 35.2761
12.8 | 12.042 | 1 | 7.824 | 276 | 35.2761
13.1 | 12.1092 | 1 | 7.824 | 276 | 35.2761
13.2 | 12.2068 | 1 | 7.824 | 276 | 35.2761
13.4 | 11.8447 | 1 | 7.824 | 276 | 35.2761
13.4 | 11.8447 | 1 | 7.824 | 276 | 35.2761
12.7 | 11.9441 | 1 | 7.824 | 276 | 35.2761
13.1 | 12.3369 | 1 | 7.824 | 276 | 35.2761
13.9 | 12.2714 | 1 | 7.824 | 276 | 35.2761
14.2 | 12.4498 | 1 | 7.824 | 276 | 35.2761
15.4 | 11.9448 | 1 | 7.824 | 276 | 35.2761
12.6 | 9.8561 | 1 | 7.824 | 276 | 35.2761
14.2 | 11.2404 | 1 | 7.824 | 276 | 35.2761
16.4 | 10.7116 | 1 | 7.824 | 276 | 35.2761
16.6 | 11.0101 | 1 | 7.824 | 276 | 35.2761
16.3 | 9.9447 | 1 | 7.824 | 276 | 35.2761
15.7 | 8.8663 | 1 | 7.824 | 276 | 35.2761
15 | 8.9438 | 1 | 7.824 | 276 | 35.2761
13.7 | 8.536 | 1 | 7.824 | 276 | 35.2761
12.9 | 7.5958 | 1 | 7.824 | 276 | 35.2761
11.2 | 7.1167 | 1 | 7.824 | 276 | 35.2761
10.1 | 6.7798 | 1 | 7.824 | 276 | 35.2761
9.2 | 6.3339 | 1 | 7.824 | 276 | 35.2761
7.4 | 5.7263 | 1 | 7.824 | 276 | 35.2761
6.9 | 5.6956 | 1 | 7.824 | 276 | 35.2761
6.3 | 4.9862 | 1 | 7.824 | 276 | 35.2761
6.6 | 5.4972 | 1 | 7.824 | 276 | 35.2761
7 | 5.8834 | 1 | 7.824 | 276 | 35.2761
8.3 | 6.8552 | 1 | 7.824 | 276 | 35.2761
10 | 7.9089 | 1 | 7.824 | 276 | 35.2761
11.5 | 9.1757 | 1 | 7.824 | 276 | 35.2761
12.9 | 10.0462 | 1 | 7.824 | 276 | 35.2761
13.4 | 10.46 | 1 | 7.824 | 276 | 35.2761
13.8 | 10.2083 | 1 | 7.824 | 276 | 35.2761
14 | 10.1586 | 1 | 7.824 | 276 | 35.2761
14.8 | 10.6466 | 1 | 7.824 | 276 | 35.2761
15.2 | 10.5953 | 1 | 7.824 | 276 | 35.2761
15 | 10.506 | 1 | 7.824 | 276 | 35.2761
15 | 10.2876 | 1 | 7.824 | 276 | 35.2761
14.7 | 10.199 | 1 | 7.824 | 276 | 35.2761
14.4 | 10.3349 | 1 | 7.824 | 276 | 35.2761
13.6 | 9.9812 | 1 | 7.824 | 276 | 35.2761
13.7 | 9.889 | 1 | 7.824 | 276 | 35.2761
13.4 | 9.8936 | 1 | 7.824 | 276 | 35.2761
13.5 | 9.9843 | 1 | 7.824 | 276 | 35.2761
13 | 10.0439 | 1 | 7.824 | 276 | 35.2761
12.6 | 9.9623 | 1 | 7.824 | 276 | 35.2761
12.4 | 9.8731 | 1 | 7.824 | 276 | 35.2761
12.1 | 9.7868 | 1 | 7.824 | 276 | 35.2761
12 | 9.9403 | 1 | 7.824 | 276 | 35.2761
11.9 | 9.5019 | 1 | 7.824 | 276 | 35.2761
11.1 | 9.5877 | 1 | 7.824 | 276 | 35.2761
11 | 9.4411 | 1 | 7.824 | 276 | 35.2761
11.5 | 9.4193 | 1 | 7.824 | 276 | 35.2761
12.4 | 9.444 | 1 | 7.824 | 276 | 35.2761
12.7 | 9.3043 | 1 | 7.824 | 276 | 35.2761
13.6 | 9.6665 | 1 | 7.824 | 276 | 35.2761
13.8 | 9.8471 | 1 | 7.824 | 276 | 35.2761
14.7 | 9.9859 | 1 | 7.824 | 276 | 35.2761
15.8 | 10.5566 | 1 | 7.824 | 276 | 35.2761
16.3 | 10.9451 | 1 | 7.824 | 276 | 35.2761
15.6 | 10.6853 | 1 | 7.824 | 276 | 35.2761
16.2 | 10.8589 | 1 | 7.824 | 276 | 35.2761
15.8 | 10.904 | 1 | 7.824 | 276 | 35.2761
15.5 | 10.6857 | 1 | 7.824 | 276 | 35.2761
14.5 | 10.5669 | 1 | 7.824 | 276 | 35.2761
14.1 | 10.3916 | 1 | 7.824 | 276 | 35.2761
13.5 | 10.1267 | 1 | 7.824 | 276 | 35.2761
12.8 | 9.9587 | 1 | 7.824 | 276 | 35.2761
12.2 | 9.1259 | 1 | 7.824 | 276 | 35.2761
11.6 | 8.8497 | 1 | 7.824 | 276 | 35.2761
10.7 | 8.5247 | 1 | 7.824 | 276 | 35.2761
10 | 8.2438 | 1 | 7.824 | 276 | 35.2761
9.5 | 7.9591 | 1 | 7.824 | 276 | 35.2761
8.3 | 7.0938 | 1 | 7.824 | 276 | 35.2761
7.6 | 6.5124 | 1 | 7.824 | 276 | 35.2761
8.4 | 6.7239 | 1 | 7.824 | 276 | 35.2761
10.6 | 8.7169 | 1 | 7.824 | 276 | 35.2761
11.6 | 9.7649 | 1 | 7.824 | 276 | 35.2761
12.1 | 10.0385 | 1 | 7.824 | 276 | 35.2761
14.2 | 10.7185 | 1 | 7.824 | 276 | 35.2761
15.3 | 11.1467 | 1 | 7.824 | 276 | 35.2761
16.2 | 11.7627 | 1 | 7.824 | 276 | 35.2761
16.9 | 12.102 | 1 | 7.824 | 276 | 35.2761
17.8 | 12.6129 | 1 | 7.824 | 276 | 35.2761
18.6 | 12.527 | 1 | 7.824 | 276 | 35.2761
18 | 12.5532 | 1 | 7.824 | 276 | 35.2761
19 | 12.6022 | 1 | 7.824 | 276 | 35.2761
18.1 | 12.1442 | 1 | 7.824 | 276 | 35.2761
18.4 | 12.0947 | 1 | 7.824 | 276 | 35.2761
17.5 | 11.6319 | 1 | 7.824 | 276 | 35.2761
15 | 11.3021 | 1 | 7.824 | 276 | 35.2761
13.1 | 10.4802 | 1 | 7.824 | 276 | 35.2761
12.7 | 10.2065 | 1 | 7.824 | 276 | 35.2761
11.4 | 9.5755 | 1 | 7.824 | 276 | 35.2761
10.3 | 9.0744 | 1 | 7.824 | 276 | 35.2761
10 | 8.9363 | 1 | 7.824 | 276 | 35.2761
10 | 8.9363 | 1 | 7.824 | 276 | 35.2761
8.8 | 8.2746 | 1 | 7.824 | 276 | 35.2761
8.2 | 7.6835 | 1 | 7.824 | 276 | 35.2761
9.2 | 8.4114 | 1 | 7.824 | 276 | 35.2761
10.8 | 9.7131 | 1 | 7.824 | 276 | 35.2761
12.1 | 10.4475 | 1 | 7.824 | 276 | 35.2761
14 | 11.2712 | 1 | 7.824 | 276 | 35.2761
15.8 | 12.2293 | 1 | 7.824 | 276 | 35.2761
18 | 12.8867 | 1 | 7.824 | 276 | 35.2761
18.6 | 13.1736 | 1 | 7.824 | 276 | 35.2761
19.5 | 13.7679 | 1 | 7.824 | 276 | 35.2761
19 | 13.1471 | 1 | 7.824 | 276 | 35.2761
19.7 | 13.5183 | 1 | 7.824 | 276 | 35.2761
20 | 14.0563 | 1 | 7.824 | 276 | 35.2761
19.8 | 13.9785 | 1 | 7.824 | 276 | 35.2761
20 | 14.1522 | 1 | 7.824 | 276 | 35.2761
19.5 | 14.0067 | 1 | 7.824 | 276 | 35.2761
19.7 | 14.0844 | 1 | 7.824 | 276 | 35.2761
18.6 | 13.7535 | 1 | 7.824 | 276 | 35.2761
16.4 | 12.3748 | 1 | 7.824 | 276 | 35.2761
15.5 | 11.7087 | 1 | 7.824 | 276 | 35.2761
15.4 | 11.0528 | 1 | 7.824 | 276 | 35.2761
14.5 | 10.8031 | 1 | 7.824 | 276 | 35.2761
14.2 | 10.72 | 1 | 7.824 | 276 | 35.2761
12.7 | 10.8643 | 1 | 7.824 | 276 | 35.2761
11.7 | 10.27 | 1 | 7.824 | 276 | 35.2761
11.2 | 9.8919 | 1 | 7.824 | 276 | 35.2761
11.4 | 9.9812 | 1 | 7.824 | 276 | 35.2761
12.2 | 10.4383 | 1 | 7.824 | 276 | 35.2761
14.3 | 11.7019 | 1 | 7.824 | 276 | 35.2761
16 | 12.309 | 1 | 7.824 | 276 | 35.2761
17.8 | 13.1399 | 1 | 7.824 | 276 | 35.2761
18.6 | 13.8516 | 1 | 7.824 | 276 | 35.2761
19.5 | 14.0046 | 1 | 7.824 | 276 | 35.2761
20.9 | 14.9824 | 1 | 7.824 | 276 | 35.2761
21.7 | 15.5775 | 1 | 7.824 | 276 | 35.2761
22.5 | 15.4751 | 1 | 7.824 | 276 | 35.2761
23 | 15.4686 | 1 | 7.824 | 276 | 35.2761
23 | 15.4658 | 1 | 7.824 | 276 | 35.2761
23.1 | 16.0823 | 1 | 7.824 | 276 | 35.2761
22.5 | 16.2707 | 1 | 7.824 | 276 | 35.2761
21.8 | 16.2265 | 1 | 7.824 | 276 | 35.2761
20.8 | 15.4964 | 1 | 7.824 | 276 | 35.2761
19.8 | 15.3923 | 1 | 7.824 | 276 | 35.2761
18.4 | 15.147 | 1 | 7.824 | 276 | 35.2761
17.1 | 14.377 | 1 | 7.824 | 276 | 35.2761
16.1 | 13.9343 | 1 | 7.824 | 276 | 35.2761
14.5 | 12.9648 | 1 | 7.824 | 276 | 35.2761
14.1 | 12.803 | 1 | 7.824 | 276 | 35.2761
13.4 | 12.292 | 1 | 7.824 | 276 | 35.2761
12.7 | 11.946 | 1 | 7.824 | 276 | 35.2761
13.2 | 11.9859 | 1 | 7.824 | 276 | 35.2761
14 | 11.9376 | 1 | 7.824 | 276 | 35.2761
16.4 | 12.4624 | 1 | 7.824 | 276 | 35.2761
17.5 | 13.4615 | 1 | 7.824 | 276 | 35.2761
18.5 | 13.9554 | 1 | 7.824 | 276 | 35.2761
19.9 | 14.6956 | 1 | 7.824 | 276 | 35.2761
21.1 | 15.5012 | 1 | 7.824 | 276 | 35.2761
22.3 | 15.2946 | 1 | 7.824 | 276 | 35.2761
23.1 | 15.4473 | 1 | 7.824 | 276 | 35.2761
23.9 | 15.6937 | 1 | 7.824 | 276 | 35.2761
24.1 | 16.4323 | 1 | 7.824 | 276 | 35.2761
23.5 | 15.9743 | 1 | 7.824 | 276 | 35.2761
23.4 | 15.9355 | 1 | 7.824 | 276 | 35.2761
22.5 | 15.3659 | 1 | 7.824 | 276 | 35.2761
20.7 | 14.3098 | 1 | 7.824 | 276 | 35.2761
18.7 | 12.5977 | 1 | 7.824 | 276 | 35.2761
16.5 | 11.4629 | 1 | 7.824 | 276 | 35.2761
15 | 10.7299 | 1 | 7.824 | 276 | 35.2761
13.3 | 9.5728 | 1 | 7.824 | 276 | 35.2761
12.1 | 8.8912 | 1 | 7.824 | 276 | 35.2761
11 | 8.2427 | 1 | 7.824 | 276 | 35.2761
10 | 7.8153 | 1 | 7.824 | 276 | 35.2761
9.3 | 7.4337 | 1 | 7.824 | 276 | 35.2761
8.5 | 6.8591 | 1 | 7.824 | 276 | 35.2761
9.3 | 7.5261 | 1 | 7.824 | 276 | 35.2761
10.5 | 7.9603 | 1 | 7.824 | 276 | 35.2761
12.5 | 9.2073 | 1 | 7.824 | 276 | 35.2761
13.8 | 10.0651 | 1 | 7.824 | 276 | 35.2761
14.9 | 10.5014 | 1 | 7.824 | 276 | 35.2761
16.5 | 11.595 | 1 | 7.824 | 276 | 35.2761
17.8 | 11.9147 | 1 | 7.824 | 276 | 35.2761
19.6 | 12.5238 | 1 | 7.824 | 276 | 35.2761
21 | 13.8182 | 1 | 7.824 | 276 | 35.2761
22 | 14.2017 | 1 | 7.824 | 276 | 35.2761
22.5 | 14.3491 | 1 | 7.824 | 276 | 35.2761
23 | 14.8898 | 1 | 7.824 | 276 | 35.2761
23.1 | 15.4332 | 1 | 7.824 | 276 | 35.2761
22.7 | 15.6685 | 1 | 7.824 | 276 | 35.2761
22.3 | 14.6237 | 1 | 7.824 | 276 | 35.2761
20.8 | 13.9593 | 1 | 7.824 | 276 | 35.2761
19.1 | 13.7751 | 1 | 7.824 | 276 | 35.2761
17.6 | 12.6969 | 1 | 7.824 | 276 | 35.2761
16.4 | 11.9168 | 1 | 7.824 | 276 | 35.2761
15.5 | 11.5411 | 1 | 7.824 | 276 | 35.2761
13.9 | 10.9601 | 1 | 7.824 | 276 | 35.2761
13.1 | 11.2339 | 1 | 7.824 | 276 | 35.2761
12.5 | 10.8719 | 1 | 7.824 | 276 | 35.2761
12.9 | 11.1489 | 1 | 7.824 | 276 | 35.2761
12.7 | 11.1699 | 1 | 7.824 | 276 | 35.2761
13.5 | 11.6146 | 1 | 7.824 | 276 | 35.2761
15 | 12.2896 | 1 | 7.824 | 276 | 35.2761
15.9 | 12.97 | 1 | 7.824 | 276 | 35.2761
18 | 13.7457 | 1 | 7.824 | 276 | 35.2761
19.6 | 14.6161 | 1 | 7.824 | 276 | 35.2761
20.5 | 14.8524 | 1 | 7.824 | 276 | 35.2761
21.6 | 15.5627 | 1 | 7.824 | 276 | 35.2761
22.1 | 15.4916 | 1 | 7.824 | 276 | 35.2761
21.7 | 15.5462 | 1 | 7.824 | 276 | 35.2761
23 | 15.8676 | 1 | 7.824 | 276 | 35.2761
22.9 | 14.6613 | 1 | 7.824 | 276 | 35.2761
23 | 14.6547 | 1 | 7.824 | 276 | 35.2761
22.8 | 14.3175 | 1 | 7.824 | 276 | 35.2761
22.3 | 13.9121 | 1 | 7.824 | 276 | 35.2761
20.9 | 13.9441 | 1 | 7.824 | 276 | 35.2761
19.6 | 13.3913 | 1 | 7.824 | 276 | 35.2761
18.2 | 12.743 | 1 | 7.824 | 276 | 35.2761
16.2 | 13.1428 | 1 | 7.824 | 276 | 35.2761
14.9 | 12.6217 | 1 | 7.824 | 276 | 35.2761
13.9 | 12.0504 | 1 | 7.824 | 276 | 35.2761
13.6 | 11.763 | 1 | 7.824 | 276 | 35.2761
12.8 | 11.5926 | 1 | 7.824 | 276 | 35.2761
11.7 | 10.7961 | 1 | 7.824 | 276 | 35.2761
11.7 | 10.7961 | 1 | 7.824 | 276 | 35.2761
12.7 | 11.6061 | 1 | 7.824 | 276 | 35.2761
14.1 | 12.461 | 1 | 7.824 | 276 | 35.2761
16.4 | 13.4351 | 1 | 7.824 | 276 | 35.2761
17.9 | 14.0716 | 1 | 7.824 | 276 | 35.2761
19.9 | 15.0367 | 1 | 7.824 | 276 | 35.2761
21.2 | 15.1085 | 1 | 7.824 | 276 | 35.2761
22.2 | 15.4762 | 1 | 7.824 | 276 | 35.2761
23.6 | 15.3665 | 1 | 7.824 | 276 | 35.2761
24.6 | 16.6764 | 1 | 7.824 | 276 | 35.2761
24.9 | 16.3444 | 1 | 7.824 | 276 | 35.2761
24 | 15.9766 | 1 | 7.824 | 276 | 35.2761
23.8 | 15.998 | 1 | 7.824 | 276 | 35.2761
23.3 | 15.4837 | 1 | 7.824 | 276 | 35.2761
22 | 15.9532 | 1 | 7.824 | 276 | 35.2761
20.2 | 14.8828 | 1 | 7.824 | 276 | 35.2761
18.7 | 13.7045 | 1 | 7.824 | 276 | 35.2761
17.6 | 13.0233 | 1 | 7.824 | 276 | 35.2761
16.7 | 12.5614 | 1 | 7.824 | 276 | 35.2761
15.7 | 12.2068 | 1 | 7.824 | 276 | 35.2761
14.9 | 12.0314 | 1 | 7.824 | 276 | 35.2761
14.3 | 11.8888 | 1 | 7.824 | 276 | 35.2761
13 | 11.2393 | 1 | 7.824 | 276 | 35.2761
12.5 | 11.1896 | 1 | 7.824 | 276 | 35.2761
12.5 | 11.1896 | 1 | 7.824 | 276 | 35.2761
13.4 | 11.3021 | 1 | 7.824 | 276 | 35.2761
14.7 | 11.949 | 1 | 7.824 | 276 | 35.2761
14.8 | 12.0435 | 1 | 7.824 | 276 | 35.2761
16.8 | 12.8533 | 1 | 7.824 | 276 | 35.2761
18.1 | 13.5191 | 1 | 7.824 | 276 | 35.2761
19 | 13.524 | 1 | 7.824 | 276 | 35.2761
19 | 13.524 | 1 | 7.824 | 276 | 35.2761
20.8 | 14.5062 | 1 | 7.824 | 276 | 35.2761
21.4 | 14.9749 | 1 | 7.824 | 276 | 35.2761
21.8 | 15.2705 | 1 | 7.824 | 276 | 35.2761
22.7 | 15.648 | 1 | 7.824 | 276 | 35.2761
21.8 | 15.6221 | 1 | 7.824 | 276 | 35.2761
20.8 | 15.2551 | 1 | 7.824 | 276 | 35.2761
21.1 | 15.0101 | 1 | 7.824 | 276 | 35.2761
18.6 | 14.3313 | 1 | 7.824 | 276 | 35.2761
17 | 13.7185 | 1 | 7.824 | 276 | 35.2761
15.5 | 12.8581 | 1 | 7.824 | 276 | 35.2761
14 | 12.1421 | 1 | 7.824 | 276 | 35.2761
13.5 | 11.8816 | 1 | 7.824 | 276 | 35.2761
13.9 | 12.1559 | 1 | 7.824 | 276 | 35.2761
13.4 | 11.731 | 1 | 7.824 | 276 | 35.2761
12.9 | 11.4677 | 1 | 7.824 | 276 | 35.2761
12.7 | 11.3837 | 1 | 7.824 | 276 | 35.2761
13.6 | 11.8684 | 1 | 7.824 | 276 | 35.2761
14.6 | 12.2793 | 1 | 7.824 | 276 | 35.2761
15.1 | 12.3776 | 1 | 7.824 | 276 | 35.2761
16.4 | 13.1112 | 1 | 7.824 | 276 | 35.2761
17 | 13.5062 | 1 | 7.824 | 276 | 35.2761
18.2 | 14.0766 | 1 | 7.824 | 276 | 35.2761
17.1 | 13.7063 | 1 | 7.824 | 276 | 35.2761
17.1 | 13.5997 | 1 | 7.824 | 276 | 35.2761
19.3 | 14.7585 | 1 | 7.824 | 276 | 35.2761
19.7 | 14.908 | 1 | 7.824 | 276 | 35.2761
20.3 | 15.0807 | 1 | 7.824 | 276 | 35.2761
20.3 | 15.1848 | 1 | 7.824 | 276 | 35.2761
20 | 14.9173 | 1 | 7.824 | 276 | 35.2761
19.3 | 14.7602 | 1 | 7.824 | 276 | 35.2761
18.5 | 14.2471 | 1 | 7.824 | 276 | 35.2761
17.5 | 13.7057 | 1 | 7.824 | 276 | 35.2761
16.9 | 13.6309 | 1 | 7.824 | 276 | 35.2761
16.3 | 13.5588 | 1 | 7.824 | 276 | 35.2761
16.1 | 13.264 | 1 | 7.824 | 276 | 35.2761
15.8 | 12.9835 | 1 | 7.824 | 276 | 35.2761
15.5 | 12.5447 | 1 | 7.824 | 276 | 35.2761
15 | 12.2885 | 1 | 7.824 | 276 | 35.2761
14.1 | 12.3511 | 1 | 7.824 | 276 | 35.2761
13.6 | 12.2018 | 1 | 7.824 | 276 | 35.2761
13.7 | 12.2985 | 1 | 7.824 | 276 | 35.2761
14.2 | 12.0126 | 1 | 7.824 | 276 | 35.2761
15.2 | 12.4756 | 1 | 7.824 | 276 | 35.2761
16 | 12.5914 | 1 | 7.824 | 276 | 35.2761
16.2 | 12.0228 | 1 | 7.824 | 276 | 35.2761
16.3 | 12.1616 | 1 | 7.824 | 276 | 35.2761
16.9 | 12.7519 | 1 | 7.824 | 276 | 35.2761
16.8 | 12.7618 | 1 | 7.824 | 276 | 35.2761
17.7 | 13.1716 | 1 | 7.824 | 276 | 35.2761
17.7 | 12.9249 | 1 | 7.824 | 276 | 35.2761
17.9 | 13.1026 | 1 | 7.824 | 276 | 35.2761
18.2 | 13.8234 | 1 | 7.824 | 276 | 35.2761
17.4 | 13.7208 | 1 | 7.824 | 276 | 35.2761
18 | 13.9535 | 1 | 7.824 | 276 | 35.2761
17.7 | 14.1029 | 1 | 7.824 | 276 | 35.2761
17 | 13.5117 | 1 | 7.824 | 276 | 35.2761
16.3 | 13.5599 | 1 | 7.824 | 276 | 35.2761
15.5 | 13.4124 | 1 | 7.824 | 276 | 35.2761
14.9 | 13.1745 | 1 | 7.824 | 276 | 35.2761
14.1 | 12.6852 | 1 | 7.824 | 276 | 35.2761
13.7 | 12.4104 | 1 | 7.824 | 276 | 35.2761
14.1 | 12.4616 | 1 | 7.824 | 276 | 35.2761
14.4 | 13.0893 | 1 | 7.824 | 276 | 35.2761
14.9 | 12.9507 | 1 | 7.824 | 276 | 35.2761
15 | 12.8254 | 1 | 7.824 | 276 | 35.2761
14.5 | 13.3014 | 1 | 7.824 | 276 | 35.2761
14.6 | 13.7499 | 1 | 7.824 | 276 | 35.2761
15.2 | 13.8649 | 1 | 7.824 | 276 | 35.2761
16 | 14.2888 | 1 | 7.824 | 276 | 35.2761
15.7 | 13.6577 | 1 | 7.824 | 276 | 35.2761
16.6 | 13.8945 | 1 | 7.824 | 276 | 35.2761
17.2 | 14.2911 | 1 | 7.824 | 276 | 35.2761
17.2 | 14.684 | 1 | 7.824 | 276 | 35.2761
16.6 | 14.8653 | 1 | 7.824 | 276 | 35.2761
16.9 | 14.86 | 1 | 7.824 | 276 | 35.2761
16.1 | 15.0381 | 1 | 7.824 | 276 | 35.2761
16.6 | 14.9836 | 1 | 7.824 | 276 | 35.2761
16.8 | 15.0579 | 1 | 7.824 | 276 | 35.2761
16.6 | 15.1634 | 1 | 7.824 | 276 | 35.2761
16.8 | 15.1774 | 1 | 7.824 | 276 | 35.2761
16.8 | 15.1774 | 1 | 7.824 | 276 | 35.2761
16.4 | 14.9694 | 1 | 7.824 | 276 | 35.2761
16.2 | 14.7755 | 1 | 7.824 | 276 | 35.2761
16.2 | 14.7755 | 1 | 7.824 | 276 | 35.2761
16 | 14.8206 | 1 | 7.824 | 276 | 35.2761
16.1 | 14.679 | 1 | 7.824 | 276 | 35.2761
16.1 | 14.1538 | 1 | 7.824 | 276 | 35.2761
15.6 | 13.2294 | 1 | 7.824 | 276 | 35.2761
15.6 | 12.429 | 1 | 7.824 | 276 | 35.2761
16.1 | 12.8405 | 1 | 7.824 | 276 | 35.2761
16.7 | 13.082 | 1 | 7.824 | 276 | 35.2761
17 | 13.3048 | 1 | 7.824 | 276 | 35.2761
18 | 13.5465 | 1 | 7.824 | 276 | 35.2761
19.1 | 13.7792 | 1 | 7.824 | 276 | 35.2761
19.4 | 13.1862 | 1 | 7.824 | 276 | 35.2761
20.3 | 13.2329 | 1 | 7.824 | 276 | 35.2761
21.3 | 13.4985 | 1 | 7.824 | 276 | 35.2761
21.4 | 13.5805 | 1 | 7.824 | 276 | 35.2761
21 | 13.3832 | 1 | 7.824 | 276 | 35.2761
21.4 | 13.5836 | 1 | 7.824 | 276 | 35.2761
20.5 | 13.2281 | 1 | 7.824 | 276 | 35.2761
20.2 | 13.3729 | 1 | 7.824 | 276 | 35.2761
19.6 | 13.3188 | 1 | 7.824 | 276 | 35.2761
18.3 | 12.989 | 1 | 7.824 | 276 | 35.2761
17 | 12.6591 | 1 | 7.824 | 276 | 35.2761
15.9 | 12.309 | 1 | 7.824 | 276 | 35.2761
13.5 | 11.3057 | 1 | 7.824 | 276 | 35.2761
12.9 | 10.945 | 1 | 7.824 | 276 | 35.2761
12.2 | 10.9077 | 1 | 7.824 | 276 | 35.2761
11.8 | 10.681 | 1 | 7.824 | 276 | 35.2761
10.9 | 10.1254 | 1 | 7.824 | 276 | 35.2761
10.5 | 9.9482 | 1 | 7.824 | 276 | 35.2761
10.6 | 9.9388 | 1 | 7.824 | 276 | 35.2761
12.2 | 10.9082 | 1 | 7.824 | 276 | 35.2761
15.3 | 12.0121 | 1 | 7.824 | 276 | 35.2761
17 | 12.3224 | 1 | 7.824 | 276 | 35.2761
18.2 | 12.672 | 1 | 7.824 | 276 | 35.2761
19.7 | 13.4092 | 1 | 7.824 | 276 | 35.2761
20.3 | 13.0278 | 1 | 7.824 | 276 | 35.2761
22 | 13.9955 | 1 | 7.824 | 276 | 35.2761
22.5 | 13.6074 | 1 | 7.824 | 276 | 35.2761
23.1 | 14.3305 | 1 | 7.824 | 276 | 35.2761
23.8 | 14.2655 | 1 | 7.824 | 276 | 35.2761
23.2 | 14.9737 | 1 | 7.824 | 276 | 35.2761
23 | 14.8958 | 1 | 7.824 | 276 | 35.2761
22.4 | 14.1374 | 1 | 7.824 | 276 | 35.2761
21.4 | 13.9261 | 1 | 7.824 | 276 | 35.2761
19 | 13.7894 | 1 | 7.824 | 276 | 35.2761
17.4 | 12.8119 | 1 | 7.824 | 276 | 35.2761
16.3 | 11.5971 | 1 | 7.824 | 276 | 35.2761
15.6 | 11.3469 | 1 | 7.824 | 276 | 35.2761
15.6 | 11.2048 | 1 | 7.824 | 276 | 35.2761
15.3 | 11.3607 | 1 | 7.824 | 276 | 35.2761
14.9 | 11.3841 | 1 | 7.824 | 276 | 35.2761
15 | 11.6225 | 1 | 7.824 | 276 | 35.2761
14.8 | 11.739 | 1 | 7.824 | 276 | 35.2761
14.7 | 11.9547 | 1 | 7.824 | 276 | 35.2761
15.9 | 12.3944 | 1 | 7.824 | 276 | 35.2761
17.7 | 13.2162 | 1 | 7.824 | 276 | 35.2761
18.9 | 13.8859 | 1 | 7.824 | 276 | 35.2761
22 | 15.598 | 1 | 7.824 | 276 | 35.2761
24.9 | 16.7754 | 1 | 7.824 | 276 | 35.2761
26.5 | 17.323 | 1 | 7.824 | 276 | 35.2761
27.6 | 18.7843 | 1 | 7.824 | 276 | 35.2761
28.1 | 19.3074 | 1 | 7.824 | 276 | 35.2761
29.1 | 19.6738 | 1 | 7.824 | 276 | 35.2761
28.8 | 20.0048 | 1 | 7.824 | 276 | 35.2761
29.2 | 20.3971 | 1 | 7.824 | 276 | 35.2761
28.6 | 20.6615 | 1 | 7.824 | 276 | 35.2761
28.1 | 20.1713 | 1 | 7.824 | 276 | 35.2761
22 | 18.1214 | 1 | 7.824 | 276 | 35.2761
19.3 | 17.59 | 1 | 7.824 | 276 | 35.2761
19.5 | 17.0998 | 1 | 7.824 | 276 | 35.2761
18 | 17.3423 | 1 | 7.824 | 276 | 35.2761
18 | 17.342 | 1 | 7.824 | 276 | 35.2761
17.9 | 17.373 | 1 | 7.824 | 276 | 35.2761
17.1 | 16.7742 | 1 | 7.824 | 276 | 35.2761
17 | 16.5462 | 1 | 7.824 | 276 | 35.2761
16.2 | 15.7536 | 1 | 7.824 | 276 | 35.2761
16 | 15.368 | 1 | 7.824 | 276 | 35.2761
15.9 | 15.2693 | 1 | 7.824 | 276 | 35.2761
15.9 | 15.4563 | 1 | 7.824 | 276 | 35.2761
16.2 | 15.4413 | 1 | 7.824 | 276 | 35.2761
15.9 | 14.9015 | 1 | 7.824 | 276 | 35.2761
16.3 | 14.9896 | 1 | 7.824 | 276 | 35.2761
16.4 | 15.0874 | 1 | 7.824 | 276 | 35.2761
18.1 | 15.7089 | 1 | 7.824 | 276 | 35.2761
20.2 | 17.042 | 1 | 7.824 | 276 | 35.2761
20.6 | 16.3715 | 1 | 7.824 | 276 | 35.2761
21 | 16.6812 | 1 | 7.824 | 276 | 35.2761
21.4 | 16.5431 | 1 | 7.824 | 276 | 35.2761
21.5 | 16.6335 | 1 | 7.824 | 276 | 35.2761
21.8 | 16.7382 | 1 | 7.824 | 276 | 35.2761
21.2 | 16.4176 | 1 | 7.824 | 276 | 35.2761
20.8 | 16.1673 | 1 | 7.824 | 276 | 35.2761
19.1 | 15.6118 | 1 | 7.824 | 276 | 35.2761
18.2 | 14.8325 | 1 | 7.824 | 276 | 35.2761
17.1 | 14.5884 | 1 | 7.824 | 276 | 35.2761
16.1 | 14.3838 | 1 | 7.824 | 276 | 35.2761
14.9 | 13.8063 | 1 | 7.824 | 276 | 35.2761
13.9 | 12.8883 | 1 | 7.824 | 276 | 35.2761
13.5 | 12.7278 | 1 | 7.824 | 276 | 35.2761
14 | 12.9287 | 1 | 7.824 | 276 | 35.2761
13.2 | 12.3189 | 1 | 7.824 | 276 | 35.2761
12.3 | 11.6628 | 1 | 7.824 | 276 | 35.2761
13.8 | 12.6201 | 1 | 7.824 | 276 | 35.2761
15.3 | 13.332 | 1 | 7.824 | 276 | 35.2761
16.9 | 13.6309 | 1 | 7.824 | 276 | 35.2761
17.8 | 14.195 | 1 | 7.824 | 276 | 35.2761
17.3 | 13.5766 | 1 | 7.824 | 276 | 35.2761
17.9 | 13.6553 | 1 | 7.824 | 276 | 35.2761
17.7 | 13.5771 | 1 | 7.824 | 276 | 35.2761
18.1 | 13.5317 | 1 | 7.824 | 276 | 35.2761
19 | 13.7813 | 1 | 7.824 | 276 | 35.2761
19.4 | 13.9855 | 1 | 7.824 | 276 | 35.2761
20.6 | 14.9402 | 1 | 7.824 | 276 | 35.2761
20.4 | 14.8655 | 1 | 7.824 | 276 | 35.2761
18.5 | 14.1476 | 1 | 7.824 | 276 | 35.2761
17.7 | 13.8916 | 1 | 7.824 | 276 | 35.2761
17.1 | 13.9281 | 1 | 7.824 | 276 | 35.2761
16 | 13.3895 | 1 | 7.824 | 276 | 35.2761
15.3 | 13.3343 | 1 | 7.824 | 276 | 35.2761
14.9 | 12.9531 | 1 | 7.824 | 276 | 35.2761
14.9 | 12.9531 | 1 | 7.824 | 276 | 35.2761
14.8 | 12.8576 | 1 | 7.824 | 276 | 35.2761
14.5 | 12.4076 | 1 | 7.824 | 276 | 35.2761
13.9 | 12.2714 | 1 | 7.824 | 276 | 35.2761
13.4 | 11.9556 | 1 | 7.824 | 276 | 35.2761
13.8 | 12.2862 | 1 | 7.824 | 276 | 35.2761
14.5 | 12.8495 | 1 | 7.824 | 276 | 35.2761
15.2 | 13.2411 | 1 | 7.824 | 276 | 35.2761
16.5 | 14.1982 | 1 | 7.824 | 276 | 35.2761
18.5 | 15.1223 | 1 | 7.824 | 276 | 35.2761
20.3 | 16.2812 | 1 | 7.824 | 276 | 35.2761
21.9 | 17.068 | 1 | 7.824 | 276 | 35.2761
23.9 | 17.9721 | 1 | 7.824 | 276 | 35.2761
24 | 18.1723 | 1 | 7.824 | 276 | 35.2761
24.5 | 18.2827 | 1 | 7.824 | 276 | 35.2761
25.3 | 18.6564 | 1 | 7.824 | 276 | 35.2761
25.4 | 18.634 | 1 | 7.824 | 276 | 35.2761
24.8 | 18.2699 | 1 | 7.824 | 276 | 35.2761
24.3 | 18.1589 | 1 | 7.824 | 276 | 35.2761
22.9 | 16.657 | 1 | 7.824 | 276 | 35.2761
21.4 | 15.4497 | 1 | 7.824 | 276 | 35.2761
19.5 | 15.2735 | 1 | 7.824 | 276 | 35.2761
18.3 | 14.8263 | 1 | 7.824 | 276 | 35.2761
16.9 | 14.4078 | 1 | 7.824 | 276 | 35.2761
15.9 | 13.9668 | 1 | 7.824 | 276 | 35.2761
15.2 | 13.0197 | 1 | 7.824 | 276 | 35.2761
14.6 | 12.5043 | 1 | 7.824 | 276 | 35.2761
14 | 12.4797 | 1 | 7.824 | 276 | 35.2761
14 | 12.479 | 1 | 7.824 | 276 | 35.2761
13.9 | 12.8338 | 1 | 7.824 | 276 | 35.2761
15.4 | 13.3197 | 1 | 7.824 | 276 | 35.2761
17.5 | 13.9244 | 1 | 7.824 | 276 | 35.2761
19.9 | 12.4698 | 1 | 7.824 | 276 | 35.2761
22.1 | 14.7347 | 1 | 7.824 | 276 | 35.2761
24.1 | 15.9824 | 1 | 7.824 | 276 | 35.2761
26 | 17.2736 | 1 | 7.824 | 276 | 35.2761
26.8 | 18.3427 | 1 | 7.824 | 276 | 35.2761
27.2 | 17.8237 | 1 | 7.824 | 276 | 35.2761
27.9 | 18.1028 | 1 | 7.824 | 276 | 35.2761
27.4 | 18.1323 | 1 | 7.824 | 276 | 35.2761
27.3 | 18.1457 | 1 | 7.824 | 276 | 35.2761
26.9 | 17.8638 | 1 | 7.824 | 276 | 35.2761
25.8 | 17.2912 | 1 | 7.824 | 276 | 35.2761
24.6 | 16.8278 | 1 | 7.824 | 276 | 35.2761
23.5 | 16.8011 | 1 | 7.824 | 276 | 35.2761
22.1 | 16.7933 | 1 | 7.824 | 276 | 35.2761
21.7 | 16.2737 | 1 | 7.824 | 276 | 35.2761
20.7 | 16.0252 | 1 | 7.824 | 276 | 35.2761
19.8 | 14.8948 | 1 | 7.824 | 276 | 35.2761
19.6 | 14.6105 | 1 | 7.824 | 276 | 35.2761
18.2 | 15.8075 | 1 | 7.824 | 276 | 35.2761
17.2 | 15.0308 | 1 | 7.824 | 276 | 35.2761
16.1 | 14.4434 | 1 | 7.824 | 276 | 35.2761
16.2 | 13.7961 | 1 | 7.824 | 276 | 35.2761
15.8 | 12.5117 | 1 | 7.824 | 276 | 35.2761
15.9 | 11.9493 | 1 | 7.824 | 276 | 35.2761
16.6 | 12.143 | 1 | 7.824 | 276 | 35.2761
17.4 | 12.282 | 1 | 7.824 | 276 | 35.2761
18.1 | 12.2062 | 1 | 7.824 | 276 | 35.2761
19.5 | 12.9552 | 1 | 7.824 | 276 | 35.2761
21.4 | 14.0152 | 1 | 7.824 | 276 | 35.2761
20.6 | 13.3082 | 1 | 7.824 | 276 | 35.2761
21.5 | 13.3669 | 1 | 7.824 | 276 | 35.2761
21.1 | 12.8399 | 1 | 7.824 | 276 | 35.2761
21 | 12.8399 | 1 | 7.824 | 276 | 35.2761
20.7 | 12.6415 | 1 | 7.824 | 276 | 35.2761
20.1 | 12.3567 | 1 | 7.824 | 276 | 35.2761
19 | 12.029 | 1 | 7.824 | 276 | 35.2761
18 | 11.5697 | 1 | 7.824 | 276 | 35.2761
16.5 | 11.4587 | 1 | 7.824 | 276 | 35.2761
15.1 | 11.0488 | 1 | 7.824 | 276 | 35.2761
13.4 | 10.1221 | 1 | 7.824 | 276 | 35.2761
12.3 | 9.6798 | 1 | 7.824 | 276 | 35.2761
12.9 | 10.1404 | 1 | 7.824 | 276 | 35.2761
12.2 | 9.8786 | 1 | 7.824 | 276 | 35.2761
11.5 | 9.7658 | 1 | 7.824 | 276 | 35.2761
10.8 | 9.3491 | 1 | 7.824 | 276 | 35.2761
11.4 | 9.8742 | 1 | 7.824 | 276 | 35.2761
13.1 | 10.5729 | 1 | 7.824 | 276 | 35.2761
15.5 | 11.6977 | 1 | 7.824 | 276 | 35.2761
17.5 | 12.478 | 1 | 7.824 | 276 | 35.2761
18.5 | 12.9772 | 1 | 7.824 | 276 | 35.2761
19.3 | 12.9772 | 1 | 7.824 | 276 | 35.2761
20.6 | 13.4507 | 1 | 7.824 | 276 | 35.2761
22.1 | 14.5199 | 1 | 7.824 | 276 | 35.2761
23.5 | 15.1814 | 1 | 7.824 | 276 | 35.2761
22.7 | 14.9253 | 1 | 7.824 | 276 | 35.2761
23.1 | 14.7615 | 1 | 7.824 | 276 | 35.2761
23.4 | 15.505 | 1 | 7.824 | 276 | 35.2761
22.6 | 15.3523 | 1 | 7.824 | 276 | 35.2761
21 | 14.6105 | 1 | 7.824 | 276 | 35.2761
20.5 | 14.2283 | 1 | 7.824 | 276 | 35.2761
18.8 | 13.1352 | 1 | 7.824 | 276 | 35.2761
17 | 13.2043 | 1 | 7.824 | 276 | 35.2761
16.3 | 13.0792 | 1 | 7.824 | 276 | 35.2761
14.4 | 12.3108 | 1 | 7.824 | 276 | 35.2761
14.3 | 12.2682 | 1 | 7.824 | 276 | 35.2761
13.8 | 12.1169 | 1 | 7.824 | 276 | 35.2761
13.6 | 12.034 | 1 | 7.824 | 276 | 35.2761
13.3 | 11.7446 | 1 | 7.824 | 276 | 35.2761
12.4 | 11.6471 | 1 | 7.824 | 276 | 35.2761
13.1 | 12.2199 | 1 | 7.824 | 276 | 35.2761
14.6 | 13.1659 | 1 | 7.824 | 276 | 35.2761
15.9 | 13.9601 | 1 | 7.824 | 276 | 35.2761
17.9 | 14.5541 | 1 | 7.824 | 276 | 35.2761
19.4 | 14.9533 | 1 | 7.824 | 276 | 35.2761
19.3 | 14.6534 | 1 | 7.824 | 276 | 35.2761
20.2 | 14.8868 | 1 | 7.824 | 276 | 35.2761
20.3 | 14.7712 | 1 | 7.824 | 276 | 35.2761
20.5 | 14.9474 | 1 | 7.824 | 276 | 35.2761
20.4 | 15.5367 | 1 | 7.824 | 276 | 35.2761
19.9 | 15.5724 | 1 | 7.824 | 276 | 35.2761
18.5 | 16.2121 | 1 | 7.824 | 276 | 35.2761
17.8 | 16.2049 | 1 | 7.824 | 276 | 35.2761
17.7 | 15.7455 | 1 | 7.824 | 276 | 35.2761
17.8 | 15.7221 | 1 | 7.824 | 276 | 35.2761
17.6 | 15.6495 | 1 | 7.824 | 276 | 35.2761
17.4 | 15.5774 | 1 | 7.824 | 276 | 35.2761
16.9 | 15.9449 | 1 | 7.824 | 276 | 35.2761
16.5 | 15.8631 | 1 | 7.824 | 276 | 35.2761
16.6 | 15.9619 | 1 | 7.824 | 276 | 35.2761
16.6 | 16.1511 | 1 | 7.824 | 276 | 35.2761
16.6 | 16.2784 | 1 | 7.824 | 276 | 35.2761
16.7 | 16.1869 | 1 | 7.824 | 276 | 35.2761
16.7 | 16.0608 | 1 | 7.824 | 276 | 35.2761
16.4 | 16.0797 | 1 | 7.824 | 276 | 35.2761
16.8 | 16.0342 | 1 | 7.824 | 276 | 35.2761
17.6 | 16.382 | 1 | 7.824 | 276 | 35.2761
18.5 | 16.3344 | 1 | 7.824 | 276 | 35.2761
20.1 | 16.6626 | 1 | 7.824 | 276 | 35.2761
19.8 | 16.1538 | 1 | 7.824 | 276 | 35.2761
20.2 | 15.9605 | 1 | 7.824 | 276 | 35.2761
20.6 | 16.382 | 1 | 7.824 | 276 | 35.2761
21.6 | 16.9574 | 1 | 7.824 | 276 | 35.2761
20.8 | 16.9071 | 1 | 7.824 | 276 | 35.2761
21.1 | 17.2424 | 1 | 7.824 | 276 | 35.2761
20.7 | 16.9301 | 1 | 7.824 | 276 | 35.2761
19.6 | 16.2543 | 1 | 7.824 | 276 | 35.2761
19.5 | 16.3929 | 1 | 7.824 | 276 | 35.2761
19 | 16.274 | 1 | 7.824 | 276 | 35.2761
18 | 15.387 | 1 | 7.824 | 276 | 35.2761
17 | 14.7269 | 1 | 7.824 | 276 | 35.2761
16.2 | 14.4827 | 1 | 7.824 | 276 | 35.2761
15.2 | 13.6921 | 1 | 7.824 | 276 | 35.2761
14.4 | 13.0898 | 1 | 7.824 | 276 | 35.2761
13.9 | 12.7178 | 1 | 7.824 | 276 | 35.2761
13.8 | 12.5074 | 1 | 7.824 | 276 | 35.2761
13.5 | 12.3853 | 1 | 7.824 | 276 | 35.2761
13.3 | 12.3032 | 1 | 7.824 | 276 | 35.2761
13.5 | 12.4989 | 1 | 7.824 | 276 | 35.2761
14.6 | 13.2833 | 1 | 7.824 | 276 | 35.2761
16.2 | 13.909 | 1 | 7.824 | 276 | 35.2761
18.1 | 14.6347 | 1 | 7.824 | 276 | 35.2761
18.3 | 15.0418 | 1 | 7.824 | 276 | 35.2761
17.5 | 14.9134 | 1 | 7.824 | 276 | 35.2761
18.5 | 15.0049 | 1 | 7.824 | 276 | 35.2761
18.6 | 15.4331 | 1 | 7.824 | 276 | 35.2761
17.7 | 15.5088 | 1 | 7.824 | 276 | 35.2761
16.3 | 15.5414 | 1 | 7.824 | 276 | 35.2761
17.2 | 15.6852 | 1 | 7.824 | 276 | 35.2761
18.6 | 15.6608 | 1 | 7.824 | 276 | 35.2761
19.1 | 15.2795 | 1 | 7.824 | 276 | 35.2761
19.5 | 15.261 | 1 | 7.824 | 276 | 35.2761
19.5 | 14.8334 | 1 | 7.824 | 276 | 35.2761
19 | 15.0749 | 1 | 7.824 | 276 | 35.2761
18 | 15.1521 | 1 | 7.824 | 276 | 35.2761
17.1 | 13.7049 | 1 | 7.824 | 276 | 35.2761
15.5 | 12.9662 | 1 | 7.824 | 276 | 35.2761
14.9 | 12.8352 | 1 | 7.824 | 276 | 35.2761
13.8 | 12.5042 | 1 | 7.824 | 276 | 35.2761
13.9 | 12.1544 | 1 | 7.824 | 276 | 35.2761
13.3 | 11.3111 | 1 | 7.824 | 276 | 35.2761
12.9 | 11.0352 | 1 | 7.824 | 276 | 35.2761
13 | 10.9202 | 1 | 7.824 | 276 | 35.2761
13.3 | 11.0989 | 1 | 7.824 | 276 | 35.2761
14 | 11.6033 | 1 | 7.824 | 276 | 35.2761
15.7 | 11.51 | 1 | 7.824 | 276 | 35.2761
16.7 | 11.9703 | 1 | 7.824 | 276 | 35.2761
16.5 | 11.1974 | 1 | 7.824 | 276 | 35.2761
16.7 | 11.3285 | 1 | 7.824 | 276 | 35.2761
16.5 | 10.7649 | 1 | 7.824 | 276 | 35.2761
14.8 | 11.2779 | 1 | 7.824 | 276 | 35.2761
16.5 | 11.4225 | 1 | 7.824 | 276 | 35.2761
16.9 | 11.1928 | 1 | 7.824 | 276 | 35.2761
16.7 | 11.418 | 1 | 7.824 | 276 | 35.2761
15.9 | 11.2663 | 1 | 7.824 | 276 | 35.2761
12.7 | 10.9517 | 1 | 7.824 | 276 | 35.2761
12.3 | 10.9955 | 1 | 7.824 | 276 | 35.2761
12.2 | 11.0078 | 1 | 7.824 | 276 | 35.2761
12.3 | 10.7813 | 1 | 7.824 | 276 | 35.2761
12.1 | 10.8032 | 1 | 7.824 | 276 | 35.2761
11.6 | 10.5875 | 1 | 7.824 | 276 | 35.2761
11.9 | 10.8257 | 1 | 7.824 | 276 | 35.2761
11.1 | 9.9942 | 1 | 7.824 | 276 | 35.2761
11 | 9.7917 | 1 | 7.824 | 276 | 35.2761
10.5 | 9.5164 | 1 | 7.824 | 276 | 35.2761
10.5 | 9.5164 | 1 | 7.824 | 276 | 35.2761
10.3 | 9.3221 | 1 | 7.824 | 276 | 35.2761
11.1 | 9.7844 | 1 | 7.824 | 276 | 35.2761
12.8 | 10.839 | 1 | 7.824 | 276 | 35.2761
14.5 | 11.8686 | 1 | 7.824 | 276 | 35.2761
16 | 11.8362 | 1 | 7.824 | 276 | 35.2761
16.9 | 12.205 | 1 | 7.824 | 276 | 35.2761
14.8 | 12.9627 | 1 | 7.824 | 276 | 35.2761
15.7 | 13.0991 | 1 | 7.824 | 276 | 35.2761
15.7 | 12.8832 | 1 | 7.824 | 276 | 35.2761
16 | 13.3802 | 1 | 7.824 | 276 | 35.2761
15.3 | 13.7834 | 1 | 7.824 | 276 | 35.2761
15.6 | 13.6124 | 1 | 7.824 | 276 | 35.2761
15.2 | 14.2153 | 1 | 7.824 | 276 | 35.2761
15.4 | 14.5313 | 1 | 7.824 | 276 | 35.2761
15.6 | 14.7276 | 1 | 7.824 | 276 | 35.2761
15.7 | 14.8254 | 1 | 7.824 | 276 | 35.2761
15.7 | 14.7039 | 1 | 7.824 | 276 | 35.2761
15.1 | 14.3573 | 1 | 7.824 | 276 | 35.2761
14 | 13.2161 | 1 | 7.824 | 276 | 35.2761
13.6 | 12.8232 | 1 | 7.824 | 276 | 35.2761
13.2 | 12.6632 | 1 | 7.824 | 276 | 35.2761
13.7 | 13.0391 | 1 | 7.824 | 276 | 35.2761
13.9 | 13.1182 | 1 | 7.824 | 276 | 35.2761
13.6 | 12.8235 | 1 | 7.824 | 276 | 35.2761
13.9 | 12.8851 | 1 | 7.824 | 276 | 35.2761
14.4 | 13.1988 | 1 | 7.824 | 276 | 35.2761
15.5 | 13.5153 | 1 | 7.824 | 276 | 35.2761
16.4 | 13.6429 | 1 | 7.824 | 276 | 35.2761
16.2 | 13.3462 | 1 | 7.824 | 276 | 35.2761
17.4 | 13.342 | 1 | 7.824 | 276 | 35.2761
18.1 | 13.5137 | 1 | 7.824 | 276 | 35.2761
17.2 | 12.1793 | 1 | 7.824 | 276 | 35.2761
17.8 | 12.4235 | 1 | 7.824 | 276 | 35.2761
18.8 | 12.3318 | 1 | 7.824 | 276 | 35.2761
18.9 | 12.1134 | 1 | 7.824 | 276 | 35.2761
19.1 | 11.8617 | 1 | 7.824 | 276 | 35.2761
18.3 | 11.0497 | 1 | 7.824 | 276 | 35.2761
17.5 | 11.4503 | 1 | 7.824 | 276 | 35.2761
16.9 | 11.6416 | 1 | 7.824 | 276 | 35.2761
16.1 | 10.9456 | 1 | 7.824 | 276 | 35.2761
14.9 | 11.1785 | 1 | 7.824 | 276 | 35.2761
14.1 | 10.7891 | 1 | 7.824 | 276 | 35.2761
13.8 | 10.6113 | 1 | 7.824 | 276 | 35.2761
13.5 | 10.5306 | 1 | 7.824 | 276 | 35.2761
13.4 | 10.5366 | 1 | 7.824 | 276 | 35.2761
13.1 | 10.1126 | 1 | 7.824 | 276 | 35.2761
13 | 10.2629 | 1 | 7.824 | 276 | 35.2761
12.8 | 10.476 | 1 | 7.824 | 276 | 35.2761
13.1 | 10.9127 | 1 | 7.824 | 276 | 35.2761
13.6 | 11.4917 | 1 | 7.824 | 276 | 35.2761
14.1 | 12.0198 | 1 | 7.824 | 276 | 35.2761
14.6 | 12.2793 | 1 | 7.824 | 276 | 35.2761
13.7 | 12.8078 | 1 | 7.824 | 276 | 35.2761
14.2 | 12.8932 | 1 | 7.824 | 276 | 35.2761
15.1 | 13.5931 | 1 | 7.824 | 276 | 35.2761
15.5 | 13.7489 | 1 | 7.824 | 276 | 35.2761
17.1 | 14.5894 | 1 | 7.824 | 276 | 35.2761
20 | 14.9173 | 1 | 7.824 | 276 | 35.2761
19.9 | 14.1244 | 1 | 7.824 | 276 | 35.2761
17.3 | 14.6667 | 1 | 7.824 | 276 | 35.2761
17.4 | 14.9325 | 1 | 7.824 | 276 | 35.2761
16.8 | 14.5358 | 1 | 7.824 | 276 | 35.2761
16.6 | 14.7498 | 1 | 7.824 | 276 | 35.2761
16.3 | 14.5783 | 1 | 7.824 | 276 | 35.2761
16.1 | 14.1553 | 1 | 7.824 | 276 | 35.2761
15.8 | 14.0399 | 1 | 7.824 | 276 | 35.2761
15.7 | 14.0591 | 1 | 7.824 | 276 | 35.2761
15.5 | 13.8664 | 1 | 7.824 | 276 | 35.2761
15.3 | 12.8922 | 1 | 7.824 | 276 | 35.2761
14.6 | 12.285 | 1 | 7.824 | 276 | 35.2761
13.9 | 11.943 | 1 | 7.824 | 276 | 35.2761
12.9 | 11.4713 | 1 | 7.824 | 276 | 35.2761
12.9 | 11.3636 | 1 | 7.824 | 276 | 35.2761
13.1 | 11.448 | 1 | 7.824 | 276 | 35.2761
13.6 | 11.7653 | 1 | 7.824 | 276 | 35.2761
15.3 | 11.9004 | 1 | 7.824 | 276 | 35.2761
17.6 | 12.4574 | 1 | 7.824 | 276 | 35.2761
18.4 | 12.8279 | 1 | 7.824 | 276 | 35.2761
18.1 | 13.3337 | 1 | 7.824 | 276 | 35.2761
17.1 | 13.6065 | 1 | 7.824 | 276 | 35.2761
17.1 | 14.037 | 1 | 7.824 | 276 | 35.2761
18 | 14.328 | 1 | 7.824 | 276 | 35.2761
17.9 | 14.0761 | 1 | 7.824 | 276 | 35.2761
19.7 | 14.7091 | 1 | 7.824 | 276 | 35.2761
19.8 | 14.7983 | 1 | 7.824 | 276 | 35.2761
19.1 | 14.7447 | 1 | 7.824 | 276 | 35.2761
18.7 | 14.7009 | 1 | 7.824 | 276 | 35.2761
18.1 | 14.8593 | 1 | 7.824 | 276 | 35.2761
17.7 | 15.1053 | 1 | 7.824 | 276 | 35.2761
17.1 | 14.709 | 1 | 7.824 | 276 | 35.2761
15.7 | 13.718 | 1 | 7.824 | 276 | 35.2761
15.3 | 13.5615 | 1 | 7.824 | 276 | 35.2761
14.8 | 13.1938 | 1 | 7.824 | 276 | 35.2761
14.3 | 13.2239 | 1 | 7.824 | 276 | 35.2761
14.5 | 12.9618 | 1 | 7.824 | 276 | 35.2761
14.6 | 12.9457 | 1 | 7.824 | 276 | 35.2761
14.4 | 12.9782 | 1 | 7.824 | 276 | 35.2761
14.3 | 12.9954 | 1 | 7.824 | 276 | 35.2761
14.4 | 12.9787 | 1 | 7.824 | 276 | 35.2761
15 | 13.3884 | 1 | 7.824 | 276 | 35.2761
15 | 13.5597 | 1 | 7.824 | 276 | 35.2761
15.6 | 13.7378 | 1 | 7.824 | 276 | 35.2761
16.5 | 14.2 | 1 | 7.824 | 276 | 35.2761
16.7 | 14.4467 | 1 | 7.824 | 276 | 35.2761
17.7 | 14.7704 | 1 | 7.824 | 276 | 35.2761
19 | 15.2016 | 1 | 7.824 | 276 | 35.2761
21.3 | 15.8843 | 1 | 7.824 | 276 | 35.2761
21.4 | 15.9205 | 1 | 7.824 | 276 | 35.2761
22.6 | 16.5577 | 1 | 7.824 | 276 | 35.2761
22.1 | 16.5955 | 1 | 7.824 | 276 | 35.2761
21.4 | 16.6757 | 1 | 7.824 | 276 | 35.2761
20.2 | 16.082 | 1 | 7.824 | 276 | 35.2761
18.9 | 15.555 | 1 | 7.824 | 276 | 35.2761
18.3 | 15.6204 | 1 | 7.824 | 276 | 35.2761
17.2 | 15.3923 | 1 | 7.824 | 276 | 35.2761
16.5 | 14.7774 | 1 | 7.824 | 276 | 35.2761
16.2 | 14.6052 | 1 | 7.824 | 276 | 35.2761
15.7 | 14.4146 | 1 | 7.824 | 276 | 35.2761
15.1 | 13.8898 | 1 | 7.824 | 276 | 35.2761
14.5 | 13.5379 | 1 | 7.824 | 276 | 35.2761
14.5 | 13.422 | 1 | 7.824 | 276 | 35.2761
15.1 | 13.7162 | 1 | 7.824 | 276 | 35.2761
16.2 | 14.1451 | 1 | 7.824 | 276 | 35.2761
19.1 | 15.5202 | 1 | 7.824 | 276 | 35.2761
21.6 | 16.643 | 1 | 7.824 | 276 | 35.2761
23.9 | 17.2331 | 1 | 7.824 | 276 | 35.2761
25.3 | 17.3578 | 1 | 7.824 | 276 | 35.2761
26.4 | 17.2973 | 1 | 7.824 | 276 | 35.2761
27.2 | 17.6666 | 1 | 7.824 | 276 | 35.2761
27.9 | 18.287 | 1 | 7.824 | 276 | 35.2761
28.8 | 18.7267 | 1 | 7.824 | 276 | 35.2761
28.6 | 18.8582 | 1 | 7.824 | 276 | 35.2761
29 | 19.0376 | 1 | 7.824 | 276 | 35.2761
28 | 18.5627 | 1 | 7.824 | 276 | 35.2761
27 | 18.7462 | 1 | 7.824 | 276 | 35.2761
25.3 | 17.923 | 1 | 7.824 | 276 | 35.2761
23.8 | 17.7894 | 1 | 7.824 | 276 | 35.2761
22.6 | 17.5465 | 1 | 7.824 | 276 | 35.2761
21.5 | 17.3402 | 1 | 7.824 | 276 | 35.2761
20.2 | 17.1822 | 1 | 7.824 | 276 | 35.2761
19.8 | 16.572 | 1 | 7.824 | 276 | 35.2761
19.5 | 16.4071 | 1 | 7.824 | 276 | 35.2761
19.2 | 16.0683 | 1 | 7.824 | 276 | 35.2761
18.5 | 16.2251 | 1 | 7.824 | 276 | 35.2761
19.1 | 15.9747 | 1 | 7.824 | 276 | 35.2761
19.2 | 16.1847 | 1 | 7.824 | 276 | 35.2761
21 | 16.3799 | 1 | 7.824 | 276 | 35.2761
23.3 | 17.4051 | 1 | 7.824 | 276 | 35.2761
23.3 | 18.1824 | 1 | 7.824 | 276 | 35.2761
24.6 | 17.9561 | 1 | 7.824 | 276 | 35.2761
25.6 | 18.7765 | 1 | 7.824 | 276 | 35.2761
26.1 | 18.8312 | 1 | 7.824 | 276 | 35.2761
26.4 | 19.2557 | 1 | 7.824 | 276 | 35.2761
26.6 | 18.9916 | 1 | 7.824 | 276 | 35.2761
27.3 | 19.0589 | 1 | 7.824 | 276 | 35.2761
27.5 | 18.9667 | 1 | 7.824 | 276 | 35.2761
27 | 17.7969 | 1 | 7.824 | 276 | 35.2761
26.3 | 17.4128 | 1 | 7.824 | 276 | 35.2761
24.3 | 17.7452 | 1 | 7.824 | 276 | 35.2761
22.9 | 16.8891 | 1 | 7.824 | 276 | 35.2761
21.9 | 16.3231 | 1 | 7.824 | 276 | 35.2761
20.9 | 16.5099 | 1 | 7.824 | 276 | 35.2761
20.3 | 16.6352 | 1 | 7.824 | 276 | 35.2761
19.2 | 16.5355 | 1 | 7.824 | 276 | 35.2761
17.4 | 15.352 | 1 | 7.824 | 276 | 35.2761
16.3 | 14.4721 | 1 | 7.824 | 276 | 35.2761
15.5 | 13.8752 | 1 | 7.824 | 276 | 35.2761
14.8 | 12.9773 | 1 | 7.824 | 276 | 35.2761
14.5 | 12.4177 | 1 | 7.824 | 276 | 35.2761
14.7 | 12.4461 | 1 | 7.824 | 276 | 35.2761
16.1 | 13.068 | 1 | 7.824 | 276 | 35.2761
17 | 13.4275 | 1 | 7.824 | 276 | 35.2761
18.7 | 14.1437 | 1 | 7.824 | 276 | 35.2761
20.1 | 14.8318 | 1 | 7.824 | 276 | 35.2761
21.7 | 15.3306 | 1 | 7.824 | 276 | 35.2761
23.4 | 16.0972 | 1 | 7.824 | 276 | 35.2761
25.2 | 16.5965 | 1 | 7.824 | 276 | 35.2761
25.9 | 17.2205 | 1 | 7.824 | 276 | 35.2761
27 | 17.5035 | 1 | 7.824 | 276 | 35.2761
26.9 | 17.1393 | 1 | 7.824 | 276 | 35.2761
26.7 | 17.3501 | 1 | 7.824 | 276 | 35.2761
26.5 | 17.6147 | 1 | 7.824 | 276 | 35.2761
24.3 | 17.3143 | 1 | 7.824 | 276 | 35.2761
22 | 16.6178 | 1 | 7.824 | 276 | 35.2761
20.1 | 16.1047 | 1 | 7.824 | 276 | 35.2761
19.7 | 15.9056 | 1 | 7.824 | 276 | 35.2761
18.4 | 15.6014 | 1 | 7.824 | 276 | 35.2761
17.2 | 15.0412 | 1 | 7.824 | 276 | 35.2761
15.8 | 14.2778 | 1 | 7.824 | 276 | 35.2761
15.4 | 14.1817 | 1 | 7.824 | 276 | 35.2761
15.2 | 14.2228 | 1 | 7.824 | 276 | 35.2761
14.9 | 13.9292 | 1 | 7.824 | 276 | 35.2761
14.9 | 14.0472 | 1 | 7.824 | 276 | 35.2761
16.3 | 14.76 | 1 | 7.824 | 276 | 35.2761
17.8 | 15.5535 | 1 | 7.824 | 276 | 35.2761
20 | 16.637 | 1 | 7.824 | 276 | 35.2761
22.3 | 17.5501 | 1 | 7.824 | 276 | 35.2761
24.5 | 18.4018 | 1 | 7.824 | 276 | 35.2761
26.3 | 18.8257 | 1 | 7.824 | 276 | 35.2761
27.6 | 19.2453 | 1 | 7.824 | 276 | 35.2761
29.1 | 20.3578 | 1 | 7.824 | 276 | 35.2761
29 | 20.2727 | 1 | 7.824 | 276 | 35.2761
28.9 | 19.4965 | 1 | 7.824 | 276 | 35.2761
29.5 | 19.7858 | 1 | 7.824 | 276 | 35.2761
28.5 | 19.7351 | 1 | 7.824 | 276 | 35.2761
28.8 | 20.0431 | 1 | 7.824 | 276 | 35.2761
26.6 | 20.0879 | 1 | 7.824 | 276 | 35.2761
25.2 | 19.8282 | 1 | 7.824 | 276 | 35.2761
23.6 | 19.024 | 1 | 7.824 | 276 | 35.2761
22.4 | 18.5123 | 1 | 7.824 | 276 | 35.2761
21 | 18.1103 | 1 | 7.824 | 276 | 35.2761
20.5 | 17.3955 | 1 | 7.824 | 276 | 35.2761
19.8 | 16.915 | 1 | 7.824 | 276 | 35.2761
19.3 | 16.5023 | 1 | 7.824 | 276 | 35.2761
18.7 | 16.1107 | 1 | 7.824 | 276 | 35.2761
18.3 | 15.7903 | 1 | 7.824 | 276 | 35.2761
18.1 | 15.7176 | 1 | 7.824 | 276 | 35.2761
19 | 16.1012 | 1 | 7.824 | 276 | 35.2761
20.3 | 16.9697 | 1 | 7.824 | 276 | 35.2761
22.1 | 17.9366 | 1 | 7.824 | 276 | 35.2761
24.6 | 19.2239 | 1 | 7.824 | 276 | 35.2761
26.5 | 19.6517 | 1 | 7.824 | 276 | 35.2761
28.1 | 19.9841 | 1 | 7.824 | 276 | 35.2761
28.9 | 19.905 | 1 | 7.824 | 276 | 35.2761
30 | 19.9293 | 1 | 7.824 | 276 | 35.2761
29.5 | 19.7706 | 1 | 7.824 | 276 | 35.2761
30.1 | 18.7301 | 1 | 7.824 | 276 | 35.2761
30.7 | 18.3331 | 1 | 7.824 | 276 | 35.2761
29.4 | 16.6849 | 1 | 7.824 | 276 | 35.2761
28.3 | 16.096 | 1 | 7.824 | 276 | 35.2761
27.2 | 15.6217 | 1 | 7.824 | 276 | 35.2761
25.2 | 16.4564 | 1 | 7.824 | 276 | 35.2761
23.3 | 16.1708 | 1 | 7.824 | 276 | 35.2761
21.7 | 16.167 | 1 | 7.824 | 276 | 35.2761
20.2 | 15.7359 | 1 | 7.824 | 276 | 35.2761
19.6 | 15.573 | 1 | 7.824 | 276 | 35.2761
19.1 | 15.7276 | 1 | 7.824 | 276 | 35.2761
18.1 | 15.4786 | 1 | 7.824 | 276 | 35.2761
17.5 | 15.1993 | 1 | 7.824 | 276 | 35.2761
16.9 | 14.7438 | 1 | 7.824 | 276 | 35.2761
16.7 | 14.8438 | 1 | 7.824 | 276 | 35.2761
17.4 | 15.4568 | 1 | 7.824 | 276 | 35.2761
18.1 | 15.8297 | 1 | 7.824 | 276 | 35.2761
19 | 16.6289 | 1 | 7.824 | 276 | 35.2761
20.8 | 17.3711 | 1 | 7.824 | 276 | 35.2761
22.7 | 17.8387 | 1 | 7.824 | 276 | 35.2761
24.6 | 17.8082 | 1 | 7.824 | 276 | 35.2761
26 | 17.6049 | 1 | 7.824 | 276 | 35.2761
26.1 | 17.5886 | 1 | 7.824 | 276 | 35.2761
27.5 | 18.1562 | 1 | 7.824 | 276 | 35.2761
26.8 | 17.8737 | 1 | 7.824 | 276 | 35.2761
26.2 | 17.1338 | 1 | 7.824 | 276 | 35.2761
26.7 | 17.2103 | 1 | 7.824 | 276 | 35.2761
25.9 | 16.6058 | 1 | 7.824 | 276 | 35.2761
25.7 | 16.3972 | 1 | 7.824 | 276 | 35.2761
23.8 | 16.5481 | 1 | 7.824 | 276 | 35.2761
22.2 | 16.1372 | 1 | 7.824 | 276 | 35.2761
20.9 | 16.0441 | 1 | 7.824 | 276 | 35.2761
19.3 | 15.7446 | 1 | 7.824 | 276 | 35.2761
19 | 14.6492 | 1 | 7.824 | 276 | 35.2761
17.9 | 14.0716 | 1 | 7.824 | 276 | 35.2761
16.7 | 13.6607 | 1 | 7.824 | 276 | 35.2761
15.8 | 13.0899 | 1 | 7.824 | 276 | 35.2761
14.9 | 12.4056 | 1 | 7.824 | 276 | 35.2761
14.8 | 12.1539 | 1 | 7.824 | 276 | 35.2761
15.4 | 11.7894 | 1 | 7.824 | 276 | 35.2761
16.8 | 12.3178 | 1 | 7.824 | 276 | 35.2761
17.5 | 12.3676 | 1 | 7.824 | 276 | 35.2761
18.9 | 13.1191 | 1 | 7.824 | 276 | 35.2761
19.9 | 13.7946 | 1 | 7.824 | 276 | 35.2761
21.2 | 14.0197 | 1 | 7.824 | 276 | 35.2761
21.9 | 14.1988 | 1 | 7.824 | 276 | 35.2761
22.9 | 14.8915 | 1 | 7.824 | 276 | 35.2761
23.1 | 14.7427 | 1 | 7.824 | 276 | 35.2761
23.7 | 15.0079 | 1 | 7.824 | 276 | 35.2761
24 | 15.2074 | 1 | 7.824 | 276 | 35.2761
23.8 | 14.7846 | 1 | 7.824 | 276 | 35.2761
23.5 | 14.9335 | 1 | 7.824 | 276 | 35.2761
22.8 | 14.6712 | 1 | 7.824 | 276 | 35.2761
21.7 | 14.5291 | 1 | 7.824 | 276 | 35.2761
20.8 | 14.62 | 1 | 7.824 | 276 | 35.2761
20.2 | 14.4419 | 1 | 7.824 | 276 | 35.2761
19.4 | 14.1865 | 1 | 7.824 | 276 | 35.2761
17.3 | 14.0583 | 1 | 7.824 | 276 | 35.2761
16.3 | 13.7812 | 1 | 7.824 | 276 | 35.2761
15.3 | 12.8922 | 1 | 7.824 | 276 | 35.2761
15.3 | 12.6756 | 1 | 7.824 | 276 | 35.2761
15 | 12.3941 | 1 | 7.824 | 276 | 35.2761
14.6 | 12.5 | 1 | 7.824 | 276 | 35.2761
15.7 | 12.8911 | 1 | 7.824 | 276 | 35.2761
17.8 | 13.7716 | 1 | 7.824 | 276 | 35.2761
19.9 | 14.5763 | 1 | 7.824 | 276 | 35.2761
21.7 | 15.1988 | 1 | 7.824 | 276 | 35.2761
23.3 | 15.9293 | 1 | 7.824 | 276 | 35.2761
25 | 16.4837 | 1 | 7.824 | 276 | 35.2761
26 | 16.5097 | 1 | 7.824 | 276 | 35.2761
26.9 | 17.1883 | 1 | 7.824 | 276 | 35.2761
28.5 | 17.28 | 1 | 7.824 | 276 | 35.2761
27.9 | 16.8989 | 1 | 7.824 | 276 | 35.2761
28.5 | 17.4087 | 1 | 7.824 | 276 | 35.2761
27.2 | 16.8285 | 1 | 7.824 | 276 | 35.2761
26.5 | 16.4466 | 1 | 7.824 | 276 | 35.2761
25 | 15.959 | 1 | 7.824 | 276 | 35.2761
23.6 | 15.5928 | 1 | 7.824 | 276 | 35.2761
22.2 | 15.0321 | 1 | 7.824 | 276 | 35.2761
21 | 15.1285 | 1 | 7.824 | 276 | 35.2761
19.6 | 14.7103 | 1 | 7.824 | 276 | 35.2761
18.3 | 14.1643 | 1 | 7.824 | 276 | 35.2761
17.6 | 14.1102 | 1 | 7.824 | 276 | 35.2761
17.1 | 14.0263 | 1 | 7.824 | 276 | 35.2761
16.1 | 13.6949 | 1 | 7.824 | 276 | 35.2761
15.9 | 13.7305 | 1 | 7.824 | 276 | 35.2761
15.6 | 13.7269 | 1 | 7.824 | 276 | 35.2761
16.8 | 14.1881 | 1 | 7.824 | 276 | 35.2761
17.7 | 14.7528 | 1 | 7.824 | 276 | 35.2761
19.3 | 15.3995 | 1 | 7.824 | 276 | 35.2761
21.7 | 15.6325 | 1 | 7.824 | 276 | 35.2761
22.3 | 15.2531 | 1 | 7.824 | 276 | 35.2761
22.6 | 15.4087 | 1 | 7.824 | 276 | 35.2761
23.3 | 15.8076 | 1 | 7.824 | 276 | 35.2761
26.4 | 16.3047 | 1 | 7.824 | 276 | 35.2761
24.3 | 15.8304 | 1 | 7.824 | 276 | 35.2761
23.1 | 16.0292 | 1 | 7.824 | 276 | 35.2761
20.7 | 16.9156 | 1 | 7.824 | 276 | 35.2761
21.6 | 17.167 | 1 | 7.824 | 276 | 35.2761
17.7 | 16.7268 | 1 | 7.824 | 276 | 35.2761
17.6 | 15.4069 | 1 | 7.824 | 276 | 35.2761
17.4 | 14.8102 | 1 | 7.824 | 276 | 35.2761
16.2 | 13.2404 | 1 | 7.824 | 276 | 35.2761
15.6 | 12.6293 | 1 | 7.824 | 276 | 35.2761
14.4 | 12.1958 | 1 | 7.824 | 276 | 35.2761
14.1 | 12.3469 | 1 | 7.824 | 276 | 35.2761
14.3 | 12.6499 | 1 | 7.824 | 276 | 35.2761
14.1 | 12.4576 | 1 | 7.824 | 276 | 35.2761
13.7 | 12.2956 | 1 | 7.824 | 276 | 35.2761
13.2 | 11.9793 | 1 | 7.824 | 276 | 35.2761
13.8 | 12.0607 | 1 | 7.824 | 276 | 35.2761
14.1 | 11.9152 | 1 | 7.824 | 276 | 35.2761
15.6 | 12.3232 | 1 | 7.824 | 276 | 35.2761
17.1 | 12.5333 | 1 | 7.824 | 276 | 35.2761
17.5 | 11.6825 | 1 | 7.824 | 276 | 35.2761
18.4 | 11.5091 | 1 | 7.824 | 276 | 35.2761
19.9 | 12.256 | 1 | 7.824 | 276 | 35.2761
21.1 | 12.2416 | 1 | 7.824 | 276 | 35.2761
20.9 | 12.8239 | 1 | 7.824 | 276 | 35.2761
23.1 | 13.6547 | 1 | 7.824 | 276 | 35.2761
23 | 13.7745 | 1 | 7.824 | 276 | 35.2761
22.5 | 13.4594 | 1 | 7.824 | 276 | 35.2761
20.9 | 13.2829 | 1 | 7.824 | 276 | 35.2761
20 | 13.2357 | 1 | 7.824 | 276 | 35.2761
19.3 | 13.1851 | 1 | 7.824 | 276 | 35.2761
18.5 | 13.054 | 1 | 7.824 | 276 | 35.2761
17.7 | 13.2251 | 1 | 7.824 | 276 | 35.2761
17.1 | 13.1896 | 1 | 7.824 | 276 | 35.2761
16.6 | 13.1985 | 1 | 7.824 | 276 | 35.2761
16.6 | 13.3569 | 1 | 7.824 | 276 | 35.2761
15.9 | 13.2954 | 1 | 7.824 | 276 | 35.2761
15.6 | 13.5085 | 1 | 7.824 | 276 | 35.2761
15.5 | 13.7516 | 1 | 7.824 | 276 | 35.2761
14.9 | 13.4028 | 1 | 7.824 | 276 | 35.2761
15.6 | 13.2863 | 1 | 7.824 | 276 | 35.2761
16.8 | 14.0866 | 1 | 7.824 | 276 | 35.2761
17.5 | 13.3496 | 1 | 7.824 | 276 | 35.2761
17.5 | 12.8015 | 1 | 7.824 | 276 | 35.2761
18.3 | 12.9784 | 1 | 7.824 | 276 | 35.2761
19.2 | 12.877 | 1 | 7.824 | 276 | 35.2761
20.7 | 13.2987 | 1 | 7.824 | 276 | 35.2761
22.1 | 13.8475 | 1 | 7.824 | 276 | 35.2761
23.4 | 14.1826 | 1 | 7.824 | 276 | 35.2761
24.3 | 14.3259 | 1 | 7.824 | 276 | 35.2761
24.9 | 14.06 | 1 | 7.824 | 276 | 35.2761
23.7 | 14.0563 | 1 | 7.824 | 276 | 35.2761
24 | 14.3347 | 1 | 7.824 | 276 | 35.2761
23.1 | 14.1119 | 1 | 7.824 | 276 | 35.2761
22 | 13.6435 | 1 | 7.824 | 276 | 35.2761
20.5 | 13.0932 | 1 | 7.824 | 276 | 35.2761
18.7 | 12.8168 | 1 | 7.824 | 276 | 35.2761
17.2 | 12.2081 | 1 | 7.824 | 276 | 35.2761
15.9 | 11.6204 | 1 | 7.824 | 276 | 35.2761
15 | 11.2881 | 1 | 7.824 | 276 | 35.2761
15 | 11.2881 | 1 | 7.824 | 276 | 35.2761
12.9 | 10.4825 | 1 | 7.824 | 276 | 35.2761
12.5 | 10.51 | 1 | 7.824 | 276 | 35.2761
12.5 | 10.8746 | 1 | 7.824 | 276 | 35.2761
12.3 | 10.7884 | 1 | 7.824 | 276 | 35.2761
13.5 | 11.6185 | 1 | 7.824 | 276 | 35.2761
15.8 | 12.4144 | 1 | 7.824 | 276 | 35.2761
16.7 | 12.5781 | 1 | 7.824 | 276 | 35.2761
17.3 | 12.7227 | 1 | 7.824 | 276 | 35.2761
18.3 | 13.1722 | 1 | 7.824 | 276 | 35.2761
18.2 | 13.3276 | 1 | 7.824 | 276 | 35.2761
18.7 | 13.722 | 1 | 7.824 | 276 | 35.2761
20.3 | 14.4351 | 1 | 7.824 | 276 | 35.2761
21.6 | 15.1198 | 1 | 7.824 | 276 | 35.2761
22.3 | 15.2817 | 1 | 7.824 | 276 | 35.2761
23.1 | 15.8625 | 1 | 7.824 | 276 | 35.2761
22.5 | 15.6943 | 1 | 7.824 | 276 | 35.2761
22.6 | 15.6813 | 1 | 7.824 | 276 | 35.2761
21.2 | 15.2682 | 1 | 7.824 | 276 | 35.2761
19.2 | 14.5202 | 1 | 7.824 | 276 | 35.2761
17.4 | 13.7237 | 1 | 7.824 | 276 | 35.2761
15.5 | 12.7596 | 1 | 7.824 | 276 | 35.2761
14.6 | 12.5026 | 1 | 7.824 | 276 | 35.2761
14.2 | 12.3386 | 1 | 7.824 | 276 | 35.2761
13.4 | 11.9544 | 1 | 7.824 | 276 | 35.2761
13.4 | 11.9544 | 1 | 7.824 | 276 | 35.2761
12.7 | 11.7187 | 1 | 7.824 | 276 | 35.2761
12.6 | 11.6207 | 1 | 7.824 | 276 | 35.2761
12.7 | 11.7183 | 1 | 7.824 | 276 | 35.2761
14 | 12.5891 | 1 | 7.824 | 276 | 35.2761
15.4 | 13.3172 | 1 | 7.824 | 276 | 35.2761
16.3 | 14.0049 | 1 | 7.824 | 276 | 35.2761
17.2 | 14.4617 | 1 | 7.824 | 276 | 35.2761
17.2 | 14.5743 | 1 | 7.824 | 276 | 35.2761
18.3 | 15.0418 | 1 | 7.824 | 276 | 35.2761
19.5 | 15.2657 | 1 | 7.824 | 276 | 35.2761
20.1 | 15.6467 | 1 | 7.824 | 276 | 35.2761
20.2 | 15.5209 | 1 | 7.824 | 276 | 35.2761
20.3 | 15.6651 | 1 | 7.824 | 276 | 35.2761
20.3 | 15.6634 | 1 | 7.824 | 276 | 35.2761
21.3 | 15.6551 | 1 | 7.824 | 276 | 35.2761
21.1 | 15.1194 | 1 | 7.824 | 276 | 35.2761
20.7 | 15.2782 | 1 | 7.824 | 276 | 35.2761
19.3 | 14.9713 | 1 | 7.824 | 276 | 35.2761
18.4 | 14.7982 | 1 | 7.824 | 276 | 35.2761
17.9 | 14.7772 | 1 | 7.824 | 276 | 35.2761
17.2 | 14.4565 | 1 | 7.824 | 276 | 35.2761
17.2 | 14.1781 | 1 | 7.824 | 276 | 35.2761
16.5 | 14.0763 | 1 | 7.824 | 276 | 35.2761
16.7 | 14.4364 | 1 | 7.824 | 276 | 35.2761
16.5 | 14.3025 | 1 | 7.824 | 276 | 35.2761
16.5 | 14.6496 | 1 | 7.824 | 276 | 35.2761
16.7 | 14.841 | 1 | 7.824 | 276 | 35.2761
16.7 | 14.7238 | 1 | 7.824 | 276 | 35.2761
17.1 | 14.9313 | 1 | 7.824 | 276 | 35.2761
18.1 | 15.3004 | 1 | 7.824 | 276 | 35.2761
18.2 | 15.2797 | 1 | 7.824 | 276 | 35.2761
18.5 | 15.1072 | 1 | 7.824 | 276 | 35.2761
19 | 15.4027 | 1 | 7.824 | 276 | 35.2761
20.5 | 15.8359 | 1 | 7.824 | 276 | 35.2761
22 | 16.0507 | 1 | 7.824 | 276 | 35.2761
21.7 | 15.9436 | 1 | 7.824 | 276 | 35.2761
21.7 | 16.1531 | 1 | 7.824 | 276 | 35.2761
21.9 | 16.2772 | 1 | 7.824 | 276 | 35.2761
21.7 | 16.3679 | 1 | 7.824 | 276 | 35.2761
21.9 | 16.4904 | 1 | 7.824 | 276 | 35.2761
21 | 16.6751 | 1 | 7.824 | 276 | 35.2761
18.7 | 16.5181 | 1 | 7.824 | 276 | 35.2761
17.7 | 16.5378 | 1 | 7.824 | 276 | 35.2761
17.9 | 15.399 | 1 | 7.824 | 276 | 35.2761
17.1 | 15.1646 | 1 | 7.824 | 276 | 35.2761
16.4 | 14.9053 | 1 | 7.824 | 276 | 35.2761
15.8 | 14.8025 | 1 | 7.824 | 276 | 35.2761
15.6 | 14.6067 | 1 | 7.824 | 276 | 35.2761
15.1 | 14.5403 | 1 | 7.824 | 276 | 35.2761
15.3 | 14.6154 | 1 | 7.824 | 276 | 35.2761
15.5 | 14.9353 | 1 | 7.824 | 276 | 35.2761
15.5 | 14.9353 | 1 | 7.824 | 276 | 35.2761
15.7 | 14.9475 | 1 | 7.824 | 276 | 35.2761
15.7 | 15.0708 | 1 | 7.824 | 276 | 35.2761
15.6 | 15.0337 | 1 | 7.824 | 276 | 35.2761
16.2 | 15.6267 | 1 | 7.824 | 276 | 35.2761
16.4 | 15.9506 | 1 | 7.824 | 276 | 35.2761
16.7 | 16.184 | 1 | 7.824 | 276 | 35.2761
16.7 | 16.184 | 1 | 7.824 | 276 | 35.2761
19.4 | 17.7468 | 1 | 7.824 | 276 | 35.2761
19.9 | 17.1694 | 1 | 7.824 | 276 | 35.2761
20 | 16.8432 | 1 | 7.824 | 276 | 35.2761
21.3 | 16.2139 | 1 | 7.824 | 276 | 35.2761
20.5 | 15.6034 | 1 | 7.824 | 276 | 35.2761
19.5 | 15.1318 | 1 | 7.824 | 276 | 35.2761
18.3 | 15.0235 | 1 | 7.824 | 276 | 35.2761
17.9 | 14.9324 | 1 | 7.824 | 276 | 35.2761
17.4 | 14.9185 | 1 | 7.824 | 276 | 35.2761
16.9 | 14.7331 | 1 | 7.824 | 276 | 35.2761
16.9 | 14.7331 | 1 | 7.824 | 276 | 35.2761
16.4 | 14.7826 | 1 | 7.824 | 276 | 35.2761
15.8 | 15.1685 | 1 | 7.824 | 276 | 35.2761
15.6 | 15.2828 | 1 | 7.824 | 276 | 35.2761
15.7 | 15.2565 | 1 | 7.824 | 276 | 35.2761
16.1 | 15.6528 | 1 | 7.824 | 276 | 35.2761
16.4 | 15.5106 | 1 | 7.824 | 276 | 35.2761
16.4 | 15.082 | 1 | 7.824 | 276 | 35.2761
17 | 15.6656 | 1 | 7.824 | 276 | 35.2761
17.6 | 16.064 | 1 | 7.824 | 276 | 35.2761
15.9 | 15.1435 | 1 | 7.824 | 276 | 35.2761
16.2 | 15.0093 | 1 | 7.824 | 276 | 35.2761
16.5 | 14.644 | 1 | 7.824 | 276 | 35.2761
16.1 | 14.0298 | 1 | 7.824 | 276 | 35.2761
15.5 | 13.5145 | 1 | 7.824 | 276 | 35.2761
15.3 | 13.3242 | 1 | 7.824 | 276 | 35.2761
15.7 | 13.4257 | 1 | 7.824 | 276 | 35.2761
15.8 | 13.0812 | 1 | 7.824 | 276 | 35.2761
15.7 | 12.8798 | 1 | 7.824 | 276 | 35.2761
15.7 | 12.5111 | 1 | 7.824 | 276 | 35.2761
15.6 | 12.6293 | 1 | 7.824 | 276 | 35.2761
15.3 | 12.4554 | 1 | 7.824 | 276 | 35.2761
15 | 12.1755 | 1 | 7.824 | 276 | 35.2761
14.8 | 12.0424 | 1 | 7.824 | 276 | 35.2761
14.6 | 11.8556 | 1 | 7.824 | 276 | 35.2761
14.4 | 11.8774 | 1 | 7.824 | 276 | 35.2761
14.2 | 11.7946 | 1 | 7.824 | 276 | 35.2761
14.1 | 11.7005 | 1 | 7.824 | 276 | 35.2761
14 | 11.7116 | 1 | 7.824 | 276 | 35.2761
14 | 11.8186 | 1 | 7.824 | 276 | 35.2761
14.4 | 12.0904 | 1 | 7.824 | 276 | 35.2761
15.2 | 12.0015 | 1 | 7.824 | 276 | 35.2761
15.9 | 12.0878 | 1 | 7.824 | 276 | 35.2761
17.1 | 12.1917 | 1 | 7.824 | 276 | 35.2761
17.5 | 12.2614 | 1 | 7.824 | 276 | 35.2761
18 | 12.6515 | 1 | 7.824 | 276 | 35.2761
19.2 | 13.175 | 1 | 7.824 | 276 | 35.2761
19.1 | 12.9965 | 1 | 7.824 | 276 | 35.2761
19.6 | 13.3791 | 1 | 7.824 | 276 | 35.2761
19.5 | 13.2933 | 1 | 7.824 | 276 | 35.2761
18.9 | 13.2447 | 1 | 7.824 | 276 | 35.2761
18.5 | 13.4755 | 1 | 7.824 | 276 | 35.2761
18 | 13.0797 | 1 | 7.824 | 276 | 35.2761
17.5 | 12.3529 | 1 | 7.824 | 276 | 35.2761
16.9 | 11.8732 | 1 | 7.824 | 276 | 35.2761
15.9 | 12.4912 | 1 | 7.824 | 276 | 35.2761
15.7 | 12.2053 | 1 | 7.824 | 276 | 35.2761
14.5 | 12.2914 | 1 | 7.824 | 276 | 35.2761
14.1 | 13.1402 | 1 | 7.824 | 276 | 35.2761
14 | 12.6977 | 1 | 7.824 | 276 | 35.2761
13.7 | 12.691 | 1 | 7.824 | 276 | 35.2761
13.5 | 12.8429 | 1 | 7.824 | 276 | 35.2761
13.4 | 12.8616 | 1 | 7.824 | 276 | 35.2761
12.8 | 12.2691 | 1 | 7.824 | 276 | 35.2761
12.9 | 12.3678 | 1 | 7.824 | 276 | 35.2761
12.9 | 12.4846 | 1 | 7.824 | 276 | 35.2761
12.8 | 12.4441 | 1 | 7.824 | 276 | 35.2761
13.3 | 12.8807 | 1 | 7.824 | 276 | 35.2761
13.4 | 12.9797 | 1 | 7.824 | 276 | 35.2761
13.6 | 12.9414 | 1 | 7.824 | 276 | 35.2761
14 | 13.3354 | 1 | 7.824 | 276 | 35.2761
14.4 | 13.8494 | 1 | 7.824 | 276 | 35.2761
14.9 | 14.222 | 1 | 7.824 | 276 | 35.2761
15.1 | 14.4191 | 1 | 7.824 | 276 | 35.2761
15 | 14.5032 | 1 | 7.824 | 276 | 35.2761
15.3 | 14.8618 | 1 | 7.824 | 276 | 35.2761
15.4 | 14.9607 | 1 | 7.824 | 276 | 35.2761
15.5 | 15.0598 | 1 | 7.824 | 276 | 35.2761
15.5 | 15.06 | 1 | 7.824 | 276 | 35.2761
15.5 | 15.1846 | 1 | 7.824 | 276 | 35.2761
15.5 | 15.3101 | 1 | 7.824 | 276 | 35.2761
15.5 | 15.3101 | 1 | 7.824 | 276 | 35.2761
15.3 | 15.1737 | 1 | 7.824 | 276 | 35.2761
15.2 | 15.0739 | 1 | 7.824 | 276 | 35.2761
15.3 | 15.1108 | 1 | 7.824 | 276 | 35.2761
15.5 | 15.3732 | 1 | 7.824 | 276 | 35.2761
15.7 | 15.5726 | 1 | 7.824 | 276 | 35.2761
15.9 | 15.7721 | 1 | 7.824 | 276 | 35.2761
16.1 | 15.9076 | 1 | 7.824 | 276 | 35.2761
16.4 | 16.2708 | 1 | 7.824 | 276 | 35.2761
17 | 16.8043 | 1 | 7.824 | 276 | 35.2761
17.5 | 17.1717 | 1 | 7.824 | 276 | 35.2761
19.2 | 18.4612 | 1 | 7.824 | 276 | 35.2761
21.7 | 19.2002 | 1 | 7.824 | 276 | 35.2761
23.2 | 19.6728 | 1 | 7.824 | 276 | 35.2761
24.4 | 19.1362 | 1 | 7.824 | 276 | 35.2761
22.9 | 18.4776 | 1 | 7.824 | 276 | 35.2761
22.4 | 19.0456 | 1 | 7.824 | 276 | 35.2761
24.9 | 18.7753 | 1 | 7.824 | 276 | 35.2761
23.3 | 18.5471 | 1 | 7.824 | 276 | 35.2761
23.7 | 18.6182 | 1 | 7.824 | 276 | 35.2761
22.3 | 17.9848 | 1 | 7.824 | 276 | 35.2761
20.9 | 17.636 | 1 | 7.824 | 276 | 35.2761
19.5 | 17.2224 | 1 | 7.824 | 276 | 35.2761
18.8 | 16.7358 | 1 | 7.824 | 276 | 35.2761
17.3 | 15.5364 | 1 | 7.824 | 276 | 35.2761
16.5 | 14.7657 | 1 | 7.824 | 276 | 35.2761
16 | 14.5783 | 1 | 7.824 | 276 | 35.2761
15.4 | 14.1738 | 1 | 7.824 | 276 | 35.2761
15.7 | 14.4063 | 1 | 7.824 | 276 | 35.2761
15.2 | 13.9786 | 1 | 7.824 | 276 | 35.2761
14.9 | 13.6872 | 1 | 7.824 | 276 | 35.2761
15.5 | 13.9773 | 1 | 7.824 | 276 | 35.2761
17.2 | 14.3423 | 1 | 7.824 | 276 | 35.2761
17.9 | 14.4418 | 1 | 7.824 | 276 | 35.2761
19.9 | 14.463 | 1 | 7.824 | 276 | 35.2761
19.8 | 14.2251 | 1 | 7.824 | 276 | 35.2761
22.4 | 15.688 | 1 | 7.824 | 276 | 35.2761
21.1 | 14.9128 | 1 | 7.824 | 276 | 35.2761
22 | 14.9552 | 1 | 7.824 | 276 | 35.2761
22.6 | 15.2723 | 1 | 7.824 | 276 | 35.2761
23 | 15.5142 | 1 | 7.824 | 276 | 35.2761
22.5 | 15.3317 | 1 | 7.824 | 276 | 35.2761
20.5 | 14.3927 | 1 | 7.824 | 276 | 35.2761
20.2 | 14.4266 | 1 | 7.824 | 276 | 35.2761
19.9 | 14.5642 | 1 | 7.824 | 276 | 35.2761
19.3 | 14.1847 | 1 | 7.824 | 276 | 35.2761
17.9 | 13.7504 | 1 | 7.824 | 276 | 35.2761
16.7 | 13.6559 | 1 | 7.824 | 276 | 35.2761
15.4 | 13.2009 | 1 | 7.824 | 276 | 35.2761
14.5 | 12.8429 | 1 | 7.824 | 276 | 35.2761
14.1 | 12.5699 | 1 | 7.824 | 276 | 35.2761
13.6 | 12.4237 | 1 | 7.824 | 276 | 35.2761
13.1 | 12.2199 | 1 | 7.824 | 276 | 35.2761
13.4 | 12.629 | 1 | 7.824 | 276 | 35.2761
14.1 | 13.025 | 1 | 7.824 | 276 | 35.2761
14.6 | 13.3963 | 1 | 7.824 | 276 | 35.2761
15.5 | 13.7475 | 1 | 7.824 | 276 | 35.2761
16.1 | 13.8097 | 1 | 7.824 | 276 | 35.2761
17.3 | 13.9423 | 1 | 7.824 | 276 | 35.2761
18.2 | 14.3941 | 1 | 7.824 | 276 | 35.2761
19.3 | 14.4936 | 1 | 7.824 | 276 | 35.2761
20.1 | 14.5385 | 1 | 7.824 | 276 | 35.2761
20.6 | 15.0805 | 1 | 7.824 | 276 | 35.2761
19.5 | 15.2563 | 1 | 7.824 | 276 | 35.2761
21 | 15.6958 | 1 | 7.824 | 276 | 35.2761
19.1 | 14.8384 | 1 | 7.824 | 276 | 35.2761
16.7 | 15.747 | 1 | 7.824 | 276 | 35.2761
16.1 | 15.0977 | 1 | 7.824 | 276 | 35.2761
16.7 | 15.6235 | 1 | 7.824 | 276 | 35.2761
15.8 | 15.233 | 1 | 7.824 | 276 | 35.2761
15.7 | 14.8274 | 1 | 7.824 | 276 | 35.2761
15.9 | 15.1463 | 1 | 7.824 | 276 | 35.2761
15.7 | 15.1342 | 1 | 7.824 | 276 | 35.2761
14.6 | 14.3522 | 1 | 7.824 | 276 | 35.2761
14.7 | 14.2677 | 1 | 7.824 | 276 | 35.2761
14.5 | 14.1916 | 1 | 7.824 | 276 | 35.2761
14.7 | 14.1464 | 1 | 7.824 | 276 | 35.2761
14.7 | 14.0257 | 1 | 7.824 | 276 | 35.2761
14.6 | 13.5127 | 1 | 7.824 | 276 | 35.2761
14.4 | 13.2022 | 1 | 7.824 | 276 | 35.2761
14.8 | 13.4752 | 1 | 7.824 | 276 | 35.2761
15.2 | 13.4599 | 1 | 7.824 | 276 | 35.2761
15.6 | 13.3926 | 1 | 7.824 | 276 | 35.2761
15.9 | 13.5103 | 1 | 7.824 | 276 | 35.2761
17.1 | 14.2518 | 1 | 7.824 | 276 | 35.2761
17 | 14.0487 | 1 | 7.824 | 276 | 35.2761
18.1 | 14.4143 | 1 | 7.824 | 276 | 35.2761
18.8 | 14.5722 | 1 | 7.824 | 276 | 35.2761
19.4 | 14.9567 | 1 | 7.824 | 276 | 35.2761
19.3 | 14.7602 | 1 | 7.824 | 276 | 35.2761
19.3 | 14.7602 | 1 | 7.824 | 276 | 35.2761
19.3 | 14.7602 | 1 | 7.824 | 276 | 35.2761
19 | 14.542 | 1 | 7.824 | 276 | 35.2761
19 | 14.5964 | 1 | 7.824 | 276 | 35.2761
18.5 | 15.3964 | 1 | 7.824 | 276 | 35.2761
17.4 | 13.9337 | 1 | 7.824 | 276 | 35.2761
16 | 13.8889 | 1 | 7.824 | 276 | 35.2761
16.2 | 13.9662 | 1 | 7.824 | 276 | 35.2761
15.6 | 14.0786 | 1 | 7.824 | 276 | 35.2761
15.9 | 14.136 | 1 | 7.824 | 276 | 35.2761
15.1 | 13.9442 | 1 | 7.824 | 276 | 35.2761
15 | 13.7883 | 1 | 7.824 | 276 | 35.2761
14.8 | 13.6519 | 1 | 7.824 | 276 | 35.2761
15.7 | 14.1753 | 1 | 7.824 | 276 | 35.2761
17.1 | 14.9378 | 1 | 7.824 | 276 | 35.2761
18.9 | 15.888 | 1 | 7.824 | 276 | 35.2761
19.3 | 15.9746 | 1 | 7.824 | 276 | 35.2761
20 | 16.1686 | 1 | 7.824 | 276 | 35.2761
20.5 | 16.2331 | 1 | 7.824 | 276 | 35.2761
22.6 | 16.026 | 1 | 7.824 | 276 | 35.2761
23.6 | 16.6325 | 1 | 7.824 | 276 | 35.2761
23.7 | 16.8214 | 1 | 7.824 | 276 | 35.2761
23.4 | 16.6135 | 1 | 7.824 | 276 | 35.2761
23.8 | 15.6305 | 1 | 7.824 | 276 | 35.2761
23.1 | 15.7544 | 1 | 7.824 | 276 | 35.2761
22.1 | 15.1467 | 1 | 7.824 | 276 | 35.2761
21.3 | 14.8982 | 1 | 7.824 | 276 | 35.2761
19.6 | 14.4588 | 1 | 7.824 | 276 | 35.2761
18.1 | 14.0429 | 1 | 7.824 | 276 | 35.2761
16.8 | 13.3262 | 1 | 7.824 | 276 | 35.2761
15.5 | 12.8623 | 1 | 7.824 | 276 | 35.2761
15 | 12.8246 | 1 | 7.824 | 276 | 35.2761
14.2 | 12.5571 | 1 | 7.824 | 276 | 35.2761
14 | 12.5312 | 1 | 7.824 | 276 | 35.2761
13.8 | 12.3381 | 1 | 7.824 | 276 | 35.2761
13.4 | 12.2307 | 1 | 7.824 | 276 | 35.2761
13.6 | 12.5382 | 1 | 7.824 | 276 | 35.2761
14.9 | 13.3999 | 1 | 7.824 | 276 | 35.2761
16.5 | 14.305 | 1 | 7.824 | 276 | 35.2761
18.3 | 15.0382 | 1 | 7.824 | 276 | 35.2761
19.4 | 15.1159 | 1 | 7.824 | 276 | 35.2761
17.7 | 15.6851 | 1 | 7.824 | 276 | 35.2761
20.6 | 15.9861 | 1 | 7.824 | 276 | 35.2761
22.2 | 15.6204 | 1 | 7.824 | 276 | 35.2761
22 | 15.3488 | 1 | 7.824 | 276 | 35.2761
22.6 | 15.5678 | 1 | 7.824 | 276 | 35.2761
15.9 | 14.6022 | 1 | 7.824 | 276 | 35.2761
19.2 | 15.9903 | 1 | 7.824 | 276 | 35.2761
19.1 | 16.0703 | 1 | 7.824 | 276 | 35.2761
18.8 | 15.9046 | 1 | 7.824 | 276 | 35.2761
17.3 | 15.7204 | 1 | 7.824 | 276 | 35.2761
17 | 15.4904 | 1 | 7.824 | 276 | 35.2761
16.7 | 15.1997 | 1 | 7.824 | 276 | 35.2761
16.3 | 14.9916 | 1 | 7.824 | 276 | 35.2761
15.6 | 14.4297 | 1 | 7.824 | 276 | 35.2761
15.5 | 14.2139 | 1 | 7.824 | 276 | 35.2761
15.5 | 13.9796 | 1 | 7.824 | 276 | 35.2761
15.4 | 13.9994 | 1 | 7.824 | 276 | 35.2761
15.2 | 13.9218 | 1 | 7.824 | 276 | 35.2761
15.3 | 14.019 | 1 | 7.824 | 276 | 35.2761
15 | 13.8446 | 1 | 7.824 | 276 | 35.2761
15.6 | 14.1927 | 1 | 7.824 | 276 | 35.2761
16.4 | 14.555 | 1 | 7.824 | 276 | 35.2761
17.1 | 14.6454 | 1 | 7.824 | 276 | 35.2761
18.1 | 14.4657 | 1 | 7.824 | 276 | 35.2761
17.2 | 14.9129 | 1 | 7.824 | 276 | 35.2761
15.5 | 14.3323 | 1 | 7.824 | 276 | 35.2761
16.6 | 14.9243 | 1 | 7.824 | 276 | 35.2761
18.5 | 15.5083 | 1 | 7.824 | 276 | 35.2761
16.4 | 13.7606 | 1 | 7.824 | 276 | 35.2761
19 | 14.9134 | 1 | 7.824 | 276 | 35.2761
16.9 | 14.4569 | 1 | 7.824 | 276 | 35.2761
16.5 | 14.7696 | 1 | 7.824 | 276 | 35.2761
16.7 | 15.2604 | 1 | 7.824 | 276 | 35.2761
16.2 | 15.3198 | 1 | 7.824 | 276 | 35.2761
15.9 | 14.9644 | 1 | 7.824 | 276 | 35.2761
15.1 | 14.0027 | 1 | 7.824 | 276 | 35.2761
14.9 | 13.808 | 1 | 7.824 | 276 | 35.2761
14.6 | 13.6912 | 1 | 7.824 | 276 | 35.2761
15 | 13.906 | 1 | 7.824 | 276 | 35.2761
14.8 | 13.7108 | 1 | 7.824 | 276 | 35.2761
14.7 | 13.6722 | 1 | 7.824 | 276 | 35.2761
14.7 | 13.7309 | 1 | 7.824 | 276 | 35.2761
14.9 | 14.0456 | 1 | 7.824 | 276 | 35.2761
15.2 | 14.043 | 1 | 7.824 | 276 | 35.2761
15.2 | 13.8099 | 1 | 7.824 | 276 | 35.2761
15.3 | 13.4497 | 1 | 7.824 | 276 | 35.2761
15.9 | 13.8541 | 1 | 7.824 | 276 | 35.2761
16.9 | 14.0752 | 1 | 7.824 | 276 | 35.2761
17.7 | 13.9004 | 1 | 7.824 | 276 | 35.2761
19.4 | 14.4001 | 1 | 7.824 | 276 | 35.2761
19.3 | 14.5154 | 1 | 7.824 | 276 | 35.2761
19.4 | 14.6567 | 1 | 7.824 | 276 | 35.2761
20.7 | 15.0935 | 1 | 7.824 | 276 | 35.2761
20.9 | 15.067 | 1 | 7.824 | 276 | 35.2761
22.1 | 15.5085 | 1 | 7.824 | 276 | 35.2761
21.5 | 15.2378 | 1 | 7.824 | 276 | 35.2761
21.6 | 15.127 | 1 | 7.824 | 276 | 35.2761
20 | 14.5779 | 1 | 7.824 | 276 | 35.2761
18.7 | 14.3906 | 1 | 7.824 | 276 | 35.2761
17.6 | 14.0753 | 1 | 7.824 | 276 | 35.2761
16.9 | 13.7496 | 1 | 7.824 | 276 | 35.2761
16.4 | 13.5535 | 1 | 7.824 | 276 | 35.2761
15.4 | 13.3229 | 1 | 7.824 | 276 | 35.2761
14.3 | 12.8832 | 1 | 7.824 | 276 | 35.2761
13.6 | 12.4863 | 1 | 7.824 | 276 | 35.2761
13.4 | 12.2916 | 1 | 7.824 | 276 | 35.2761
12.6 | 11.8475 | 1 | 7.824 | 276 | 35.2761
12.6 | 11.8475 | 1 | 7.824 | 276 | 35.2761
13.1 | 11.9995 | 1 | 7.824 | 276 | 35.2761
13.9 | 12.6091 | 1 | 7.824 | 276 | 35.2761
15.4 | 13.5477 | 1 | 7.824 | 276 | 35.2761
17.5 | 13.7204 | 1 | 7.824 | 276 | 35.2761
18 | 13.5569 | 1 | 7.824 | 276 | 35.2761
18.9 | 13.9091 | 1 | 7.824 | 276 | 35.2761
19.5 | 14.4928 | 1 | 7.824 | 276 | 35.2761
21 | 15.1065 | 1 | 7.824 | 276 | 35.2761
21.9 | 15.5393 | 1 | 7.824 | 276 | 35.2761
22.8 | 16.014 | 1 | 7.824 | 276 | 35.2761
23.2 | 15.6229 | 1 | 7.824 | 276 | 35.2761
24.1 | 16.1873 | 1 | 7.824 | 276 | 35.2761
23.9 | 16.1156 | 1 | 7.824 | 276 | 35.2761
23.1 | 16.2219 | 1 | 7.824 | 276 | 35.2761
21.7 | 16.0268 | 1 | 7.824 | 276 | 35.2761
20.6 | 15.7342 | 1 | 7.824 | 276 | 35.2761
20 | 15.6231 | 1 | 7.824 | 276 | 35.2761
18.7 | 15.822 | 1 | 7.824 | 276 | 35.2761
17.2 | 15.272 | 1 | 7.824 | 276 | 35.2761
16 | 14.8841 | 1 | 7.824 | 276 | 35.2761
17.2 | 15.5693 | 1 | 7.824 | 276 | 35.2761
17.5 | 15.7388 | 1 | 7.824 | 276 | 35.2761
17.7 | 15.6331 | 1 | 7.824 | 276 | 35.2761
17.7 | 15.3399 | 1 | 7.824 | 276 | 35.2761
17.5 | 15.5606 | 1 | 7.824 | 276 | 35.2761
18.1 | 15.9572 | 1 | 7.824 | 276 | 35.2761
19 | 16.3987 | 1 | 7.824 | 276 | 35.2761
20.3 | 17.0921 | 1 | 7.824 | 276 | 35.2761
21.7 | 17.7486 | 1 | 7.824 | 276 | 35.2761
22.5 | 18.1933 | 1 | 7.824 | 276 | 35.2761
21.9 | 17.8748 | 1 | 7.824 | 276 | 35.2761
23 | 18.1277 | 1 | 7.824 | 276 | 35.2761
22.7 | 18.2014 | 1 | 7.824 | 276 | 35.2761
23.5 | 18.6408 | 1 | 7.824 | 276 | 35.2761
24.2 | 18.0215 | 1 | 7.824 | 276 | 35.2761
23.8 | 17.7773 | 1 | 7.824 | 276 | 35.2761
22.5 | 17.4459 | 1 | 7.824 | 276 | 35.2761
22.4 | 17.2442 | 1 | 7.824 | 276 | 35.2761
21.3 | 16.9187 | 1 | 7.824 | 276 | 35.2761
20.2 | 16.7643 | 1 | 7.824 | 276 | 35.2761
19.6 | 16.4361 | 1 | 7.824 | 276 | 35.2761
19.1 | 16.3753 | 1 | 7.824 | 276 | 35.2761
18.5 | 16.2807 | 1 | 7.824 | 276 | 35.2761
17.8 | 16.0891 | 1 | 7.824 | 276 | 35.2761
18.3 | 16.3891 | 1 | 7.824 | 276 | 35.2761
18.1 | 16.3787 | 1 | 7.824 | 276 | 35.2761
17.8 | 16.2716 | 1 | 7.824 | 276 | 35.2761
17.8 | 16.3944 | 1 | 7.824 | 276 | 35.2761
17.5 | 16.2874 | 1 | 7.824 | 276 | 35.2761
18.7 | 16.8351 | 1 | 7.824 | 276 | 35.2761
19.4 | 16.9581 | 1 | 7.824 | 276 | 35.2761
20.3 | 17.3899 | 1 | 7.824 | 276 | 35.2761
21.9 | 17.6996 | 1 | 7.824 | 276 | 35.2761
21.2 | 17.5198 | 1 | 7.824 | 276 | 35.2761
21.6 | 17.4222 | 1 | 7.824 | 276 | 35.2761
21.9 | 17.4674 | 1 | 7.824 | 276 | 35.2761
22 | 17.6164 | 1 | 7.824 | 276 | 35.2761
22.2 | 17.7983 | 1 | 7.824 | 276 | 35.2761
21.8 | 17.1457 | 1 | 7.824 | 276 | 35.2761
22.3 | 17.3179 | 1 | 7.824 | 276 | 35.2761
22 | 17.5 | 1 | 7.824 | 276 | 35.2761
21.4 | 17.0654 | 1 | 7.824 | 276 | 35.2761
20.3 | 16.8551 | 1 | 7.824 | 276 | 35.2761
19.8 | 16.3316 | 1 | 7.824 | 276 | 35.2761
19 | 16.0452 | 1 | 7.824 | 276 | 35.2761
18.1 | 16.0153 | 1 | 7.824 | 276 | 35.2761
17.6 | 15.8346 | 1 | 7.824 | 276 | 35.2761
17.1 | 15.9574 | 1 | 7.824 | 276 | 35.2761
17 | 15.8597 | 1 | 7.824 | 276 | 35.2761
16.5 | 15.4934 | 1 | 7.824 | 276 | 35.2761
16.3 | 15.5431 | 1 | 7.824 | 276 | 35.2761
16.5 | 15.678 | 1 | 7.824 | 276 | 35.2761
17.2 | 15.9934 | 1 | 7.824 | 276 | 35.2761
18.1 | 16.6226 | 1 | 7.824 | 276 | 35.2761
19.2 | 16.9465 | 1 | 7.824 | 276 | 35.2761
19.7 | 17.3022 | 1 | 7.824 | 276 | 35.2761
19.2 | 17.5647 | 1 | 7.824 | 276 | 35.2761
20 | 18.0857 | 1 | 7.824 | 276 | 35.2761
20.8 | 18.0416 | 1 | 7.824 | 276 | 35.2761
22.2 | 17.5651 | 1 | 7.824 | 276 | 35.2761
22.4 | 17.1834 | 1 | 7.824 | 276 | 35.2761
21.8 | 16.7542 | 1 | 7.824 | 276 | 35.2761
21.5 | 17.097 | 1 | 7.824 | 276 | 35.2761
21.7 | 17.0531 | 1 | 7.824 | 276 | 35.2761
21.9 | 16.7874 | 1 | 7.824 | 276 | 35.2761
21.1 | 16.4509 | 1 | 7.824 | 276 | 35.2761
20 | 16.6882 | 1 | 7.824 | 276 | 35.2761
19.6 | 16.964 | 1 | 7.824 | 276 | 35.2761
18.3 | 17.0664 | 1 | 7.824 | 276 | 35.2761
17.7 | 16.6683 | 1 | 7.824 | 276 | 35.2761
17 | 16.2319 | 1 | 7.824 | 276 | 35.2761
16.6 | 15.5297 | 1 | 7.824 | 276 | 35.2761
16.1 | 15.1622 | 1 | 7.824 | 276 | 35.2761
15.4 | 14.7785 | 1 | 7.824 | 276 | 35.2761
15 | 14.4445 | 1 | 7.824 | 276 | 35.2761
14.7 | 14.1481 | 1 | 7.824 | 276 | 35.2761
15.3 | 14.619 | 1 | 7.824 | 276 | 35.2761
15.1 | 14.7885 | 1 | 7.824 | 276 | 35.2761
15.5 | 15.0618 | 1 | 7.824 | 276 | 35.2761
16.8 | 15.4203 | 1 | 7.824 | 276 | 35.2761
18.1 | 16.2539 | 1 | 7.824 | 276 | 35.2761
19.9 | 17.0074 | 1 | 7.824 | 276 | 35.2761
21.8 | 17.3111 | 1 | 7.824 | 276 | 35.2761
21.9 | 17.3438 | 1 | 7.824 | 276 | 35.2761
22.2 | 17.2207 | 1 | 7.824 | 276 | 35.2761
22.8 | 17.5359 | 1 | 7.824 | 276 | 35.2761
22.9 | 17.2927 | 1 | 7.824 | 276 | 35.2761
21.9 | 16.8907 | 1 | 7.824 | 276 | 35.2761
21.1 | 16.6113 | 1 | 7.824 | 276 | 35.2761
20.4 | 16.1402 | 1 | 7.824 | 276 | 35.2761
19.4 | 16.0654 | 1 | 7.824 | 276 | 35.2761
18.6 | 15.7196 | 1 | 7.824 | 276 | 35.2761
18.4 | 15.5891 | 1 | 7.824 | 276 | 35.2761
18.1 | 15.364 | 1 | 7.824 | 276 | 35.2761
17.1 | 15.1115 | 1 | 7.824 | 276 | 35.2761
17.2 | 15.3849 | 1 | 7.824 | 276 | 35.2761
17.3 | 15.7215 | 1 | 7.824 | 276 | 35.2761
17.4 | 15.8177 | 1 | 7.824 | 276 | 35.2761
17.3 | 15.9035 | 1 | 7.824 | 276 | 35.2761
17.3 | 15.9648 | 1 | 7.824 | 276 | 35.2761
17.6 | 16.0119 | 1 | 7.824 | 276 | 35.2761
18 | 16.0342 | 1 | 7.824 | 276 | 35.2761
18.5 | 16.2728 | 1 | 7.824 | 276 | 35.2761
19.2 | 16.5214 | 1 | 7.824 | 276 | 35.2761
20 | 16.6263 | 1 | 7.824 | 276 | 35.2761
20.2 | 16.4073 | 1 | 7.824 | 276 | 35.2761
21.2 | 16.9286 | 1 | 7.824 | 276 | 35.2761
22.6 | 16.6465 | 1 | 7.824 | 276 | 35.2761
23.8 | 17.2217 | 1 | 7.824 | 276 | 35.2761
24 | 16.8743 | 1 | 7.824 | 276 | 35.2761
25 | 17.019 | 1 | 7.824 | 276 | 35.2761
24.7 | 16.9151 | 1 | 7.824 | 276 | 35.2761
23.4 | 16.7686 | 1 | 7.824 | 276 | 35.2761
21.6 | 16.2938 | 1 | 7.824 | 276 | 35.2761
19.8 | 16.1512 | 1 | 7.824 | 276 | 35.2761
19.1 | 15.6734 | 1 | 7.824 | 276 | 35.2761
18.3 | 15.3811 | 1 | 7.824 | 276 | 35.2761
17.4 | 15.0487 | 1 | 7.824 | 276 | 35.2761
16.4 | 14.6746 | 1 | 7.824 | 276 | 35.2761
15.8 | 14.3887 | 1 | 7.824 | 276 | 35.2761
15.4 | 14.177 | 1 | 7.824 | 276 | 35.2761
15.3 | 14.0205 | 1 | 7.824 | 276 | 35.2761
15.8 | 14.2708 | 1 | 7.824 | 276 | 35.2761
16.4 | 14.2115 | 1 | 7.824 | 276 | 35.2761
17 | 14.5544 | 1 | 7.824 | 276 | 35.2761
17.3 | 14.896 | 1 | 7.824 | 276 | 35.2761
18.4 | 14.9677 | 1 | 7.824 | 276 | 35.2761
19.2 | 14.9925 | 1 | 7.824 | 276 | 35.2761
19.5 | 14.6819 | 1 | 7.824 | 276 | 35.2761
20.8 | 15.3708 | 1 | 7.824 | 276 | 35.2761
21.6 | 15.5605 | 1 | 7.824 | 276 | 35.2761
22.3 | 15.8651 | 1 | 7.824 | 276 | 35.2761
23.7 | 16.4626 | 1 | 7.824 | 276 | 35.2761
24.2 | 16.0066 | 1 | 7.824 | 276 | 35.2761
24.7 | 16.1352 | 1 | 7.824 | 276 | 35.2761
24.3 | 15.9922 | 1 | 7.824 | 276 | 35.2761
23.9 | 15.9436 | 1 | 7.824 | 276 | 35.2761
23.3 | 15.6794 | 1 | 7.824 | 276 | 35.2761
22.5 | 15.8316 | 1 | 7.824 | 276 | 35.2761
21.1 | 16.2756 | 1 | 7.824 | 276 | 35.2761
19.4 | 15.7219 | 1 | 7.824 | 276 | 35.2761
17.6 | 14.8917 | 1 | 7.824 | 276 | 35.2761
17.1 | 14.6464 | 1 | 7.824 | 276 | 35.2761
15.9 | 13.9608 | 1 | 7.824 | 276 | 35.2761
15.5 | 13.6917 | 1 | 7.824 | 276 | 35.2761
14 | 12.8136 | 1 | 7.824 | 276 | 35.2761
14 | 12.8136 | 1 | 7.824 | 276 | 35.2761
13.6 | 12.5382 | 1 | 7.824 | 276 | 35.2761
15.3 | 13.9025 | 1 | 7.824 | 276 | 35.2761
16.5 | 14.2489 | 1 | 7.824 | 276 | 35.2761
18.1 | 14.6858 | 1 | 7.824 | 276 | 35.2761
20.3 | 15.2353 | 1 | 7.824 | 276 | 35.2761
21.7 | 15.7462 | 1 | 7.824 | 276 | 35.2761
23.2 | 16.1326 | 1 | 7.824 | 276 | 35.2761
23.9 | 16.3316 | 1 | 7.824 | 276 | 35.2761
25 | 17.161 | 1 | 7.824 | 276 | 35.2761
26.5 | 17.3776 | 1 | 7.824 | 276 | 35.2761
26.7 | 17.4455 | 1 | 7.824 | 276 | 35.2761
26.7 | 17.3975 | 1 | 7.824 | 276 | 35.2761
26.5 | 18.073 | 1 | 7.824 | 276 | 35.2761
25.1 | 17.4496 | 1 | 7.824 | 276 | 35.2761
23.2 | 17.3346 | 1 | 7.824 | 276 | 35.2761
21.5 | 16.9163 | 1 | 7.824 | 276 | 35.2761
19.9 | 16.1842 | 1 | 7.824 | 276 | 35.2761
18.7 | 15.929 | 1 | 7.824 | 276 | 35.2761
17.8 | 15.3688 | 1 | 7.824 | 276 | 35.2761
17 | 14.8981 | 1 | 7.824 | 276 | 35.2761
16.5 | 14.8877 | 1 | 7.824 | 276 | 35.2761
15.9 | 14.6032 | 1 | 7.824 | 276 | 35.2761
15.6 | 14.4898 | 1 | 7.824 | 276 | 35.2761
15.2 | 14.338 | 1 | 7.824 | 276 | 35.2761
15.5 | 14.6324 | 1 | 7.824 | 276 | 35.2761
16.3 | 14.9921 | 1 | 7.824 | 276 | 35.2761
17 | 15.4307 | 1 | 7.824 | 276 | 35.2761
17.5 | 15.7331 | 1 | 7.824 | 276 | 35.2761
19.5 | 16.2742 | 1 | 7.824 | 276 | 35.2761
20.4 | 16.7651 | 1 | 7.824 | 276 | 35.2761
21.1 | 17.1237 | 1 | 7.824 | 276 | 35.2761
22.1 | 17.466 | 1 | 7.824 | 276 | 35.2761
23.4 | 17.8466 | 1 | 7.824 | 276 | 35.2761
23.2 | 17.7235 | 1 | 7.824 | 276 | 35.2761
22.4 | 17.2282 | 1 | 7.824 | 276 | 35.2761
20.5 | 17.1498 | 1 | 7.824 | 276 | 35.2761
20.1 | 16.4279 | 1 | 7.824 | 276 | 35.2761
19.1 | 17.2762 | 1 | 7.824 | 276 | 35.2761
18.8 | 17.0487 | 1 | 7.824 | 276 | 35.2761
19.1 | 17.1521 | 1 | 7.824 | 276 | 35.2761
18.8 | 16.6799 | 1 | 7.824 | 276 | 35.2761
18.3 | 16.9381 | 1 | 7.824 | 276 | 35.2761
18.1 | 17.0581 | 1 | 7.824 | 276 | 35.2761
18.1 | 17.5074 | 1 | 7.824 | 276 | 35.2761
18.5 | 17.8377 | 1 | 7.824 | 276 | 35.2761
18.7 | 17.6461 | 1 | 7.824 | 276 | 35.2761
18.3 | 16.5044 | 1 | 7.824 | 276 | 35.2761
18.1 | 16.4338 | 1 | 7.824 | 276 | 35.2761
18 | 16.5218 | 1 | 7.824 | 276 | 35.2761
18.6 | 17.0419 | 1 | 7.824 | 276 | 35.2761
19.2 | 17.3727 | 1 | 7.824 | 276 | 35.2761
20 | 18.0187 | 1 | 7.824 | 276 | 35.2761
20.1 | 18.2417 | 1 | 7.824 | 276 | 35.2761
21 | 18.3499 | 1 | 7.824 | 276 | 35.2761
21.4 | 18.4812 | 1 | 7.824 | 276 | 35.2761
22.2 | 18.0204 | 1 | 7.824 | 276 | 35.2761
22.7 | 17.8962 | 1 | 7.824 | 276 | 35.2761
21.6 | 17.7618 | 1 | 7.824 | 276 | 35.2761
21.4 | 17.5175 | 1 | 7.824 | 276 | 35.2761
21.4 | 17.6932 | 1 | 7.824 | 276 | 35.2761
21.8 | 17.5353 | 1 | 7.824 | 276 | 35.2761
21.1 | 17.4745 | 1 | 7.824 | 276 | 35.2761
19.9 | 16.825 | 1 | 7.824 | 276 | 35.2761
19.2 | 16.9418 | 1 | 7.824 | 276 | 35.2761
18.4 | 16.5409 | 1 | 7.824 | 276 | 35.2761
18 | 16.7093 | 1 | 7.824 | 276 | 35.2761
17.5 | 16.3465 | 1 | 7.824 | 276 | 35.2761
16.7 | 15.3221 | 1 | 7.824 | 276 | 35.2761
16.1 | 14.8589 | 1 | 7.824 | 276 | 35.2761
15.8 | 14.7464 | 1 | 7.824 | 276 | 35.2761
16 | 14.882 | 1 | 7.824 | 276 | 35.2761
15.7 | 14.47 | 1 | 7.824 | 276 | 35.2761
15.2 | 13.9834 | 1 | 7.824 | 276 | 35.2761
15 | 13.7887 | 1 | 7.824 | 276 | 35.2761
14.8 | 13.5946 | 1 | 7.824 | 276 | 35.2761
17.5 | 14.4111 | 1 | 7.824 | 276 | 35.2761
18.9 | 14.2527 | 1 | 7.824 | 276 | 35.2761
20.2 | 14.1059 | 1 | 7.824 | 276 | 35.2761
21.2 | 13.9351 | 1 | 7.824 | 276 | 35.2761
20.8 | 13.5566 | 1 | 7.824 | 276 | 35.2761
22.3 | 14.7609 | 1 | 7.824 | 276 | 35.2761
23.8 | 14.6638 | 1 | 7.824 | 276 | 35.2761
23.3 | 14.3027 | 1 | 7.824 | 276 | 35.2761
21.9 | 14.6538 | 1 | 7.824 | 276 | 35.2761
20.8 | 14.0955 | 1 | 7.824 | 276 | 35.2761
20.1 | 14.3032 | 1 | 7.824 | 276 | 35.2761
19.3 | 15.0297 | 1 | 7.824 | 276 | 35.2761
18.5 | 14.678 | 1 | 7.824 | 276 | 35.2761
17.8 | 14.4117 | 1 | 7.824 | 276 | 35.2761
17 | 14.6114 | 1 | 7.824 | 276 | 35.2761
16.8 | 14.7078 | 1 | 7.824 | 276 | 35.2761
16.7 | 14.9039 | 1 | 7.824 | 276 | 35.2761
16.7 | 15.2003 | 1 | 7.824 | 276 | 35.2761
17.2 | 15.4439 | 1 | 7.824 | 276 | 35.2761
15.8 | 14.6851 | 1 | 7.824 | 276 | 35.2761
15.4 | 14.2353 | 1 | 7.824 | 276 | 35.2761
15.1 | 14.061 | 1 | 7.824 | 276 | 35.2761
14.9 | 13.748 | 1 | 7.824 | 276 | 35.2761
16.4 | 14.2106 | 1 | 7.824 | 276 | 35.2761
17.6 | 14.7783 | 1 | 7.824 | 276 | 35.2761
18.8 | 14.7862 | 1 | 7.824 | 276 | 35.2761
19.8 | 14.8427 | 1 | 7.824 | 276 | 35.2761
20.4 | 14.4106 | 1 | 7.824 | 276 | 35.2761
21.2 | 14.6641 | 1 | 7.824 | 276 | 35.2761
22.1 | 15.5865 | 1 | 7.824 | 276 | 35.2761
21.3 | 15.3425 | 1 | 7.824 | 276 | 35.2761
23 | 15.3297 | 1 | 7.824 | 276 | 35.2761
23 | 15.7591 | 1 | 7.824 | 276 | 35.2761
21.9 | 15.0167 | 1 | 7.824 | 276 | 35.2761
20.8 | 15.0524 | 1 | 7.824 | 276 | 35.2761
19.7 | 15.0612 | 1 | 7.824 | 276 | 35.2761
18.8 | 14.8343 | 1 | 7.824 | 276 | 35.2761
17.7 | 14.8114 | 1 | 7.824 | 276 | 35.2761
16.6 | 14.5707 | 1 | 7.824 | 276 | 35.2761
16.1 | 14.3818 | 1 | 7.824 | 276 | 35.2761
15.6 | 14.1916 | 1 | 7.824 | 276 | 35.2761
15.4 | 14.233 | 1 | 7.824 | 276 | 35.2761
15.6 | 14.6683 | 1 | 7.824 | 276 | 35.2761
15.2 | 14.4568 | 1 | 7.824 | 276 | 35.2761
15.4 | 14.4719 | 1 | 7.824 | 276 | 35.2761
15.1 | 13.9402 | 1 | 7.824 | 276 | 35.2761
15.4 | 13.7074 | 1 | 7.824 | 276 | 35.2761
16 | 13.4903 | 1 | 7.824 | 276 | 35.2761
16 | 13.2178 | 1 | 7.824 | 276 | 35.2761
18 | 13.48 | 1 | 7.824 | 276 | 35.2761
19.3 | 13.3102 | 1 | 7.824 | 276 | 35.2761
20.2 | 13.8021 | 1 | 7.824 | 276 | 35.2761
19.6 | 13.1517 | 1 | 7.824 | 276 | 35.2761
21.8 | 13.411 | 1 | 7.824 | 276 | 35.2761
22.4 | 13.7279 | 1 | 7.824 | 276 | 35.2761
20.8 | 14.08 | 1 | 7.824 | 276 | 35.2761
16 | 14.0558 | 1 | 7.824 | 276 | 35.2761
17.4 | 14.2545 | 1 | 7.824 | 276 | 35.2761
17.5 | 13.9133 | 1 | 7.824 | 276 | 35.2761
17 | 13.8278 | 1 | 7.824 | 276 | 35.2761
16.9 | 14.0643 | 1 | 7.824 | 276 | 35.2761
16.7 | 14.0988 | 1 | 7.824 | 276 | 35.2761
15.8 | 13.8644 | 1 | 7.824 | 276 | 35.2761
15.4 | 13.7668 | 1 | 7.824 | 276 | 35.2761
15.2 | 13.8633 | 1 | 7.824 | 276 | 35.2761
14.8 | 13.4752 | 1 | 7.824 | 276 | 35.2761
14.3 | 13.5133 | 1 | 7.824 | 276 | 35.2761
13.9 | 13.297 | 1 | 7.824 | 276 | 35.2761
13.8 | 13.2576 | 1 | 7.824 | 276 | 35.2761
13.8 | 13.1392 | 1 | 7.824 | 276 | 35.2761
14.1 | 13.3755 | 1 | 7.824 | 276 | 35.2761
15.3 | 14.0778 | 1 | 7.824 | 276 | 35.2761
15.5 | 14.4511 | 1 | 7.824 | 276 | 35.2761
15.3 | 14.5561 | 1 | 7.824 | 276 | 35.2761
16.9 | 15.5742 | 1 | 7.824 | 276 | 35.2761
18.1 | 15.651 | 1 | 7.824 | 276 | 35.2761
18.4 | 15.4697 | 1 | 7.824 | 276 | 35.2761
19.7 | 15.0081 | 1 | 7.824 | 276 | 35.2761
19.4 | 14.6856 | 1 | 7.824 | 276 | 35.2761
19.5 | 14.6709 | 1 | 7.824 | 276 | 35.2761
19.7 | 13.939 | 1 | 7.824 | 276 | 35.2761
19.4 | 14.6316 | 1 | 7.824 | 276 | 35.2761
18.8 | 14.6694 | 1 | 7.824 | 276 | 35.2761
18.5 | 14.6664 | 1 | 7.824 | 276 | 35.2761
17.9 | 14.9413 | 1 | 7.824 | 276 | 35.2761
16.9 | 15.0923 | 1 | 7.824 | 276 | 35.2761
16.2 | 14.8924 | 1 | 7.824 | 276 | 35.2761
15.5 | 14.6914 | 1 | 7.824 | 276 | 35.2761
15.3 | 14.6772 | 1 | 7.824 | 276 | 35.2761
15.1 | 14.5409 | 1 | 7.824 | 276 | 35.2761
14.2 | 13.8326 | 1 | 7.824 | 276 | 35.2761
15.1 | 14.4799 | 1 | 7.824 | 276 | 35.2761
14.8 | 14.3663 | 1 | 7.824 | 276 | 35.2761
15.5 | 14.813 | 1 | 7.824 | 276 | 35.2761
16.2 | 15.1945 | 1 | 7.824 | 276 | 35.2761
16.9 | 15.5727 | 1 | 7.824 | 276 | 35.2761
17.3 | 15.4765 | 1 | 7.824 | 276 | 35.2761
17.5 | 14.8484 | 1 | 7.824 | 276 | 35.2761
19.3 | 14.9112 | 1 | 7.824 | 276 | 35.2761
20.7 | 14.0834 | 1 | 7.824 | 276 | 35.2761
21.8 | 13.9157 | 1 | 7.824 | 276 | 35.2761
22.3 | 13.9384 | 1 | 7.824 | 276 | 35.2761
22.2 | 13.8572 | 1 | 7.824 | 276 | 35.2761
22.6 | 14.0962 | 1 | 7.824 | 276 | 35.2761
21.4 | 13.5039 | 1 | 7.824 | 276 | 35.2761
21.1 | 13.3008 | 1 | 7.824 | 276 | 35.2761
20.9 | 13.0978 | 1 | 7.824 | 276 | 35.2761
19.6 | 12.6637 | 1 | 7.824 | 276 | 35.2761
18.3 | 12.7253 | 1 | 7.824 | 276 | 35.2761
18.1 | 12.3676 | 1 | 7.824 | 276 | 35.2761
17.1 | 11.9139 | 1 | 7.824 | 276 | 35.2761
16.1 | 11.9747 | 1 | 7.824 | 276 | 35.2761
15.1 | 11.9105 | 1 | 7.824 | 276 | 35.2761
14.8 | 11.889 | 1 | 7.824 | 276 | 35.2761
13.4 | 11.4095 | 1 | 7.824 | 276 | 35.2761
13 | 11.1876 | 1 | 7.824 | 276 | 35.2761
12.5 | 11.0286 | 1 | 7.824 | 276 | 35.2761
12.9 | 11.1985 | 1 | 7.824 | 276 | 35.2761
13.1 | 11.0717 | 1 | 7.824 | 276 | 35.2761
14.4 | 11.5184 | 1 | 7.824 | 276 | 35.2761
16.2 | 12.5656 | 1 | 7.824 | 276 | 35.2761
18.4 | 13.1975 | 1 | 7.824 | 276 | 35.2761
19.8 | 13.2334 | 1 | 7.824 | 276 | 35.2761
20.6 | 13.2387 | 1 | 7.824 | 276 | 35.2761
20.8 | 13.6257 | 1 | 7.824 | 276 | 35.2761
20.8 | 13.7155 | 1 | 7.824 | 276 | 35.2761
21.1 | 13.4758 | 1 | 7.824 | 276 | 35.2761
21 | 13.5707 | 1 | 7.824 | 276 | 35.2761
20.8 | 13.4896 | 1 | 7.824 | 276 | 35.2761
21.2 | 13.7782 | 1 | 7.824 | 276 | 35.2761
20.8 | 13.4896 | 1 | 7.824 | 276 | 35.2761
19.6 | 13.1517 | 1 | 7.824 | 276 | 35.2761
18.6 | 13.0355 | 1 | 7.824 | 276 | 35.2761
17.1 | 12.7757 | 1 | 7.824 | 276 | 35.2761
15.9 | 12.5455 | 1 | 7.824 | 276 | 35.2761
14.9 | 12.6189 | 1 | 7.824 | 276 | 35.2761
13.5 | 11.9921 | 1 | 7.824 | 276 | 35.2761
13 | 11.6746 | 1 | 7.824 | 276 | 35.2761
12.3 | 11.2709 | 1 | 7.824 | 276 | 35.2761
11.9 | 10.5569 | 1 | 7.824 | 276 | 35.2761
10.4 | 9.5782 | 1 | 7.824 | 276 | 35.2761
10.8 | 9.8626 | 1 | 7.824 | 276 | 35.2761
10.8 | 9.6514 | 1 | 7.824 | 276 | 35.2761
12.7 | 10.6412 | 1 | 7.824 | 276 | 35.2761
14.6 | 11.6022 | 1 | 7.824 | 276 | 35.2761
16.5 | 12.5857 | 1 | 7.824 | 276 | 35.2761
18.4 | 12.4489 | 1 | 7.824 | 276 | 35.2761
19.3 | 12.9469 | 1 | 7.824 | 276 | 35.2761
20.7 | 12.4921 | 1 | 7.824 | 276 | 35.2761
21.7 | 12.7396 | 1 | 7.824 | 276 | 35.2761
18.7 | 12.0878 | 1 | 7.824 | 276 | 35.2761
19.3 | 12.5481 | 1 | 7.824 | 276 | 35.2761
20.5 | 12.6943 | 1 | 7.824 | 276 | 35.2761
19.3 | 12.1653 | 1 | 7.824 | 276 | 35.2761
19.4 | 11.8796 | 1 | 7.824 | 276 | 35.2761
18.2 | 11.9706 | 1 | 7.824 | 276 | 35.2761
16.6 | 11.3044 | 1 | 7.824 | 276 | 35.2761
15.6 | 11.6748 | 1 | 7.824 | 276 | 35.2761
14.6 | 11.7079 | 1 | 7.824 | 276 | 35.2761
13.3 | 11.3178 | 1 | 7.824 | 276 | 35.2761
12.9 | 11.2548 | 1 | 7.824 | 276 | 35.2761
12.3 | 11.0536 | 1 | 7.824 | 276 | 35.2761
12.1 | 11.0231 | 1 | 7.824 | 276 | 35.2761
11.9 | 10.9375 | 1 | 7.824 | 276 | 35.2761
11.4 | 10.7777 | 1 | 7.824 | 276 | 35.2761
11.2 | 10.4166 | 1 | 7.824 | 276 | 35.2761
11.9 | 10.9379 | 1 | 7.824 | 276 | 35.2761
13.7 | 12.1886 | 1 | 7.824 | 276 | 35.2761
16.1 | 13.3202 | 1 | 7.824 | 276 | 35.2761
17.5 | 13.8698 | 1 | 7.824 | 276 | 35.2761
19.9 | 13.6093 | 1 | 7.824 | 276 | 35.2761
20.2 | 13.4547 | 1 | 7.824 | 276 | 35.2761
20.2 | 13.6368 | 1 | 7.824 | 276 | 35.2761
21 | 14.0365 | 1 | 7.824 | 276 | 35.2761
22.5 | 14.2992 | 1 | 7.824 | 276 | 35.2761
21.4 | 13.9203 | 1 | 7.824 | 276 | 35.2761
21.2 | 13.7984 | 1 | 7.824 | 276 | 35.2761
20.9 | 13.6371 | 1 | 7.824 | 276 | 35.2761
20.8 | 13.4658 | 1 | 7.824 | 276 | 35.2761
19.2 | 13.5258 | 1 | 7.824 | 276 | 35.2761
17.8 | 13.419 | 1 | 7.824 | 276 | 35.2761
16.6 | 13.1489 | 1 | 7.824 | 276 | 35.2761
15.9 | 12.9747 | 1 | 7.824 | 276 | 35.2761
16.5 | 12.699 | 1 | 7.824 | 276 | 35.2761
15.7 | 13.1104 | 1 | 7.824 | 276 | 35.2761
15.1 | 13.1456 | 1 | 7.824 | 276 | 35.2761
14.4 | 12.9216 | 1 | 7.824 | 276 | 35.2761
14.1 | 12.4649 | 1 | 7.824 | 276 | 35.2761
13.5 | 11.9983 | 1 | 7.824 | 276 | 35.2761
13.4 | 12.0672 | 1 | 7.824 | 276 | 35.2761
13.9 | 12.6075 | 1 | 7.824 | 276 | 35.2761
15.5 | 13.5848 | 1 | 7.824 | 276 | 35.2761
17.5 | 14.471 | 1 | 7.824 | 276 | 35.2761
19 | 14.3495 | 1 | 7.824 | 276 | 35.2761
21 | 14.5171 | 1 | 7.824 | 276 | 35.2761
21.7 | 14.2739 | 1 | 7.824 | 276 | 35.2761
22.3 | 14.1052 | 1 | 7.824 | 276 | 35.2761
23.2 | 14.6215 | 1 | 7.824 | 276 | 35.2761
22.8 | 14.2122 | 1 | 7.824 | 276 | 35.2761
23.1 | 14.6706 | 1 | 7.824 | 276 | 35.2761
22.5 | 14.3991 | 1 | 7.824 | 276 | 35.2761
21.6 | 14.0981 | 1 | 7.824 | 276 | 35.2761
20.3 | 13.8218 | 1 | 7.824 | 276 | 35.2761
18.9 | 13.2715 | 1 | 7.824 | 276 | 35.2761
17.9 | 13.165 | 1 | 7.824 | 276 | 35.2761
17.1 | 13.1973 | 1 | 7.824 | 276 | 35.2761
16.4 | 13.4983 | 1 | 7.824 | 276 | 35.2761
15.7 | 13.4408 | 1 | 7.824 | 276 | 35.2761
15.1 | 13.2029 | 1 | 7.824 | 276 | 35.2761
14.4 | 12.9228 | 1 | 7.824 | 276 | 35.2761
13.9 | 12.7211 | 1 | 7.824 | 276 | 35.2761
13.5 | 12.6155 | 1 | 7.824 | 276 | 35.2761
13.1 | 12.2811 | 1 | 7.824 | 276 | 35.2761
12.8 | 12.0433 | 1 | 7.824 | 276 | 35.2761
13 | 12.1263 | 1 | 7.824 | 276 | 35.2761
14.8 | 13.5386 | 1 | 7.824 | 276 | 35.2761
17.3 | 15.0175 | 1 | 7.824 | 276 | 35.2761
19.7 | 15.8442 | 1 | 7.824 | 276 | 35.2761
22.1 | 16.3277 | 1 | 7.824 | 276 | 35.2761
23.4 | 16.3791 | 1 | 7.824 | 276 | 35.2761
24.7 | 15.9809 | 1 | 7.824 | 276 | 35.2761
25.2 | 15.3264 | 1 | 7.824 | 276 | 35.2761
26.3 | 15.6881 | 1 | 7.824 | 276 | 35.2761
26.6 | 15.5546 | 1 | 7.824 | 276 | 35.2761
27 | 15.8567 | 1 | 7.824 | 276 | 35.2761
26.2 | 15.6892 | 1 | 7.824 | 276 | 35.2761
25.1 | 15.2439 | 1 | 7.824 | 276 | 35.2761
23.4 | 15.8336 | 1 | 7.824 | 276 | 35.2761
21 | 15.1524 | 1 | 7.824 | 276 | 35.2761
19.8 | 14.4999 | 1 | 7.824 | 276 | 35.2761
19.7 | 14.2123 | 1 | 7.824 | 276 | 35.2761
18.5 | 14.2079 | 1 | 7.824 | 276 | 35.2761
17.6 | 13.5991 | 1 | 7.824 | 276 | 35.2761
17 | 13.4672 | 1 | 7.824 | 276 | 35.2761
16.6 | 13.9028 | 1 | 7.824 | 276 | 35.2761
15.7 | 13.3837 | 1 | 7.824 | 276 | 35.2761
15.3 | 12.8961 | 1 | 7.824 | 276 | 35.2761
15.1 | 13.0901 | 1 | 7.824 | 276 | 35.2761
15.7 | 13.6624 | 1 | 7.824 | 276 | 35.2761
17.5 | 13.9791 | 1 | 7.824 | 276 | 35.2761
19.3 | 13.3782 | 1 | 7.824 | 276 | 35.2761
21.8 | 14.6242 | 1 | 7.824 | 276 | 35.2761
23.2 | 15.4258 | 1 | 7.824 | 276 | 35.2761
24.6 | 15.5263 | 1 | 7.824 | 276 | 35.2761
25.1 | 16.7677 | 1 | 7.824 | 276 | 35.2761
25.3 | 16.041 | 1 | 7.824 | 276 | 35.2761
25.2 | 16.187 | 1 | 7.824 | 276 | 35.2761
24.6 | 15.0829 | 1 | 7.824 | 276 | 35.2761
24 | 13.8842 | 1 | 7.824 | 276 | 35.2761
22.3 | 15.0772 | 1 | 7.824 | 276 | 35.2761
20.5 | 15.9535 | 1 | 7.824 | 276 | 35.2761
19.6 | 16.1345 | 1 | 7.824 | 276 | 35.2761
19.1 | 16.4248 | 1 | 7.824 | 276 | 35.2761
19 | 16.6281 | 1 | 7.824 | 276 | 35.2761
19.3 | 16.8527 | 1 | 7.824 | 276 | 35.2761
18.7 | 17.0124 | 1 | 7.824 | 276 | 35.2761
18.8 | 16.9842 | 1 | 7.824 | 276 | 35.2761
18.6 | 16.6063 | 1 | 7.824 | 276 | 35.2761
18.6 | 16.424 | 1 | 7.824 | 276 | 35.2761
19.5 | 16.1515 | 1 | 7.824 | 276 | 35.2761
19.7 | 16.2213 | 1 | 7.824 | 276 | 35.2761
19.5 | 16.2081 | 1 | 7.824 | 276 | 35.2761
20.3 | 17.1946 | 1 | 7.824 | 276 | 35.2761
19.6 | 17.1961 | 1 | 7.824 | 276 | 35.2761
19.3 | 17.1548 | 1 | 7.824 | 276 | 35.2761
19.7 | 16.9282 | 1 | 7.824 | 276 | 35.2761
18.3 | 16.6249 | 1 | 7.824 | 276 | 35.2761
17.9 | 16.5463 | 1 | 7.824 | 276 | 35.2761
17.7 | 16.4137 | 1 | 7.824 | 276 | 35.2761
18 | 16.8949 | 1 | 7.824 | 276 | 35.2761
18.5 | 17.1304 | 1 | 7.824 | 276 | 35.2761
18.5 | 17.5125 | 1 | 7.824 | 276 | 35.2761
18.3 | 16.9981 | 1 | 7.824 | 276 | 35.2761
18.6 | 17.5463 | 1 | 7.824 | 276 | 35.2761
18.9 | 17.5836 | 1 | 7.824 | 276 | 35.2761
18.5 | 17.3843 | 1 | 7.824 | 276 | 35.2761
18 | 17.2137 | 1 | 7.824 | 276 | 35.2761
17.8 | 17.0809 | 1 | 7.824 | 276 | 35.2761
17.2 | 16.553 | 1 | 7.824 | 276 | 35.2761
16.1 | 15.1587 | 1 | 7.824 | 276 | 35.2761
15 | 14.1404 | 1 | 7.824 | 276 | 35.2761
14.1 | 13.3755 | 1 | 7.824 | 276 | 35.2761
13.7 | 13.1586 | 1 | 7.824 | 276 | 35.2761
14 | 13.3361 | 1 | 7.824 | 276 | 35.2761
14.1 | 13.494 | 1 | 7.824 | 276 | 35.2761
13.6 | 13.1191 | 1 | 7.824 | 276 | 35.2761
13.9 | 13.297 | 1 | 7.824 | 276 | 35.2761
14.4 | 13.6712 | 1 | 7.824 | 276 | 35.2761
14.9 | 13.8652 | 1 | 7.824 | 276 | 35.2761
15.6 | 14.4297 | 1 | 7.824 | 276 | 35.2761
16.2 | 14.598 | 1 | 7.824 | 276 | 35.2761
17.3 | 14.9519 | 1 | 7.824 | 276 | 35.2761
19.6 | 15.573 | 1 | 7.824 | 276 | 35.2761
20.8 | 14.96 | 1 | 7.824 | 276 | 35.2761
21.2 | 13.9661 | 1 | 7.824 | 276 | 35.2761
20.1 | 13.5849 | 1 | 7.824 | 276 | 35.2761
16.5 | 14.7703 | 1 | 7.824 | 276 | 35.2761
17.8 | 15.196 | 1 | 7.824 | 276 | 35.2761
17.5 | 14.5732 | 1 | 7.824 | 276 | 35.2761
16.9 | 14.1219 | 1 | 7.824 | 276 | 35.2761
16.6 | 14.2888 | 1 | 7.824 | 276 | 35.2761
16.3 | 13.6696 | 1 | 7.824 | 276 | 35.2761
15.6 | 13.3397 | 1 | 7.824 | 276 | 35.2761
14.8 | 12.5812 | 1 | 7.824 | 276 | 35.2761
14.1 | 12.629 | 1 | 7.824 | 276 | 35.2761
13.8 | 12.2844 | 1 | 7.824 | 276 | 35.2761
13 | 11.8428 | 1 | 7.824 | 276 | 35.2761
13.2 | 12.0372 | 1 | 7.824 | 276 | 35.2761
12 | 11.2003 | 1 | 7.824 | 276 | 35.2761
12.1 | 11.1322 | 1 | 7.824 | 276 | 35.2761
12.6 | 11.399 | 1 | 7.824 | 276 | 35.2761
13 | 11.5678 | 1 | 7.824 | 276 | 35.2761
15 | 12.7172 | 1 | 7.824 | 276 | 35.2761
16.8 | 13.5944 | 1 | 7.824 | 276 | 35.2761
17.5 | 13.0939 | 1 | 7.824 | 276 | 35.2761
16.5 | 13.97 | 1 | 7.824 | 276 | 35.2761
17.1 | 14.2562 | 1 | 7.824 | 276 | 35.2761
18.5 | 14.8946 | 1 | 7.824 | 276 | 35.2761
19.2 | 14.5687 | 1 | 7.824 | 276 | 35.2761
18.6 | 14.6602 | 1 | 7.824 | 276 | 35.2761
19.4 | 14.3867 | 1 | 7.824 | 276 | 35.2761
19 | 13.732 | 1 | 7.824 | 276 | 35.2761
18.6 | 13.7252 | 1 | 7.824 | 276 | 35.2761
17.8 | 13.114 | 1 | 7.824 | 276 | 35.2761
17 | 12.7441 | 1 | 7.824 | 276 | 35.2761
15.9 | 12.3479 | 1 | 7.824 | 276 | 35.2761
15.5 | 12.1345 | 1 | 7.824 | 276 | 35.2761
14.1 | 12.1344 | 1 | 7.824 | 276 | 35.2761
13 | 11.1393 | 1 | 7.824 | 276 | 35.2761
12.5 | 11.1399 | 1 | 7.824 | 276 | 35.2761
11.9 | 10.7208 | 1 | 7.824 | 276 | 35.2761
11.8 | 10.8403 | 1 | 7.824 | 276 | 35.2761
11.4 | 10.5584 | 1 | 7.824 | 276 | 35.2761
10.9 | 10.3955 | 1 | 7.824 | 276 | 35.2761
11.3 | 10.5699 | 1 | 7.824 | 276 | 35.2761
11.8 | 10.8954 | 1 | 7.824 | 276 | 35.2761
13.8 | 12.3969 | 1 | 7.824 | 276 | 35.2761
16.3 | 13.4544 | 1 | 7.824 | 276 | 35.2761
17.7 | 13.7895 | 1 | 7.824 | 276 | 35.2761
18.5 | 13.7421 | 1 | 7.824 | 276 | 35.2761
19.4 | 13.7964 | 1 | 7.824 | 276 | 35.2761
19.8 | 13.8556 | 1 | 7.824 | 276 | 35.2761
20 | 13.8382 | 1 | 7.824 | 276 | 35.2761
20.1 | 13.4606 | 1 | 7.824 | 276 | 35.2761
20.8 | 12.8309 | 1 | 7.824 | 276 | 35.2761
21.4 | 13.5714 | 1 | 7.824 | 276 | 35.2761
20.5 | 13.525 | 1 | 7.824 | 276 | 35.2761
19.4 | 13.3686 | 1 | 7.824 | 276 | 35.2761
18.4 | 13.1617 | 1 | 7.824 | 276 | 35.2761
17.3 | 12.7698 | 1 | 7.824 | 276 | 35.2761
16.2 | 12.3728 | 1 | 7.824 | 276 | 35.2761
15.1 | 12.0217 | 1 | 7.824 | 276 | 35.2761
14.6 | 12.0747 | 1 | 7.824 | 276 | 35.2761
14.4 | 12.8641 | 1 | 7.824 | 276 | 35.2761
13.8 | 12.5654 | 1 | 7.824 | 276 | 35.2761
13.5 | 12.2741 | 1 | 7.824 | 276 | 35.2761
13.1 | 11.9972 | 1 | 7.824 | 276 | 35.2761
13.5 | 11.8325 | 1 | 7.824 | 276 | 35.2761
13 | 11.1929 | 1 | 7.824 | 276 | 35.2761
13.9 | 11.8375 | 1 | 7.824 | 276 | 35.2761
15.1 | 12.1245 | 1 | 7.824 | 276 | 35.2761
17.3 | 12.87 | 1 | 7.824 | 276 | 35.2761
18.7 | 12.4986 | 1 | 7.824 | 276 | 35.2761
19.7 | 13.2572 | 1 | 7.824 | 276 | 35.2761
20.2 | 13.1848 | 1 | 7.824 | 276 | 35.2761
21.2 | 13.4074 | 1 | 7.824 | 276 | 35.2761
21.1 | 12.7866 | 1 | 7.824 | 276 | 35.2761
21.7 | 13.1067 | 1 | 7.824 | 276 | 35.2761
20.9 | 12.9913 | 1 | 7.824 | 276 | 35.2761
21 | 12.6633 | 1 | 7.824 | 276 | 35.2761
19.7 | 13.6199 | 1 | 7.824 | 276 | 35.2761
17.5 | 13.1942 | 1 | 7.824 | 276 | 35.2761
16.1 | 12.787 | 1 | 7.824 | 276 | 35.2761
15.2 | 12.5286 | 1 | 7.824 | 276 | 35.2761
14.5 | 12.3508 | 1 | 7.824 | 276 | 35.2761
13.2 | 11.651 | 1 | 7.824 | 276 | 35.2761
12.9 | 11.58 | 1 | 7.824 | 276 | 35.2761
12.9 | 11.58 | 1 | 7.824 | 276 | 35.2761
12.1 | 11.187 | 1 | 7.824 | 276 | 35.2761
11.4 | 10.6668 | 1 | 7.824 | 276 | 35.2761
10.9 | 10.2847 | 1 | 7.824 | 276 | 35.2761
11 | 10.3284 | 1 | 7.824 | 276 | 35.2761
11.4 | 10.7213 | 1 | 7.824 | 276 | 35.2761
12.5 | 11.6332 | 1 | 7.824 | 276 | 35.2761
15 | 12.8769 | 1 | 7.824 | 276 | 35.2761
16 | 13.1122 | 1 | 7.824 | 276 | 35.2761
17.9 | 13.647 | 1 | 7.824 | 276 | 35.2761
19.3 | 13.9862 | 1 | 7.824 | 276 | 35.2761
20 | 13.7693 | 1 | 7.824 | 276 | 35.2761
21.3 | 14.1272 | 1 | 7.824 | 276 | 35.2761
21.4 | 13.2472 | 1 | 7.824 | 276 | 35.2761
21.3 | 13.7196 | 1 | 7.824 | 276 | 35.2761
20.2 | 14.126 | 1 | 7.824 | 276 | 35.2761
19 | 14.2159 | 1 | 7.824 | 276 | 35.2761
18.7 | 14.0482 | 1 | 7.824 | 276 | 35.2761
17.5 | 14.562 | 1 | 7.824 | 276 | 35.2761
17 | 14.4872 | 1 | 7.824 | 276 | 35.2761
16.6 | 13.9955 | 1 | 7.824 | 276 | 35.2761
15.1 | 13.6457 | 1 | 7.824 | 276 | 35.2761
14.7 | 13.6069 | 1 | 7.824 | 276 | 35.2761
14.7 | 13.5482 | 1 | 7.824 | 276 | 35.2761
14.8 | 14.3042 | 1 | 7.824 | 276 | 35.2761
15.1 | 14.7864 | 1 | 7.824 | 276 | 35.2761
14.7 | 14.0831 | 1 | 7.824 | 276 | 35.2761
14.6 | 13.6251 | 1 | 7.824 | 276 | 35.2761
14.7 | 14.0218 | 1 | 7.824 | 276 | 35.2761
15.3 | 14.4295 | 1 | 7.824 | 276 | 35.2761
15.2 | 14.5134 | 1 | 7.824 | 276 | 35.2761
15 | 14.3158 | 1 | 7.824 | 276 | 35.2761
14.8 | 14.6115 | 1 | 7.824 | 276 | 35.2761
15.5 | 14.9319 | 1 | 7.824 | 276 | 35.2761
16.3 | 15.2849 | 1 | 7.824 | 276 | 35.2761
16.5 | 15.2952 | 1 | 7.824 | 276 | 35.2761
16.3 | 15.0997 | 1 | 7.824 | 276 | 35.2761
17.4 | 15.9864 | 1 | 7.824 | 276 | 35.2761
18 | 14.0662 | 1 | 7.824 | 276 | 35.2761
17.6 | 13.6475 | 1 | 7.824 | 276 | 35.2761
17 | 12.7915 | 1 | 7.824 | 276 | 35.2761
16.3 | 12.5652 | 1 | 7.824 | 276 | 35.2761
15.5 | 12.7227 | 1 | 7.824 | 276 | 35.2761
15.2 | 12.7675 | 1 | 7.824 | 276 | 35.2761
14.4 | 12.3942 | 1 | 7.824 | 276 | 35.2761
13.7 | 12.7984 | 1 | 7.824 | 276 | 35.2761
13 | 12.1129 | 1 | 7.824 | 276 | 35.2761
12.7 | 11.8191 | 1 | 7.824 | 276 | 35.2761
13.2 | 11.5215 | 1 | 7.824 | 276 | 35.2761
13.4 | 11.1745 | 1 | 7.824 | 276 | 35.2761
13.2 | 10.8809 | 1 | 7.824 | 276 | 35.2761
13 | 10.9022 | 1 | 7.824 | 276 | 35.2761
11.7 | 11.0088 | 1 | 7.824 | 276 | 35.2761
12 | 10.9123 | 1 | 7.824 | 276 | 35.2761
12.5 | 10.5867 | 1 | 7.824 | 276 | 35.2761
13.4 | 11.0734 | 1 | 7.824 | 276 | 35.2761
14.5 | 11.1781 | 1 | 7.824 | 276 | 35.2761
15.7 | 11.2921 | 1 | 7.824 | 276 | 35.2761
16.6 | 11.6186 | 1 | 7.824 | 276 | 35.2761
12.8 | 11.3603 | 1 | 7.824 | 276 | 35.2761
15.9 | 12.6779 | 1 | 7.824 | 276 | 35.2761
17 | 12.0216 | 1 | 7.824 | 276 | 35.2761
15.1 | 12.4655 | 1 | 7.824 | 276 | 35.2761
15.5 | 12.5193 | 1 | 7.824 | 276 | 35.2761
16 | 11.1459 | 1 | 7.824 | 276 | 35.2761
15.6 | 11.1634 | 1 | 7.824 | 276 | 35.2761
14.3 | 11.1025 | 1 | 7.824 | 276 | 35.2761
14.2 | 10.7656 | 1 | 7.824 | 276 | 35.2761
13 | 10.4496 | 1 | 7.824 | 276 | 35.2761
12.6 | 10.2778 | 1 | 7.824 | 276 | 35.2761
11.7 | 9.9365 | 1 | 7.824 | 276 | 35.2761
11.4 | 9.7015 | 1 | 7.824 | 276 | 35.2761
11.3 | 9.7606 | 1 | 7.824 | 276 | 35.2761
11.5 | 9.8487 | 1 | 7.824 | 276 | 35.2761
11.4 | 9.961 | 1 | 7.824 | 276 | 35.2761
11.5 | 9.9519 | 1 | 7.824 | 276 | 35.2761
11.4 | 10.0658 | 1 | 7.824 | 276 | 35.2761
11.4 | 10.0664 | 1 | 7.824 | 276 | 35.2761
12.2 | 10.7851 | 1 | 7.824 | 276 | 35.2761
13.2 | 10.9457 | 1 | 7.824 | 276 | 35.2761
14.6 | 11.1326 | 1 | 7.824 | 276 | 35.2761
16 | 11.6684 | 1 | 7.824 | 276 | 35.2761
16.6 | 11.6333 | 1 | 7.824 | 276 | 35.2761
17.2 | 12.1156 | 1 | 7.824 | 276 | 35.2761
17.8 | 12.3126 | 1 | 7.824 | 276 | 35.2761
17.5 | 12.0082 | 1 | 7.824 | 276 | 35.2761
18.3 | 12.4707 | 1 | 7.824 | 276 | 35.2761
17.6 | 12.2359 | 1 | 7.824 | 276 | 35.2761
18.2 | 12.1607 | 1 | 7.824 | 276 | 35.2761
16.5 | 10.5447 | 1 | 7.824 | 276 | 35.2761
14.8 | 10.0647 | 1 | 7.824 | 276 | 35.2761
13.6 | 9.8534 | 1 | 7.824 | 276 | 35.2761
12.5 | 9.1804 | 1 | 7.824 | 276 | 35.2761
12 | 9.3305 | 1 | 7.824 | 276 | 35.2761
11 | 8.879 | 1 | 7.824 | 276 | 35.2761
11.1 | 9.0721 | 1 | 7.824 | 276 | 35.2761
10.3 | 8.8576 | 1 | 7.824 | 276 | 35.2761
10.1 | 8.7661 | 1 | 7.824 | 276 | 35.2761
9.5 | 8.3886 | 1 | 7.824 | 276 | 35.2761
10.7 | 9.3965 | 1 | 7.824 | 276 | 35.2761
9.7 | 8.5829 | 1 | 7.824 | 276 | 35.2761
10.2 | 8.8637 | 1 | 7.824 | 276 | 35.2761
11.1 | 9.8886 | 1 | 7.824 | 276 | 35.2761
13.1 | 10.9146 | 1 | 7.824 | 276 | 35.2761
15.7 | 11.8568 | 1 | 7.824 | 276 | 35.2761
16.9 | 11.5131 | 1 | 7.824 | 276 | 35.2761
17.2 | 11.9553 | 1 | 7.824 | 276 | 35.2761
18 | 12.1059 | 1 | 7.824 | 276 | 35.2761
18.5 | 12.4895 | 1 | 7.824 | 276 | 35.2761
19.3 | 12.5048 | 1 | 7.824 | 276 | 35.2761
19 | 12.2109 | 1 | 7.824 | 276 | 35.2761
18.8 | 12.5661 | 1 | 7.824 | 276 | 35.2761
18.6 | 12.266 | 1 | 7.824 | 276 | 35.2761
17.6 | 11.8987 | 1 | 7.824 | 276 | 35.2761
16 | 11.8414 | 1 | 7.824 | 276 | 35.2761
15.1 | 12.2758 | 1 | 7.824 | 276 | 35.2761
14.1 | 12.132 | 1 | 7.824 | 276 | 35.2761
13.6 | 12.2012 | 1 | 7.824 | 276 | 35.2761
13.4 | 12.0634 | 1 | 7.824 | 276 | 35.2761
11.8 | 11.115 | 1 | 7.824 | 276 | 35.2761
12.7 | 11.9429 | 1 | 7.824 | 276 | 35.2761
13 | 12.2371 | 1 | 7.824 | 276 | 35.2761
13.4 | 12.6296 | 1 | 7.824 | 276 | 35.2761
13.9 | 12.8883 | 1 | 7.824 | 276 | 35.2761
14 | 13.0439 | 1 | 7.824 | 276 | 35.2761
13.7 | 13.2777 | 1 | 7.824 | 276 | 35.2761
14.4 | 13.9712 | 1 | 7.824 | 276 | 35.2761
14.9 | 14.4665 | 1 | 7.824 | 276 | 35.2761
16.1 | 15.4683 | 1 | 7.824 | 276 | 35.2761
16.8 | 15.4188 | 1 | 7.824 | 276 | 35.2761
19 | 15.9808 | 1 | 7.824 | 276 | 35.2761
20.2 | 14.9957 | 1 | 7.824 | 276 | 35.2761
21.1 | 15.0282 | 1 | 7.824 | 276 | 35.2761
21.3 | 14.9054 | 1 | 7.824 | 276 | 35.2761
21.7 | 15.1056 | 1 | 7.824 | 276 | 35.2761
21.5 | 14.9825 | 1 | 7.824 | 276 | 35.2761
20.3 | 14.4351 | 1 | 7.824 | 276 | 35.2761
18.4 | 13.9591 | 1 | 7.824 | 276 | 35.2761
17.2 | 13.7027 | 1 | 7.824 | 276 | 35.2761
16.6 | 13.684 | 1 | 7.824 | 276 | 35.2761
15.9 | 13.2995 | 1 | 7.824 | 276 | 35.2761
14.6 | 12.397 | 1 | 7.824 | 276 | 35.2761
14.4 | 12.2084 | 1 | 7.824 | 276 | 35.2761
12.5 | 11.089 | 1 | 7.824 | 276 | 35.2761
12.5 | 11.749 | 1 | 7.824 | 276 | 35.2761
11.7 | 10.9087 | 1 | 7.824 | 276 | 35.2761
11.2 | 10.6377 | 1 | 7.824 | 276 | 35.2761
10.7 | 10.1449 | 1 | 7.824 | 276 | 35.2761
10.1 | 9.7694 | 1 | 7.824 | 276 | 35.2761
11 | 10.4406 | 1 | 7.824 | 276 | 35.2761
11.7 | 10.9093 | 1 | 7.824 | 276 | 35.2761
13.1 | 12 | 1 | 7.824 | 276 | 35.2761
14.4 | 12.9804 | 1 | 7.824 | 276 | 35.2761
16.7 | 13.4597 | 1 | 7.824 | 276 | 35.2761
19.5 | 14.5439 | 1 | 7.824 | 276 | 35.2761
20.7 | 14.8466 | 1 | 7.824 | 276 | 35.2761
21.9 | 16.5248 | 1 | 7.824 | 276 | 35.2761
23 | 17.1793 | 1 | 7.824 | 276 | 35.2761
23.1 | 16.4266 | 1 | 7.824 | 276 | 35.2761
24 | 17.2061 | 1 | 7.824 | 276 | 35.2761
23 | 16.3402 | 1 | 7.824 | 276 | 35.2761
21.7 | 16.7261 | 1 | 7.824 | 276 | 35.2761
20.3 | 15.6803 | 1 | 7.824 | 276 | 35.2761
18.7 | 15.1464 | 1 | 7.824 | 276 | 35.2761
17.7 | 14.6612 | 1 | 7.824 | 276 | 35.2761
17 | 13.7375 | 1 | 7.824 | 276 | 35.2761
15.5 | 13.4198 | 1 | 7.824 | 276 | 35.2761
14.9 | 13.294 | 1 | 7.824 | 276 | 35.2761
14.8 | 13.2536 | 1 | 7.824 | 276 | 35.2761
14.2 | 12.9 | 1 | 7.824 | 276 | 35.2761
13.9 | 12.7221 | 1 | 7.824 | 276 | 35.2761
13.2 | 12.3229 | 1 | 7.824 | 276 | 35.2761
13.6 | 12.4867 | 1 | 7.824 | 276 | 35.2761
13.6 | 12.6002 | 1 | 7.824 | 276 | 35.2761
14.6 | 13.3453 | 1 | 7.824 | 276 | 35.2761
17.2 | 15.2741 | 1 | 7.824 | 276 | 35.2761
19.7 | 16.7076 | 1 | 7.824 | 276 | 35.2761
21.6 | 17.5422 | 1 | 7.824 | 276 | 35.2761
23.8 | 17.0351 | 1 | 7.824 | 276 | 35.2761
24.6 | 16.9571 | 1 | 7.824 | 276 | 35.2761
25.6 | 17.9594 | 1 | 7.824 | 276 | 35.2761
26 | 17.9392 | 1 | 7.824 | 276 | 35.2761
26.2 | 18.579 | 1 | 7.824 | 276 | 35.2761
25.7 | 16.9917 | 1 | 7.824 | 276 | 35.2761
24.9 | 16.3777 | 1 | 7.824 | 276 | 35.2761
23.4 | 15.7434 | 1 | 7.824 | 276 | 35.2761
21.4 | 15.5558 | 1 | 7.824 | 276 | 35.2761
19 | 15.3089 | 1 | 7.824 | 276 | 35.2761
18.3 | 15.3876 | 1 | 7.824 | 276 | 35.2761
17.4 | 15.2281 | 1 | 7.824 | 276 | 35.2761
17.3 | 15.2488 | 1 | 7.824 | 276 | 35.2761
16 | 14.4676 | 1 | 7.824 | 276 | 35.2761
16.1 | 14.2732 | 1 | 7.824 | 276 | 35.2761
16 | 14.0618 | 1 | 7.824 | 276 | 35.2761
15.2 | 13.8094 | 1 | 7.824 | 276 | 35.2761
15.8 | 13.8704 | 1 | 7.824 | 276 | 35.2761
15.4 | 13.2079 | 1 | 7.824 | 276 | 35.2761
16.2 | 13.8008 | 1 | 7.824 | 276 | 35.2761
16.4 | 13.9891 | 1 | 7.824 | 276 | 35.2761
18.9 | 15.4351 | 1 | 7.824 | 276 | 35.2761
20.1 | 15.4358 | 1 | 7.824 | 276 | 35.2761
20.7 | 15.4947 | 1 | 7.824 | 276 | 35.2761
21.7 | 15.3997 | 1 | 7.824 | 276 | 35.2761
23.6 | 16.686 | 1 | 7.824 | 276 | 35.2761
24.5 | 17.7279 | 1 | 7.824 | 276 | 35.2761
25.5 | 17.7471 | 1 | 7.824 | 276 | 35.2761
25.1 | 17.2539 | 1 | 7.824 | 276 | 35.2761
24 | 16.7723 | 1 | 7.824 | 276 | 35.2761
22.7 | 16.3151 | 1 | 7.824 | 276 | 35.2761
21.7 | 15.7505 | 1 | 7.824 | 276 | 35.2761
21.2 | 15.9901 | 1 | 7.824 | 276 | 35.2761
19.9 | 16.2439 | 1 | 7.824 | 276 | 35.2761
19.8 | 16.5549 | 1 | 7.824 | 276 | 35.2761
18.5 | 15.7995 | 1 | 7.824 | 276 | 35.2761
18.3 | 16.383 | 1 | 7.824 | 276 | 35.2761
18 | 16.2766 | 1 | 7.824 | 276 | 35.2761
16.8 | 15.7233 | 1 | 7.824 | 276 | 35.2761
16 | 14.9415 | 1 | 7.824 | 276 | 35.2761
15.3 | 14.1979 | 1 | 7.824 | 276 | 35.2761
14.6 | 13.8092 | 1 | 7.824 | 276 | 35.2761
14.1 | 13.3181 | 1 | 7.824 | 276 | 35.2761
13.8 | 12.9076 | 1 | 7.824 | 276 | 35.2761
15 | 13.5569 | 1 | 7.824 | 276 | 35.2761
16.1 | 13.9284 | 1 | 7.824 | 276 | 35.2761
17.1 | 14.481 | 1 | 7.824 | 276 | 35.2761
18.5 | 15.0088 | 1 | 7.824 | 276 | 35.2761
20.1 | 15.6532 | 1 | 7.824 | 276 | 35.2761
20.5 | 15.2163 | 1 | 7.824 | 276 | 35.2761
21.3 | 15.4595 | 1 | 7.824 | 276 | 35.2761
21.8 | 15.6423 | 1 | 7.824 | 276 | 35.2761
22.3 | 15.8262 | 1 | 7.824 | 276 | 35.2761
22.2 | 15.94 | 1 | 7.824 | 276 | 35.2761
22 | 15.5167 | 1 | 7.824 | 276 | 35.2761
20.8 | 15.3808 | 1 | 7.824 | 276 | 35.2761
19.1 | 14.8615 | 1 | 7.824 | 276 | 35.2761
17.8 | 14.4182 | 1 | 7.824 | 276 | 35.2761
16.6 | 13.793 | 1 | 7.824 | 276 | 35.2761
15.8 | 13.6463 | 1 | 7.824 | 276 | 35.2761
15 | 12.9403 | 1 | 7.824 | 276 | 35.2761
14.3 | 12.882 | 1 | 7.824 | 276 | 35.2761
13.3 | 12.0819 | 1 | 7.824 | 276 | 35.2761
12.5 | 11.6368 | 1 | 7.824 | 276 | 35.2761
11.9 | 11.1601 | 1 | 7.824 | 276 | 35.2761
11.3 | 10.736 | 1 | 7.824 | 276 | 35.2761
11 | 10.4403 | 1 | 7.824 | 276 | 35.2761
11.3 | 10.9589 | 1 | 7.824 | 276 | 35.2761
12 | 11.4261 | 1 | 7.824 | 276 | 35.2761
13.4 | 12.4041 | 1 | 7.824 | 276 | 35.2761
15.9 | 14.1408 | 1 | 7.824 | 276 | 35.2761
18.8 | 15.1259 | 1 | 7.824 | 276 | 35.2761
19.8 | 15.7143 | 1 | 7.824 | 276 | 35.2761
21.6 | 15.7828 | 1 | 7.824 | 276 | 35.2761
22.4 | 16.382 | 1 | 7.824 | 276 | 35.2761
22.9 | 16.2998 | 1 | 7.824 | 276 | 35.2761
21.8 | 15.9566 | 1 | 7.824 | 276 | 35.2761
20.6 | 16.1672 | 1 | 7.824 | 276 | 35.2761
20 | 15.676 | 1 | 7.824 | 276 | 35.2761
19.8 | 15.1703 | 1 | 7.824 | 276 | 35.2761
17.8 | 13.9904 | 1 | 7.824 | 276 | 35.2761
17.8 | 14.639 | 1 | 7.824 | 276 | 35.2761
16.6 | 14.0135 | 1 | 7.824 | 276 | 35.2761
15.8 | 13.8719 | 1 | 7.824 | 276 | 35.2761
15 | 13.5018 | 1 | 7.824 | 276 | 35.2761
14.5 | 13.1889 | 1 | 7.824 | 276 | 35.2761
13.8 | 12.7939 | 1 | 7.824 | 276 | 35.2761
13.8 | 12.7939 | 1 | 7.824 | 276 | 35.2761
13.6 | 12.428 | 1 | 7.824 | 276 | 35.2761
13 | 12.1252 | 1 | 7.824 | 276 | 35.2761
12.6 | 11.8463 | 1 | 7.824 | 276 | 35.2761
13.5 | 12.2746 | 1 | 7.824 | 276 | 35.2761
14 | 12.8169 | 1 | 7.824 | 276 | 35.2761
14.5 | 13.1883 | 1 | 7.824 | 276 | 35.2761
14.7 | 13.2683 | 1 | 7.824 | 276 | 35.2761
15.8 | 14.2743 | 1 | 7.824 | 276 | 35.2761
16.5 | 14.6573 | 1 | 7.824 | 276 | 35.2761
15.5 | 14.3952 | 1 | 7.824 | 276 | 35.2761
17.9 | 14.7866 | 1 | 7.824 | 276 | 35.2761
18.5 | 13.3992 | 1 | 7.824 | 276 | 35.2761
19.1 | 12.6636 | 1 | 7.824 | 276 | 35.2761
18.9 | 12.1495 | 1 | 7.824 | 276 | 35.2761
18.8 | 12.1508 | 1 | 7.824 | 276 | 35.2761
17.4 | 11.9238 | 1 | 7.824 | 276 | 35.2761
16 | 11.7575 | 1 | 7.824 | 276 | 35.2761
15 | 11.385 | 1 | 7.824 | 276 | 35.2761
12 | 10.1381 | 1 | 7.824 | 276 | 35.2761
10.7 | 9.0502 | 1 | 7.824 | 276 | 35.2761
9.7 | 8.489 | 1 | 7.824 | 276 | 35.2761
9.1 | 7.9093 | 1 | 7.824 | 276 | 35.2761
8.6 | 7.4743 | 1 | 7.824 | 276 | 35.2761
8.4 | 7.4266 | 1 | 7.824 | 276 | 35.2761
8.5 | 7.5238 | 1 | 7.824 | 276 | 35.2761
9.7 | 8.9477 | 1 | 7.824 | 276 | 35.2761
9.9 | 9.4622 | 1 | 7.824 | 276 | 35.2761
10.8 | 10.025 | 1 | 7.824 | 276 | 35.2761
11.5 | 10.4935 | 1 | 7.824 | 276 | 35.2761
12.6 | 11.1819 | 1 | 7.824 | 276 | 35.2761
14.2 | 11.8006 | 1 | 7.824 | 276 | 35.2761
15 | 12.028 | 1 | 7.824 | 276 | 35.2761
16 | 12.59 | 1 | 7.824 | 276 | 35.2761
16.5 | 12.2402 | 1 | 7.824 | 276 | 35.2761
16.3 | 13.0214 | 1 | 7.824 | 276 | 35.2761
16.7 | 13.1789 | 1 | 7.824 | 276 | 35.2761
16.9 | 12.5483 | 1 | 7.824 | 276 | 35.2761
17.2 | 11.2912 | 1 | 7.824 | 276 | 35.2761
17.1 | 11.1633 | 1 | 7.824 | 276 | 35.2761
15.8 | 10.5202 | 1 | 7.824 | 276 | 35.2761
14.6 | 9.9538 | 1 | 7.824 | 276 | 35.2761
14.2 | 9.7765 | 1 | 7.824 | 276 | 35.2761
13.1 | 9.5541 | 1 | 7.824 | 276 | 35.2761
12.1 | 9.1962 | 1 | 7.824 | 276 | 35.2761
10.5 | 8.2726 | 1 | 7.824 | 276 | 35.2761
9.4 | 7.9482 | 1 | 7.824 | 276 | 35.2761
9.6 | 8.2881 | 1 | 7.824 | 276 | 35.2761
10.2 | 8.6656 | 1 | 7.824 | 276 | 35.2761
10.5 | 8.8524 | 1 | 7.824 | 276 | 35.2761
10.6 | 8.9479 | 1 | 7.824 | 276 | 35.2761
10.6 | 8.8486 | 1 | 7.824 | 276 | 35.2761
10.9 | 8.7907 | 1 | 7.824 | 276 | 35.2761
11 | 8.8849 | 1 | 7.824 | 276 | 35.2761
11.5 | 9.3069 | 1 | 7.824 | 276 | 35.2761
12 | 9.7775 | 1 | 7.824 | 276 | 35.2761
13 | 10.1223 | 1 | 7.824 | 276 | 35.2761
14.1 | 10.602 | 1 | 7.824 | 276 | 35.2761
14.9 | 10.7126 | 1 | 7.824 | 276 | 35.2761
11.4 | 10.0758 | 1 | 7.824 | 276 | 35.2761
13.6 | 11.1831 | 1 | 7.824 | 276 | 35.2761
14 | 10.7046 | 1 | 7.824 | 276 | 35.2761
13.1 | 10.563 | 1 | 7.824 | 276 | 35.2761
13.6 | 10.6307 | 1 | 7.824 | 276 | 35.2761
13.8 | 10.1926 | 1 | 7.824 | 276 | 35.2761
12.1 | 9.6783 | 1 | 7.824 | 276 | 35.2761
11.1 | 9.3287 | 1 | 7.824 | 276 | 35.2761
12.1 | 9.6794 | 1 | 7.824 | 276 | 35.2761
11.9 | 9.2532 | 1 | 7.824 | 276 | 35.2761
12.1 | 9.3438 | 1 | 7.824 | 276 | 35.2761
11.7 | 9.0688 | 1 | 7.824 | 276 | 35.2761
11.5 | 8.8364 | 1 | 7.824 | 276 | 35.2761
11.1 | 8.8893 | 1 | 7.824 | 276 | 35.2761
11.3 | 9.0772 | 1 | 7.824 | 276 | 35.2761
11.3 | 9.0772 | 1 | 7.824 | 276 | 35.2761
11.2 | 8.7934 | 1 | 7.824 | 276 | 35.2761
11.6 | 8.8371 | 1 | 7.824 | 276 | 35.2761
11.6 | 9.3125 | 1 | 7.824 | 276 | 35.2761
12 | 9.5901 | 1 | 7.824 | 276 | 35.2761
12.1 | 9.7827 | 1 | 7.824 | 276 | 35.2761
12.5 | 9.8646 | 1 | 7.824 | 276 | 35.2761
12.3 | 10.1207 | 1 | 7.824 | 276 | 35.2761
13.3 | 10.5596 | 1 | 7.824 | 276 | 35.2761
14.1 | 10.7126 | 1 | 7.824 | 276 | 35.2761
14.3 | 10.5642 | 1 | 7.824 | 276 | 35.2761
13.9 | 10.1569 | 1 | 7.824 | 276 | 35.2761
13.6 | 9.9796 | 1 | 7.824 | 276 | 35.2761
13.7 | 9.9782 | 1 | 7.824 | 276 | 35.2761
13.1 | 9.8029 | 1 | 7.824 | 276 | 35.2761
12.9 | 9.7147 | 1 | 7.824 | 276 | 35.2761
12.7 | 9.7201 | 1 | 7.824 | 276 | 35.2761
12.4 | 9.7763 | 1 | 7.824 | 276 | 35.2761
12.1 | 9.5944 | 1 | 7.824 | 276 | 35.2761
11.8 | 9.4105 | 1 | 7.824 | 276 | 35.2761
11.5 | 9.4203 | 1 | 7.824 | 276 | 35.2761
11.4 | 9.4241 | 1 | 7.824 | 276 | 35.2761
10.6 | 9.2607 | 1 | 7.824 | 276 | 35.2761
10.6 | 9.06 | 1 | 7.824 | 276 | 35.2761
10.3 | 8.9722 | 1 | 7.824 | 276 | 35.2761
10.1 | 8.88 | 1 | 7.824 | 276 | 35.2761
9.8 | 8.5901 | 1 | 7.824 | 276 | 35.2761
10.7 | 9.2569 | 1 | 7.824 | 276 | 35.2761
12.2 | 10.0331 | 1 | 7.824 | 276 | 35.2761
13.6 | 10.6498 | 1 | 7.824 | 276 | 35.2761
14.5 | 10.8016 | 1 | 7.824 | 276 | 35.2761
14.9 | 10.6518 | 1 | 7.824 | 276 | 35.2761
15.5 | 10.9123 | 1 | 7.824 | 276 | 35.2761
15.5 | 11.0482 | 1 | 7.824 | 276 | 35.2761
15 | 10.7408 | 1 | 7.824 | 276 | 35.2761
15.6 | 11.1369 | 1 | 7.824 | 276 | 35.2761
14.7 | 10.8866 | 1 | 7.824 | 276 | 35.2761
14.4 | 10.8039 | 1 | 7.824 | 276 | 35.2761
14.3 | 10.8081 | 1 | 7.824 | 276 | 35.2761
14 | 10.8224 | 1 | 7.824 | 276 | 35.2761
13.1 | 10.83 | 1 | 7.824 | 276 | 35.2761
12.9 | 10.6923 | 1 | 7.824 | 276 | 35.2761
12.6 | 10.6126 | 1 | 7.824 | 276 | 35.2761
12.3 | 10.9003 | 1 | 7.824 | 276 | 35.2761
11.8 | 10.4707 | 1 | 7.824 | 276 | 35.2761
11.5 | 10.1804 | 1 | 7.824 | 276 | 35.2761
11.5 | 9.8705 | 1 | 7.824 | 276 | 35.2761
11.1 | 9.8976 | 1 | 7.824 | 276 | 35.2761
11.2 | 9.8902 | 1 | 7.824 | 276 | 35.2761
11.3 | 9.9867 | 1 | 7.824 | 276 | 35.2761
11 | 9.9054 | 1 | 7.824 | 276 | 35.2761
11.1 | 9.8976 | 1 | 7.824 | 276 | 35.2761
12 | 10.3483 | 1 | 7.824 | 276 | 35.2761
13 | 10.9388 | 1 | 7.824 | 276 | 35.2761
14.7 | 11.7642 | 1 | 7.824 | 276 | 35.2761
15.7 | 12.231 | 1 | 7.824 | 276 | 35.2761
17.4 | 12.9738 | 1 | 7.824 | 276 | 35.2761
18.5 | 13.4112 | 1 | 7.824 | 276 | 35.2761
18.5 | 13.0756 | 1 | 7.824 | 276 | 35.2761
19 | 13.0433 | 1 | 7.824 | 276 | 35.2761
19.3 | 13.6784 | 1 | 7.824 | 276 | 35.2761
19.3 | 13.6762 | 1 | 7.824 | 276 | 35.2761
18.7 | 13.5878 | 1 | 7.824 | 276 | 35.2761
18 | 13.4599 | 1 | 7.824 | 276 | 35.2761
17 | 13.4219 | 1 | 7.824 | 276 | 35.2761
16.5 | 13.1185 | 1 | 7.824 | 276 | 35.2761
16 | 13.0772 | 1 | 7.824 | 276 | 35.2761
15.3 | 13.1207 | 1 | 7.824 | 276 | 35.2761
15 | 13.0555 | 1 | 7.824 | 276 | 35.2761
15 | 13.0555 | 1 | 7.824 | 276 | 35.2761
14.8 | 12.8646 | 1 | 7.824 | 276 | 35.2761
14.3 | 12.8849 | 1 | 7.824 | 276 | 35.2761
14 | 12.7071 | 1 | 7.824 | 276 | 35.2761
13.6 | 12.4313 | 1 | 7.824 | 276 | 35.2761
13.6 | 12.3192 | 1 | 7.824 | 276 | 35.2761
14 | 12.7076 | 1 | 7.824 | 276 | 35.2761
15.6 | 13.4056 | 1 | 7.824 | 276 | 35.2761
15.7 | 13.4452 | 1 | 7.824 | 276 | 35.2761
15.6 | 13.4065 | 1 | 7.824 | 276 | 35.2761
16.1 | 13.8256 | 1 | 7.824 | 276 | 35.2761
17.3 | 13.9643 | 1 | 7.824 | 276 | 35.2761
18 | 14.2352 | 1 | 7.824 | 276 | 35.2761
18 | 14.3419 | 1 | 7.824 | 276 | 35.2761
18.4 | 14.7098 | 1 | 7.824 | 276 | 35.2761
18 | 14.5565 | 1 | 7.824 | 276 | 35.2761
17.7 | 14.3332 | 1 | 7.824 | 276 | 35.2761
17.1 | 13.9391 | 1 | 7.824 | 276 | 35.2761
16.2 | 12.8434 | 1 | 7.824 | 276 | 35.2761
15.4 | 12.5717 | 1 | 7.824 | 276 | 35.2761
14.5 | 12.3085 | 1 | 7.824 | 276 | 35.2761
14 | 11.1661 | 1 | 7.824 | 276 | 35.2761
13.6 | 11.1974 | 1 | 7.824 | 276 | 35.2761
12.9 | 10.4898 | 1 | 7.824 | 276 | 35.2761
12.6 | 10.308 | 1 | 7.824 | 276 | 35.2761
12.4 | 10.3205 | 1 | 7.824 | 276 | 35.2761
12 | 9.9931 | 1 | 7.824 | 276 | 35.2761
12.1 | 10.1383 | 1 | 7.824 | 276 | 35.2761
12.1 | 10.1374 | 1 | 7.824 | 276 | 35.2761
12.2 | 10.2323 | 1 | 7.824 | 276 | 35.2761
12.4 | 10.2207 | 1 | 7.824 | 276 | 35.2761
13 | 10.8377 | 1 | 7.824 | 276 | 35.2761
14.1 | 11.6166 | 1 | 7.824 | 276 | 35.2761
15.3 | 12.1187 | 1 | 7.824 | 276 | 35.2761
15.8 | 12.0759 | 1 | 7.824 | 276 | 35.2761
16.5 | 12.2696 | 1 | 7.824 | 276 | 35.2761
17.3 | 12.6462 | 1 | 7.824 | 276 | 35.2761
17.2 | 12.6519 | 1 | 7.824 | 276 | 35.2761
17.8 | 12.7048 | 1 | 7.824 | 276 | 35.2761
18 | 13.2181 | 1 | 7.824 | 276 | 35.2761
17.4 | 12.8303 | 1 | 7.824 | 276 | 35.2761
16.7 | 12.6939 | 1 | 7.824 | 276 | 35.2761
15.7 | 12.2352 | 1 | 7.824 | 276 | 35.2761
14.3 | 11.9096 | 1 | 7.824 | 276 | 35.2761
13.2 | 11.2352 | 1 | 7.824 | 276 | 35.2761
12.2 | 10.911 | 1 | 7.824 | 276 | 35.2761
11 | 10.0121 | 1 | 7.824 | 276 | 35.2761
10 | 9.2457 | 1 | 7.824 | 276 | 35.2761
9.9 | 9.2528 | 1 | 7.824 | 276 | 35.2761
9.3 | 8.872 | 1 | 7.824 | 276 | 35.2761
8.7 | 8.279 | 1 | 7.824 | 276 | 35.2761
8.3 | 7.9865 | 1 | 7.824 | 276 | 35.2761
7 | 6.55 | 1 | 7.824 | 276 | 35.2761
7.1 | 6.8973 | 1 | 7.824 | 276 | 35.2761
8.3 | 7.9865 | 1 | 7.824 | 276 | 35.2761
10 | 9.3513 | 1 | 7.824 | 276 | 35.2761
11.7 | 10.3758 | 1 | 7.824 | 276 | 35.2761
12.9 | 11.0557 | 1 | 7.824 | 276 | 35.2761
13.6 | 11.6172 | 1 | 7.824 | 276 | 35.2761
14.3 | 11.9106 | 1 | 7.824 | 276 | 35.2761
15.5 | 12.5637 | 1 | 7.824 | 276 | 35.2761
16.9 | 13.4414 | 1 | 7.824 | 276 | 35.2761
17.3 | 13.5983 | 1 | 7.824 | 276 | 35.2761
17 | 13.3237 | 1 | 7.824 | 276 | 35.2761
16.3 | 12.9395 | 1 | 7.824 | 276 | 35.2761
15.2 | 12.4921 | 1 | 7.824 | 276 | 35.2761
14.1 | 11.9313 | 1 | 7.824 | 276 | 35.2761
13.2 | 11.6606 | 1 | 7.824 | 276 | 35.2761
12.3 | 11.1154 | 1 | 7.824 | 276 | 35.2761
11.5 | 10.4988 | 1 | 7.824 | 276 | 35.2761
10.5 | 9.9492 | 1 | 7.824 | 276 | 35.2761
9.9 | 9.4645 | 1 | 7.824 | 276 | 35.2761
9.4 | 8.9704 | 1 | 7.824 | 276 | 35.2761
8.5 | 8.1844 | 1 | 7.824 | 276 | 35.2761
8 | 7.7917 | 1 | 7.824 | 276 | 35.2761
7.8 | 7.5928 | 1 | 7.824 | 276 | 35.2761
7.4 | 7.1952 | 1 | 7.824 | 276 | 35.2761
7.2 | 6.9964 | 1 | 7.824 | 276 | 35.2761
7.6 | 7.2923 | 1 | 7.824 | 276 | 35.2761
9.3 | 8.7665 | 1 | 7.824 | 276 | 35.2761
10.4 | 9.7432 | 1 | 7.824 | 276 | 35.2761
11.4 | 10.2943 | 1 | 7.824 | 276 | 35.2761
12.4 | 11.1028 | 1 | 7.824 | 276 | 35.2761
12.5 | 11.092 | 1 | 7.824 | 276 | 35.2761
12.8 | 11.2732 | 1 | 7.824 | 276 | 35.2761
12.9 | 11.1555 | 1 | 7.824 | 276 | 35.2761
13.3 | 11.5381 | 1 | 7.824 | 276 | 35.2761
13.2 | 11.1257 | 1 | 7.824 | 276 | 35.2761
13 | 11.4637 | 1 | 7.824 | 276 | 35.2761
12.6 | 11.403 | 1 | 7.824 | 276 | 35.2761
12.1 | 10.9179 | 1 | 7.824 | 276 | 35.2761
11.5 | 10.3886 | 1 | 7.824 | 276 | 35.2761
11.2 | 10.4187 | 1 | 7.824 | 276 | 35.2761
11 | 10.3311 | 1 | 7.824 | 276 | 35.2761
10.1 | 9.8785 | 1 | 7.824 | 276 | 35.2761
10.5 | 10.0558 | 1 | 7.824 | 276 | 35.2761
9.6 | 9.3813 | 1 | 7.824 | 276 | 35.2761
9.5 | 9.2818 | 1 | 7.824 | 276 | 35.2761
9.7 | 9.4807 | 1 | 7.824 | 276 | 35.2761
10 | 9.7788 | 1 | 7.824 | 276 | 35.2761
10.2 | 9.9776 | 1 | 7.824 | 276 | 35.2761
10.8 | 10.3518 | 1 | 7.824 | 276 | 35.2761
11.1 | 10.6483 | 1 | 7.824 | 276 | 35.2761
11.9 | 11.0477 | 1 | 7.824 | 276 | 35.2761
12.6 | 11.5096 | 1 | 7.824 | 276 | 35.2761
13.8 | 12.3951 | 1 | 7.824 | 276 | 35.2761
15.5 | 13.637 | 1 | 7.824 | 276 | 35.2761
15.5 | 13.4116 | 1 | 7.824 | 276 | 35.2761
16.5 | 13.8015 | 1 | 7.824 | 276 | 35.2761
17.5 | 13.9161 | 1 | 7.824 | 276 | 35.2761
17.2 | 14.1793 | 1 | 7.824 | 276 | 35.2761
17 | 14.3817 | 1 | 7.824 | 276 | 35.2761
16.8 | 14.3047 | 1 | 7.824 | 276 | 35.2761
16.4 | 14.0953 | 1 | 7.824 | 276 | 35.2761
15.4 | 13.6521 | 1 | 7.824 | 276 | 35.2761
15 | 13.3814 | 1 | 7.824 | 276 | 35.2761
13.6 | 12.5949 | 1 | 7.824 | 276 | 35.2761
13.8 | 12.7898 | 1 | 7.824 | 276 | 35.2761
13.5 | 12.4969 | 1 | 7.824 | 276 | 35.2761
13.6 | 12.7092 | 1 | 7.824 | 276 | 35.2761
13.5 | 12.6112 | 1 | 7.824 | 276 | 35.2761
13.2 | 12.5477 | 1 | 7.824 | 276 | 35.2761
13.1 | 12.6826 | 1 | 7.824 | 276 | 35.2761
13.1 | 12.8601 | 1 | 7.824 | 276 | 35.2761
13 | 12.7605 | 1 | 7.824 | 276 | 35.2761
13.5 | 13.0784 | 1 | 7.824 | 276 | 35.2761
13.7 | 13.0393 | 1 | 7.824 | 276 | 35.2761
14.4 | 12.9696 | 1 | 7.824 | 276 | 35.2761
14.5 | 13.0663 | 1 | 7.824 | 276 | 35.2761
16 | 13.4873 | 1 | 7.824 | 276 | 35.2761
17.9 | 14.5452 | 1 | 7.824 | 276 | 35.2761
18.5 | 12.9328 | 1 | 7.824 | 276 | 35.2761
19.1 | 11.4102 | 1 | 7.824 | 276 | 35.2761
18 | 11.6031 | 1 | 7.824 | 276 | 35.2761
17.5 | 12.0151 | 1 | 7.824 | 276 | 35.2761
16.8 | 11.8641 | 1 | 7.824 | 276 | 35.2761
15.9 | 12.4814 | 1 | 7.824 | 276 | 35.2761
15.7 | 12.4007 | 1 | 7.824 | 276 | 35.2761
14.4 | 12.6294 | 1 | 7.824 | 276 | 35.2761
13.6 | 12.7063 | 1 | 7.824 | 276 | 35.2761
12.3 | 11.4338 | 1 | 7.824 | 276 | 35.2761
11.5 | 10.596 | 1 | 7.824 | 276 | 35.2761
11 | 10.3252 | 1 | 7.824 | 276 | 35.2761
10.8 | 9.9116 | 1 | 7.824 | 276 | 35.2761
10.3 | 9.2129 | 1 | 7.824 | 276 | 35.2761
10.4 | 9.4146 | 1 | 7.824 | 276 | 35.2761
10.9 | 9.6884 | 1 | 7.824 | 276 | 35.2761
11.5 | 10.594 | 1 | 7.824 | 276 | 35.2761
12.1 | 11.0133 | 1 | 7.824 | 276 | 35.2761
11.8 | 11.1089 | 1 | 7.824 | 276 | 35.2761
12.6 | 12.2435 | 1 | 7.824 | 276 | 35.2761
14.6 | 13.3876 | 1 | 7.824 | 276 | 35.2761
14.5 | 12.8308 | 1 | 7.824 | 276 | 35.2761
16.1 | 12.9161 | 1 | 7.824 | 276 | 35.2761
16.8 | 11.2537 | 1 | 7.824 | 276 | 35.2761
15.8 | 10.1406 | 1 | 7.824 | 276 | 35.2761
15.9 | 10.2283 | 1 | 7.824 | 276 | 35.2761
16.6 | 10.288 | 1 | 7.824 | 276 | 35.2761
16.5 | 9.9702 | 1 | 7.824 | 276 | 35.2761
16 | 9.4486 | 1 | 7.824 | 276 | 35.2761
15 | 9.3534 | 1 | 7.824 | 276 | 35.2761
14 | 8.4327 | 1 | 7.824 | 276 | 35.2761
13 | 8.6587 | 1 | 7.824 | 276 | 35.2761
11.8 | 8.1479 | 1 | 7.824 | 276 | 35.2761
11.5 | 9.1546 | 1 | 7.824 | 276 | 35.2761
11.4 | 9.0609 | 1 | 7.824 | 276 | 35.2761
10.9 | 8.7848 | 1 | 7.824 | 276 | 35.2761
10.7 | 8.7909 | 1 | 7.824 | 276 | 35.2761
11.5 | 9.5996 | 1 | 7.824 | 276 | 35.2761
11.4 | 9.5047 | 1 | 7.824 | 276 | 35.2761
12.1 | 9.7651 | 1 | 7.824 | 276 | 35.2761
12.8 | 10.3708 | 1 | 7.824 | 276 | 35.2761
13.4 | 10.8824 | 1 | 7.824 | 276 | 35.2761
13.7 | 11.6346 | 1 | 7.824 | 276 | 35.2761
14.5 | 11.9661 | 1 | 7.824 | 276 | 35.2761
15 | 12.5974 | 1 | 7.824 | 276 | 35.2761
15.5 | 12.7452 | 1 | 7.824 | 276 | 35.2761
16 | 12.84 | 1 | 7.824 | 276 | 35.2761
16.1 | 13.255 | 1 | 7.824 | 276 | 35.2761
15.9 | 13.5056 | 1 | 7.824 | 276 | 35.2761
15.9 | 13.3949 | 1 | 7.824 | 276 | 35.2761
15.4 | 13.536 | 1 | 7.824 | 276 | 35.2761
14.5 | 13.298 | 1 | 7.824 | 276 | 35.2761
14.8 | 13.2438 | 1 | 7.824 | 276 | 35.2761
14.6 | 13.0508 | 1 | 7.824 | 276 | 35.2761
15 | 13.5518 | 1 | 7.824 | 276 | 35.2761
14.4 | 13.5514 | 1 | 7.824 | 276 | 35.2761
14.4 | 13.6109 | 1 | 7.824 | 276 | 35.2761
14.5 | 13.9486 | 1 | 7.824 | 276 | 35.2761
14.6 | 13.9269 | 1 | 7.824 | 276 | 35.2761
14.6 | 14.0476 | 1 | 7.824 | 276 | 35.2761
15.1 | 14.2389 | 1 | 7.824 | 276 | 35.2761
15.1 | 14.4198 | 1 | 7.824 | 276 | 35.2761
15.1 | 14.2389 | 1 | 7.824 | 276 | 35.2761
15.3 | 14.8625 | 1 | 7.824 | 276 | 35.2761
15.5 | 14.7532 | 1 | 7.824 | 276 | 35.2761
15.5 | 14.8758 | 1 | 7.824 | 276 | 35.2761
15.5 | 14.7535 | 1 | 7.824 | 276 | 35.2761
15.5 | 14.7538 | 1 | 7.824 | 276 | 35.2761
16 | 14.8206 | 1 | 7.824 | 276 | 35.2761
16.2 | 14.8953 | 1 | 7.824 | 276 | 35.2761
16.3 | 15.4183 | 1 | 7.824 | 276 | 35.2761
17.2 | 15.3856 | 1 | 7.824 | 276 | 35.2761
18.3 | 15.9044 | 1 | 7.824 | 276 | 35.2761
19.9 | 16.3584 | 1 | 7.824 | 276 | 35.2761
19.3 | 16.2613 | 1 | 7.824 | 276 | 35.2761
19.2 | 16.6998 | 1 | 7.824 | 276 | 35.2761
19.3 | 16.6152 | 1 | 7.824 | 276 | 35.2761
19.5 | 15.9313 | 1 | 7.824 | 276 | 35.2761
18.5 | 15.0049 | 1 | 7.824 | 276 | 35.2761
17.9 | 15.1765 | 1 | 7.824 | 276 | 35.2761
16.8 | 14.9419 | 1 | 7.824 | 276 | 35.2761
16.9 | 14.9206 | 1 | 7.824 | 276 | 35.2761
16.8 | 14.8248 | 1 | 7.824 | 276 | 35.2761
16.5 | 14.6538 | 1 | 7.824 | 276 | 35.2761
16.5 | 14.5375 | 1 | 7.824 | 276 | 35.2761
16.5 | 14.3075 | 1 | 7.824 | 276 | 35.2761
16.1 | 14.0394 | 1 | 7.824 | 276 | 35.2761
15.9 | 13.9623 | 1 | 7.824 | 276 | 35.2761
16 | 14.1723 | 1 | 7.824 | 276 | 35.2761
16.2 | 14.2488 | 1 | 7.824 | 276 | 35.2761
16.4 | 14.4403 | 1 | 7.824 | 276 | 35.2761
16.6 | 14.7491 | 1 | 7.824 | 276 | 35.2761
17.1 | 15.1704 | 1 | 7.824 | 276 | 35.2761
17.4 | 15.4582 | 1 | 7.824 | 276 | 35.2761
18 | 16.0945 | 1 | 7.824 | 276 | 35.2761
18.8 | 16.084 | 1 | 7.824 | 276 | 35.2761
17.1 | 15.8941 | 1 | 7.824 | 276 | 35.2761
17.4 | 15.7589 | 1 | 7.824 | 276 | 35.2761
17.7 | 15.7476 | 1 | 7.824 | 276 | 35.2761
18 | 15.1574 | 1 | 7.824 | 276 | 35.2761
17.8 | 15.1989 | 1 | 7.824 | 276 | 35.2761
16.6 | 15.9625 | 1 | 7.824 | 276 | 35.2761
16.5 | 16.0525 | 1 | 7.824 | 276 | 35.2761
16.6 | 15.9625 | 1 | 7.824 | 276 | 35.2761
16.3 | 15.5423 | 1 | 7.824 | 276 | 35.2761
16 | 15.3703 | 1 | 7.824 | 276 | 35.2761
15.8 | 14.9278 | 1 | 7.824 | 276 | 35.2761
15.7 | 15.074 | 1 | 7.824 | 276 | 35.2761
16 | 15.1238 | 1 | 7.824 | 276 | 35.2761
15.5 | 14.9378 | 1 | 7.824 | 276 | 35.2761
15.8 | 15.0496 | 1 | 7.824 | 276 | 35.2761
15.6 | 14.9749 | 1 | 7.824 | 276 | 35.2761
15.8 | 14.8059 | 1 | 7.824 | 276 | 35.2761
15.8 | 14.8059 | 1 | 7.824 | 276 | 35.2761
16 | 15.0017 | 1 | 7.824 | 276 | 35.2761
16.5 | 15.1871 | 1 | 7.824 | 276 | 35.2761
16.3 | 15.418 | 1 | 7.824 | 276 | 35.2761
16.6 | 15.7125 | 1 | 7.824 | 276 | 35.2761
17 | 15.9185 | 1 | 7.824 | 276 | 35.2761
17 | 15.7953 | 1 | 7.824 | 276 | 35.2761
17.2 | 15.99 | 1 | 7.824 | 276 | 35.2761
16.8 | 15.9082 | 1 | 7.824 | 276 | 35.2761
16.6 | 15.7115 | 1 | 7.824 | 276 | 35.2761
16.4 | 15.639 | 1 | 7.824 | 276 | 35.2761
16.4 | 15.6388 | 1 | 7.824 | 276 | 35.2761
16.3 | 15.2328 | 1 | 7.824 | 276 | 35.2761
15.8 | 14.6234 | 1 | 7.824 | 276 | 35.2761
16.3 | 14.7513 | 1 | 7.824 | 276 | 35.2761
16 | 14.8179 | 1 | 7.824 | 276 | 35.2761
16 | 14.6975 | 1 | 7.824 | 276 | 35.2761
16.1 | 14.6753 | 1 | 7.824 | 276 | 35.2761
16.3 | 14.9882 | 1 | 7.824 | 276 | 35.2761
15.7 | 15.1334 | 1 | 7.824 | 276 | 35.2761
16 | 15.2433 | 1 | 7.824 | 276 | 35.2761
16 | 15.1199 | 1 | 7.824 | 276 | 35.2761
16.1 | 15.4655 | 1 | 7.824 | 276 | 35.2761
12.1 | 11.7492 | 1 | 7.824 | 276 | 35.2761
12.3 | 11.5464 | 1 | 7.824 | 276 | 35.2761
12 | 10.8646 | 1 | 7.824 | 276 | 35.2761
12 | 11.0293 | 1 | 7.824 | 276 | 35.2761
13.3 | 11.8489 | 1 | 7.824 | 276 | 35.2761
14.3 | 12.5328 | 1 | 7.824 | 276 | 35.2761
14.7 | 12.2576 | 1 | 7.824 | 276 | 35.2761
14.3 | 11.9339 | 1 | 7.824 | 276 | 35.2761
15.3 | 12.0819 | 1 | 7.824 | 276 | 35.2761
16.7 | 11.543 | 1 | 7.824 | 276 | 35.2761
15.9 | 11.0249 | 1 | 7.824 | 276 | 35.2761
13.2 | 11.4254 | 1 | 7.824 | 276 | 35.2761
14.1 | 11.1264 | 1 | 7.824 | 276 | 35.2761
12.4 | 10.0938 | 1 | 7.824 | 276 | 35.2761
10.6 | 9.0417 | 1 | 7.824 | 276 | 35.2761
11.3 | 9.208 | 1 | 7.824 | 276 | 35.2761
10.2 | 8.6593 | 1 | 7.824 | 276 | 35.2761
10 | 8.5674 | 1 | 7.824 | 276 | 35.2761
9.5 | 8.2868 | 1 | 7.824 | 276 | 35.2761
9.1 | 8.0004 | 1 | 7.824 | 276 | 35.2761
8.7 | 7.8123 | 1 | 7.824 | 276 | 35.2761
8.4 | 7.8233 | 1 | 7.824 | 276 | 35.2761
8.6 | 7.7152 | 1 | 7.824 | 276 | 35.2761
8.2 | 7.1782 | 1 | 7.824 | 276 | 35.2761
7.7 | 6.9364 | 1 | 7.824 | 276 | 35.2761
7.8 | 7.0345 | 1 | 7.824 | 276 | 35.2761
7.6 | 6.6933 | 1 | 7.824 | 276 | 35.2761
7.8 | 7.0353 | 1 | 7.824 | 276 | 35.2761
9.2 | 8.1004 | 1 | 7.824 | 276 | 35.2761
10.9 | 9.0367 | 1 | 7.824 | 276 | 35.2761
12.5 | 9.4249 | 1 | 7.824 | 276 | 35.2761
14.2 | 10.1367 | 1 | 7.824 | 276 | 35.2761
13.8 | 9.0475 | 1 | 7.824 | 276 | 35.2761
14.7 | 9.537 | 1 | 7.824 | 276 | 35.2761
12.8 | 8.8491 | 1 | 7.824 | 276 | 35.2761
15.5 | 9.5379 | 1 | 7.824 | 276 | 35.2761
15 | 9.3915 | 1 | 7.824 | 276 | 35.2761
13.7 | 8.408 | 1 | 7.824 | 276 | 35.2761
12.8 | 8.8491 | 1 | 7.824 | 276 | 35.2761
12 | 8.7001 | 1 | 7.824 | 276 | 35.2761
11.6 | 8.5163 | 1 | 7.824 | 276 | 35.2761
9.5 | 7.2973 | 1 | 7.824 | 276 | 35.2761
9.3 | 7.6177 | 1 | 7.824 | 276 | 35.2761
7.6 | 6.5076 | 1 | 7.824 | 276 | 35.2761
6.8 | 5.9198 | 1 | 7.824 | 276 | 35.2761
6.4 | 5.624 | 1 | 7.824 | 276 | 35.2761
4.8 | 4.3328 | 1 | 7.824 | 276 | 35.2761
5.1 | 4.8613 | 1 | 7.824 | 276 | 35.2761
5 | 4.5298 | 1 | 7.824 | 276 | 35.2761
4.7 | 4.2346 | 1 | 7.824 | 276 | 35.2761
4.7 | 4.1445 | 1 | 7.824 | 276 | 35.2761
5.1 | 4.6751 | 1 | 7.824 | 276 | 35.2761
7 | 5.8839 | 1 | 7.824 | 276 | 35.2761
9.7 | 7.7213 | 1 | 7.824 | 276 | 35.2761
11.4 | 8.082 | 1 | 7.824 | 276 | 35.2761
12.8 | 8.1671 | 1 | 7.824 | 276 | 35.2761
13 | 7.9527 | 1 | 7.824 | 276 | 35.2761
13.8 | 8.4057 | 1 | 7.824 | 276 | 35.2761
14.4 | 8.3566 | 1 | 7.824 | 276 | 35.2761
14.5 | 8.5841 | 1 | 7.824 | 276 | 35.2761
13.9 | 8.1934 | 1 | 7.824 | 276 | 35.2761
13.6 | 7.9789 | 1 | 7.824 | 276 | 35.2761
12.5 | 7.7546 | 1 | 7.824 | 276 | 35.2761
11.4 | 7.2259 | 1 | 7.824 | 276 | 35.2761
10.8 | 7.5423 | 1 | 7.824 | 276 | 35.2761
10.4 | 8.0108 | 1 | 7.824 | 276 | 35.2761
10.1 | 8.29 | 1 | 7.824 | 276 | 35.2761
9.6 | 8.6989 | 1 | 7.824 | 276 | 35.2761
10.2 | 9.4934 | 1 | 7.824 | 276 | 35.2761
11 | 10.3866 | 1 | 7.824 | 276 | 35.2761
11.6 | 11.1442 | 1 | 7.824 | 276 | 35.2761
12.3 | 12.1244 | 1 | 7.824 | 276 | 35.2761
12.9 | 12.9 | 1 | 7.824 | 276 | 35.2761
12.6 | 12.6 | 1 | 7.824 | 276 | 35.2761
12.7 | 12.7 | 1 | 7.824 | 276 | 35.2761
12.7 | 12.7 | 1 | 7.824 | 276 | 35.2761
12.7 | 12.7 | 1 | 7.824 | 276 | 35.2761
12.8 | 12.8 | 1 | 7.824 | 276 | 35.2761
13.3 | 12.9419 | 1 | 7.824 | 276 | 35.2761
13.9 | 13.3585 | 1 | 7.824 | 276 | 35.2761
14 | 13.2214 | 1 | 7.824 | 276 | 35.2761
14.7 | 13.8497 | 1 | 7.824 | 276 | 35.2761
15.3 | 13.8483 | 1 | 7.824 | 276 | 35.2761
15.7 | 14.061 | 1 | 7.824 | 276 | 35.2761
15.6 | 13.9646 | 1 | 7.824 | 276 | 35.2761
15.5 | 13.8676 | 1 | 7.824 | 276 | 35.2761
15.5 | 13.8683 | 1 | 7.824 | 276 | 35.2761
15.2 | 13.8675 | 1 | 7.824 | 276 | 35.2761
15 | 13.9068 | 1 | 7.824 | 276 | 35.2761
15.2 | 13.8675 | 1 | 7.824 | 276 | 35.2761
15.1 | 13.8865 | 1 | 7.824 | 276 | 35.2761
14.5 | 13.6531 | 1 | 7.824 | 276 | 35.2761
13 | 12.4692 | 1 | 7.824 | 276 | 35.2761
12.4 | 12.1071 | 1 | 7.824 | 276 | 35.2761
13 | 12.5856 | 1 | 7.824 | 276 | 35.2761
13.9 | 12.607 | 1 | 7.824 | 276 | 35.2761
13.6 | 11.3965 | 1 | 7.824 | 276 | 35.2761
13 | 10.8294 | 1 | 7.824 | 276 | 35.2761
12.7 | 10.8564 | 1 | 7.824 | 276 | 35.2761
12.9 | 10.9425 | 1 | 7.824 | 276 | 35.2761
13 | 11.196 | 1 | 7.824 | 276 | 35.2761
14.2 | 11.1445 | 1 | 7.824 | 276 | 35.2761
15.5 | 11.5494 | 1 | 7.824 | 276 | 35.2761
16.5 | 12.4521 | 1 | 7.824 | 276 | 35.2761
17.8 | 13.0271 | 1 | 7.824 | 276 | 35.2761
17.4 | 13.1663 | 1 | 7.824 | 276 | 35.2761
18 | 13.7573 | 1 | 7.824 | 276 | 35.2761
18.6 | 13.5897 | 1 | 7.824 | 276 | 35.2761
17.9 | 13.4636 | 1 | 7.824 | 276 | 35.2761
18.1 | 13.7468 | 1 | 7.824 | 276 | 35.2761
17.4 | 13.6275 | 1 | 7.824 | 276 | 35.2761
16.8 | 13.7645 | 1 | 7.824 | 276 | 35.2761
16.4 | 13.7729 | 1 | 7.824 | 276 | 35.2761
16.1 | 13.4907 | 1 | 7.824 | 276 | 35.2761
15.7 | 13.3324 | 1 | 7.824 | 276 | 35.2761
15.5 | 13.308 | 1 | 7.824 | 276 | 35.2761
15.2 | 13.2442 | 1 | 7.824 | 276 | 35.2761
14.6 | 12.8369 | 1 | 7.824 | 276 | 35.2761
14.1 | 12.6898 | 1 | 7.824 | 276 | 35.2761
13.5 | 12.3889 | 1 | 7.824 | 276 | 35.2761
12.2 | 11.2331 | 1 | 7.824 | 276 | 35.2761
11.7 | 10.909 | 1 | 7.824 | 276 | 35.2761
11.5 | 10.8228 | 1 | 7.824 | 276 | 35.2761
11.2 | 10.5282 | 1 | 7.824 | 276 | 35.2761
12.8 | 11.8191 | 1 | 7.824 | 276 | 35.2761
14.7 | 12.8772 | 1 | 7.824 | 276 | 35.2761
16.6 | 13.4722 | 1 | 7.824 | 276 | 35.2761
17.9 | 13.8766 | 1 | 7.824 | 276 | 35.2761
18.9 | 13.8078 | 1 | 7.824 | 276 | 35.2761
19.5 | 14.0901 | 1 | 7.824 | 276 | 35.2761
19.6 | 13.9798 | 1 | 7.824 | 276 | 35.2761
19.5 | 14.088 | 1 | 7.824 | 276 | 35.2761
18.8 | 13.8165 | 1 | 7.824 | 276 | 35.2761
17.4 | 13.1646 | 1 | 7.824 | 276 | 35.2761
15.4 | 12.1001 | 1 | 7.824 | 276 | 35.2761
14.1 | 10.955 | 1 | 7.824 | 276 | 35.2761
13.3 | 10.7588 | 1 | 7.824 | 276 | 35.2761
13.3 | 10.7588 | 1 | 7.824 | 276 | 35.2761
12.7 | 10.498 | 1 | 7.824 | 276 | 35.2761
13.1 | 10.7733 | 1 | 7.824 | 276 | 35.2761
12.7 | 10.7033 | 1 | 7.824 | 276 | 35.2761
11.5 | 10.713 | 1 | 7.824 | 276 | 35.2761
11 | 10.223 | 1 | 7.824 | 276 | 35.2761
11.1 | 10.1065 | 1 | 7.824 | 276 | 35.2761
10.7 | 9.8221 | 1 | 7.824 | 276 | 35.2761
10.6 | 9.8308 | 1 | 7.824 | 276 | 35.2761
10.3 | 9.7504 | 1 | 7.824 | 276 | 35.2761
10.8 | 10.0267 | 1 | 7.824 | 276 | 35.2761
12.9 | 11.2596 | 1 | 7.824 | 276 | 35.2761
14.5 | 12.0384 | 1 | 7.824 | 276 | 35.2761
16.4 | 12.3634 | 1 | 7.824 | 276 | 35.2761
18 | 12.8663 | 1 | 7.824 | 276 | 35.2761
18.7 | 13.1469 | 1 | 7.824 | 276 | 35.2761
18.6 | 13.6371 | 1 | 7.824 | 276 | 35.2761
18.7 | 13.7737 | 1 | 7.824 | 276 | 35.2761
18.4 | 13.1659 | 1 | 7.824 | 276 | 35.2761
17.8 | 12.6391 | 1 | 7.824 | 276 | 35.2761
16.9 | 12.0823 | 1 | 7.824 | 276 | 35.2761
15 | 12.294 | 1 | 7.824 | 276 | 35.2761
13.8 | 12.2869 | 1 | 7.824 | 276 | 35.2761
14 | 12.3688 | 1 | 7.824 | 276 | 35.2761
14 | 12.3688 | 1 | 7.824 | 276 | 35.2761
13.5 | 12.3876 | 1 | 7.824 | 276 | 35.2761
13.5 | 12.7303 | 1 | 7.824 | 276 | 35.2761
13.6 | 12.4845 | 1 | 7.824 | 276 | 35.2761
13.3 | 12.3053 | 1 | 7.824 | 276 | 35.2761
12.1 | 11.4114 | 1 | 7.824 | 276 | 35.2761
12.2 | 11.7933 | 1 | 7.824 | 276 | 35.2761
11.7 | 11.3549 | 1 | 7.824 | 276 | 35.2761
11.2 | 10.9719 | 1 | 7.824 | 276 | 35.2761
11.3 | 10.9583 | 1 | 7.824 | 276 | 35.2761
11 | 10.6609 | 1 | 7.824 | 276 | 35.2761
12.6 | 11.9029 | 1 | 7.824 | 276 | 35.2761
13.2 | 12.4354 | 1 | 7.824 | 276 | 35.2761
14.1 | 13.1444 | 1 | 7.824 | 276 | 35.2761
14 | 13.3388 | 1 | 7.824 | 276 | 35.2761
14.5 | 14.0714 | 1 | 7.824 | 276 | 35.2761
15.5 | 14.5145 | 1 | 7.824 | 276 | 35.2761
16.4 | 14.8544 | 1 | 7.824 | 276 | 35.2761
17 | 15.0201 | 1 | 7.824 | 276 | 35.2761
17.1 | 15.1746 | 1 | 7.824 | 276 | 35.2761
17 | 15.3748 | 1 | 7.824 | 276 | 35.2761
16.6 | 14.4078 | 1 | 7.824 | 276 | 35.2761
16 | 13.8366 | 1 | 7.824 | 276 | 35.2761
15.5 | 13.8695 | 1 | 7.824 | 276 | 35.2761
16 | 13.9503 | 1 | 7.824 | 276 | 35.2761
15.1 | 13.772 | 1 | 7.824 | 276 | 35.2761
13.9 | 13.1238 | 1 | 7.824 | 276 | 35.2761
12.7 | 12.0591 | 1 | 7.824 | 276 | 35.2761
12.2 | 11.8514 | 1 | 7.824 | 276 | 35.2761
11.7 | 11.2427 | 1 | 7.824 | 276 | 35.2761
11.2 | 10.8599 | 1 | 7.824 | 276 | 35.2761
11.1 | 10.8169 | 1 | 7.824 | 276 | 35.2761
12.1 | 11.6953 | 1 | 7.824 | 276 | 35.2761
12.5 | 11.8627 | 1 | 7.824 | 276 | 35.2761
12.5 | 11.9197 | 1 | 7.824 | 276 | 35.2761
13 | 12.4127 | 1 | 7.824 | 276 | 35.2761
14 | 12.9343 | 1 | 7.824 | 276 | 35.2761
16.7 | 14.002 | 1 | 7.824 | 276 | 35.2761
18 | 14.4481 | 1 | 7.824 | 276 | 35.2761
19.3 | 14.4713 | 1 | 7.824 | 276 | 35.2761
20 | 14.2381 | 1 | 7.824 | 276 | 35.2761
19.4 | 14.2044 | 1 | 7.824 | 276 | 35.2761
19.5 | 14.6483 | 1 | 7.824 | 276 | 35.2761
19.1 | 14.6525 | 1 | 7.824 | 276 | 35.2761
18.2 | 14.7402 | 1 | 7.824 | 276 | 35.2761
17.8 | 14.7546 | 1 | 7.824 | 276 | 35.2761
17.3 | 14.7918 | 1 | 7.824 | 276 | 35.2761
17 | 14.7355 | 1 | 7.824 | 276 | 35.2761
16.6 | 14.8743 | 1 | 7.824 | 276 | 35.2761
16 | 14.6475 | 1 | 7.824 | 276 | 35.2761
16 | 14.6475 | 1 | 7.824 | 276 | 35.2761
14.1 | 13.1466 | 1 | 7.824 | 276 | 35.2761
13.6 | 12.9461 | 1 | 7.824 | 276 | 35.2761
13.9 | 13.3593 | 1 | 7.824 | 276 | 35.2761
13.3 | 12.7667 | 1 | 7.824 | 276 | 35.2761
13.4 | 12.8653 | 1 | 7.824 | 276 | 35.2761
12.6 | 12.1327 | 1 | 7.824 | 276 | 35.2761
12.2 | 11.8517 | 1 | 7.824 | 276 | 35.2761
13.4 | 12.8655 | 1 | 7.824 | 276 | 35.2761
14 | 13.1066 | 1 | 7.824 | 276 | 35.2761
15.4 | 13.5484 | 1 | 7.824 | 276 | 35.2761
17.2 | 13.8144 | 1 | 7.824 | 276 | 35.2761
19.3 | 14.4677 | 1 | 7.824 | 276 | 35.2761
20.7 | 15.4056 | 1 | 7.824 | 276 | 35.2761
21.6 | 15.787 | 1 | 7.824 | 276 | 35.2761
21.2 | 15.691 | 1 | 7.824 | 276 | 35.2761
21.1 | 16.0224 | 1 | 7.824 | 276 | 35.2761
21.1 | 16.0224 | 1 | 7.824 | 276 | 35.2761
19.8 | 15.6045 | 1 | 7.824 | 276 | 35.2761
19 | 15.5892 | 1 | 7.824 | 276 | 35.2761
18 | 15.3937 | 1 | 7.824 | 276 | 35.2761
18 | 15.2217 | 1 | 7.824 | 276 | 35.2761
17.1 | 14.828 | 1 | 7.824 | 276 | 35.2761
15.9 | 14.0833 | 1 | 7.824 | 276 | 35.2761
14.7 | 13.4997 | 1 | 7.824 | 276 | 35.2761
13.4 | 12.633 | 1 | 7.824 | 276 | 35.2761
14.2 | 13.1285 | 1 | 7.824 | 276 | 35.2761
13.7 | 12.928 | 1 | 7.824 | 276 | 35.2761
13.7 | 12.9277 | 1 | 7.824 | 276 | 35.2761
13.6 | 12.8294 | 1 | 7.824 | 276 | 35.2761
13.6 | 12.9456 | 1 | 7.824 | 276 | 35.2761
13.7 | 12.928 | 1 | 7.824 | 276 | 35.2761
14 | 13.0484 | 1 | 7.824 | 276 | 35.2761
14.4 | 13.4397 | 1 | 7.824 | 276 | 35.2761
15.3 | 13.9676 | 1 | 7.824 | 276 | 35.2761
16.4 | 14.4492 | 1 | 7.824 | 276 | 35.2761
17.3 | 14.7899 | 1 | 7.824 | 276 | 35.2761
19.6 | 15.6995 | 1 | 7.824 | 276 | 35.2761
20.4 | 14.1946 | 1 | 7.824 | 276 | 35.2761
20.6 | 14.3191 | 1 | 7.824 | 276 | 35.2761
20 | 14.5779 | 1 | 7.824 | 276 | 35.2761
19.3 | 14.6189 | 1 | 7.824 | 276 | 35.2761
18.4 | 14.7572 | 1 | 7.824 | 276 | 35.2761
17.1 | 14.6556 | 1 | 7.824 | 276 | 35.2761
16 | 14.1212 | 1 | 7.824 | 276 | 35.2761
15.2 | 14.0444 | 1 | 7.824 | 276 | 35.2761
13.8 | 13.2008 | 1 | 7.824 | 276 | 35.2761
13 | 12.5277 | 1 | 7.824 | 276 | 35.2761
13.5 | 12.7306 | 1 | 7.824 | 276 | 35.2761
13.7 | 12.7539 | 1 | 7.824 | 276 | 35.2761
13.4 | 12.178 | 1 | 7.824 | 276 | 35.2761
13.5 | 12.2751 | 1 | 7.824 | 276 | 35.2761
13.2 | 12.1512 | 1 | 7.824 | 276 | 35.2761
13.5 | 12.3867 | 1 | 7.824 | 276 | 35.2761
13.8 | 12.7358 | 1 | 7.824 | 276 | 35.2761
14 | 12.9309 | 1 | 7.824 | 276 | 35.2761
13.8 | 12.7358 | 1 | 7.824 | 276 | 35.2761
14.1 | 12.7999 | 1 | 7.824 | 276 | 35.2761
15.1 | 13.0331 | 1 | 7.824 | 276 | 35.2761
16.2 | 13.6888 | 1 | 7.824 | 276 | 35.2761
17.8 | 14.1977 | 1 | 7.824 | 276 | 35.2761
19.2 | 14.8353 | 1 | 7.824 | 276 | 35.2761
20.8 | 15.2715 | 1 | 7.824 | 276 | 35.2761
21.7 | 15.7527 | 1 | 7.824 | 276 | 35.2761
20.7 | 15.5964 | 1 | 7.824 | 276 | 35.2761
19.9 | 15.1439 | 1 | 7.824 | 276 | 35.2761
17.3 | 14.3858 | 1 | 7.824 | 276 | 35.2761
15.3 | 13.4446 | 1 | 7.824 | 276 | 35.2761
14.1 | 12.8552 | 1 | 7.824 | 276 | 35.2761
13.2 | 12.206 | 1 | 7.824 | 276 | 35.2761
12.6 | 11.8447 | 1 | 7.824 | 276 | 35.2761
12.3 | 11.5502 | 1 | 7.824 | 276 | 35.2761
12.3 | 11.5499 | 1 | 7.824 | 276 | 35.2761
11 | 10.5487 | 1 | 7.824 | 276 | 35.2761
12.4 | 11.9326 | 1 | 7.824 | 276 | 35.2761
12.8 | 12.2702 | 1 | 7.824 | 276 | 35.2761
13.4 | 13.0397 | 1 | 7.824 | 276 | 35.2761
13.8 | 13.3766 | 1 | 7.824 | 276 | 35.2761
13.8 | 13.3766 | 1 | 7.824 | 276 | 35.2761
14.2 | 13.5334 | 1 | 7.824 | 276 | 35.2761
14.2 | 13.4741 | 1 | 7.824 | 276 | 35.2761
14.5 | 13.7098 | 1 | 7.824 | 276 | 35.2761
15.7 | 13.9404 | 1 | 7.824 | 276 | 35.2761
16.6 | 14.2861 | 1 | 7.824 | 276 | 35.2761
17.1 | 14.7036 | 1 | 7.824 | 276 | 35.2761
17.9 | 15.0024 | 1 | 7.824 | 276 | 35.2761
18.1 | 15.1901 | 1 | 7.824 | 276 | 35.2761
18.8 | 15.8476 | 1 | 7.824 | 276 | 35.2761
18.2 | 15.0572 | 1 | 7.824 | 276 | 35.2761
16.9 | 14.9184 | 1 | 7.824 | 276 | 35.2761
16.1 | 13.9251 | 1 | 7.824 | 276 | 35.2761
15.5 | 13.0791 | 1 | 7.824 | 276 | 35.2761
15 | 12.5543 | 1 | 7.824 | 276 | 35.2761
14.2 | 12.2289 | 1 | 7.824 | 276 | 35.2761
13.9 | 11.9438 | 1 | 7.824 | 276 | 35.2761
13.5 | 11.9409 | 1 | 7.824 | 276 | 35.2761
13.1 | 11.8853 | 1 | 7.824 | 276 | 35.2761
12 | 11.0908 | 1 | 7.824 | 276 | 35.2761
11 | 10.5499 | 1 | 7.824 | 276 | 35.2761
10.1 | 9.8783 | 1 | 7.824 | 276 | 35.2761
9.5 | 9.2819 | 1 | 7.824 | 276 | 35.2761
9.5 | 9.2819 | 1 | 7.824 | 276 | 35.2761
9.6 | 9.3814 | 1 | 7.824 | 276 | 35.2761
9.4 | 9.0754 | 1 | 7.824 | 276 | 35.2761
10 | 9.455 | 1 | 7.824 | 276 | 35.2761
11 | 9.6954 | 1 | 7.824 | 276 | 35.2761
12.1 | 10.2357 | 1 | 7.824 | 276 | 35.2761
13.6 | 10.9407 | 1 | 7.824 | 276 | 35.2761
15.3 | 11.3739 | 1 | 7.824 | 276 | 35.2761
17.1 | 12.3161 | 1 | 7.824 | 276 | 35.2761
16.9 | 11.1104 | 1 | 7.824 | 276 | 35.2761
17.1 | 11.3237 | 1 | 7.824 | 276 | 35.2761
17.2 | 11.2386 | 1 | 7.824 | 276 | 35.2761
16.7 | 11.0246 | 1 | 7.824 | 276 | 35.2761
15.9 | 10.2998 | 1 | 7.824 | 276 | 35.2761
14.4 | 10.0222 | 1 | 7.824 | 276 | 35.2761
13.3 | 9.4407 | 1 | 7.824 | 276 | 35.2761
12.5 | 9.0318 | 1 | 7.824 | 276 | 35.2761
11.3 | 8.8934 | 1 | 7.824 | 276 | 35.2761
10.4 | 8.7674 | 1 | 7.824 | 276 | 35.2761
9.5 | 8.3983 | 1 | 7.824 | 276 | 35.2761
9.4 | 8.7601 | 1 | 7.824 | 276 | 35.2761
8.8 | 8.3769 | 1 | 7.824 | 276 | 35.2761
8.3 | 7.9857 | 1 | 7.824 | 276 | 35.2761
8.4 | 7.9303 | 1 | 7.824 | 276 | 35.2761
7.8 | 7.644 | 1 | 7.824 | 276 | 35.2761
6.8 | 6.6988 | 1 | 7.824 | 276 | 35.2761
6.8 | 6.6988 | 1 | 7.824 | 276 | 35.2761
7.7 | 7.4418 | 1 | 7.824 | 276 | 35.2761
8.9 | 8.4753 | 1 | 7.824 | 276 | 35.2761
11.3 | 10.1953 | 1 | 7.824 | 276 | 35.2761
12.7 | 11.2831 | 1 | 7.824 | 276 | 35.2761
13.2 | 11.765 | 1 | 7.824 | 276 | 35.2761
14.1 | 12.4669 | 1 | 7.824 | 276 | 35.2761
15.3 | 13.3382 | 1 | 7.824 | 276 | 35.2761
16.2 | 13.6917 | 1 | 7.824 | 276 | 35.2761
16.6 | 13.9028 | 1 | 7.824 | 276 | 35.2761
16.1 | 13.7071 | 1 | 7.824 | 276 | 35.2761
15.5 | 13.5277 | 1 | 7.824 | 276 | 35.2761
14.7 | 13.2114 | 1 | 7.824 | 276 | 35.2761
13.4 | 12.7478 | 1 | 7.824 | 276 | 35.2761
12.2 | 11.9664 | 1 | 7.824 | 276 | 35.2761
12.5 | 12.2648 | 1 | 7.824 | 276 | 35.2761
11.7 | 11.4693 | 1 | 7.824 | 276 | 35.2761
11.7 | 11.4693 | 1 | 7.824 | 276 | 35.2761
11 | 10.7731 | 1 | 7.824 | 276 | 35.2761
10.8 | 10.6867 | 1 | 7.824 | 276 | 35.2761
10.1 | 10.1 | 1 | 7.824 | 276 | 35.2761
11.2 | 11.2 | 1 | 7.824 | 276 | 35.2761
11.5 | 11.5 | 1 | 7.824 | 276 | 35.2761
11.5 | 11.5 | 1 | 7.824 | 276 | 35.2761
11.7 | 11.7 | 1 | 7.824 | 276 | 35.2761
11.5 | 11.5 | 1 | 7.824 | 276 | 35.2761
11 | 11 | 1 | 7.824 | 276 | 35.2761
11.3 | 11.3 | 1 | 7.824 | 276 | 35.2761
11.8 | 11.8 | 1 | 7.824 | 276 | 35.2761
12.6 | 12.364 | 1 | 7.824 | 276 | 35.2761
13.9 | 13.0062 | 1 | 7.824 | 276 | 35.2761
16 | 13.9463 | 1 | 7.824 | 276 | 35.2761
16.5 | 14.3092 | 1 | 7.824 | 276 | 35.2761
16.8 | 14.5376 | 1 | 7.824 | 276 | 35.2761
16.8 | 14.4227 | 1 | 7.824 | 276 | 35.2761
16.1 | 14.3864 | 1 | 7.824 | 276 | 35.2761
14.5 | 13.4177 | 1 | 7.824 | 276 | 35.2761
14.6 | 13.5153 | 1 | 7.824 | 276 | 35.2761
13.4 | 12.9812 | 1 | 7.824 | 276 | 35.2761
13.1 | 12.7429 | 1 | 7.824 | 276 | 35.2761
13.1 | 12.861 | 1 | 7.824 | 276 | 35.2761
12.2 | 12.2 | 1 | 7.824 | 276 | 35.2761
12.7 | 12.7 | 1 | 7.824 | 276 | 35.2761
12.3 | 12.3 | 1 | 7.824 | 276 | 35.2761
12.4 | 12.4 | 1 | 7.824 | 276 | 35.2761
12.5 | 12.5 | 1 | 7.824 | 276 | 35.2761
12.3 | 12.3 | 1 | 7.824 | 276 | 35.2761
12.3 | 12.3 | 1 | 7.824 | 276 | 35.2761
12.2 | 12.2 | 1 | 7.824 | 276 | 35.2761
12 | 12 | 1 | 7.824 | 276 | 35.2761
12.1 | 12.1 | 1 | 7.824 | 276 | 35.2761
12.7 | 12.7 | 1 | 7.824 | 276 | 35.2761
12.7 | 12.4632 | 1 | 7.824 | 276 | 35.2761
14.7 | 13.9671 | 1 | 7.824 | 276 | 35.2761
15.8 | 14.507 | 1 | 7.824 | 276 | 35.2761
16.4 | 14.8509 | 1 | 7.824 | 276 | 35.2761
16.7 | 14.9629 | 1 | 7.824 | 276 | 35.2761
17.6 | 15.4133 | 1 | 7.824 | 276 | 35.2761
17.1 | 15.2294 | 1 | 7.824 | 276 | 35.2761
16.9 | 15.3946 | 1 | 7.824 | 276 | 35.2761
16.5 | 15.2479 | 1 | 7.824 | 276 | 35.2761
15.7 | 15.1355 | 1 | 7.824 | 276 | 35.2761
15.5 | 15.3107 | 1 | 7.824 | 276 | 35.2761
15.3 | 15.0492 | 1 | 7.824 | 276 | 35.2761
15 | 14.8749 | 1 | 7.824 | 276 | 35.2761
15 | 14.8749 | 1 | 7.824 | 276 | 35.2761
15 | 14.7507 | 1 | 7.824 | 276 | 35.2761
14.8 | 14.6135 | 1 | 7.824 | 276 | 35.2761
14.6 | 14.3529 | 1 | 7.824 | 276 | 35.2761
14.5 | 13.9503 | 1 | 7.824 | 276 | 35.2761
13.5 | 12.8455 | 1 | 7.824 | 276 | 35.2761
13.4 | 12.6315 | 1 | 7.824 | 276 | 35.2761
13.3 | 12.7072 | 1 | 7.824 | 276 | 35.2761
12.7 | 11.9445 | 1 | 7.824 | 276 | 35.2761
12.6 | 11.1843 | 1 | 7.824 | 276 | 35.2761
12.3 | 11.0028 | 1 | 7.824 | 276 | 35.2761
12.4 | 10.8329 | 1 | 7.824 | 276 | 35.2761
13.3 | 11.5359 | 1 | 7.824 | 276 | 35.2761
14.5 | 11.4228 | 1 | 7.824 | 276 | 35.2761
15 | 11.7335 | 1 | 7.824 | 276 | 35.2761
15 | 11.7335 | 1 | 7.824 | 276 | 35.2761
15.1 | 10.9555 | 1 | 7.824 | 276 | 35.2761
14.8 | 10.2372 | 1 | 7.824 | 276 | 35.2761
14 | 10.1552 | 1 | 7.824 | 276 | 35.2761
12.5 | 9.3001 | 1 | 7.824 | 276 | 35.2761
11.9 | 8.9355 | 1 | 7.824 | 276 | 35.2761
10.7 | 8.4735 | 1 | 7.824 | 276 | 35.2761
9.6 | 7.8132 | 1 | 7.824 | 276 | 35.2761
8.7 | 7.3812 | 1 | 7.824 | 276 | 35.2761
7.6 | 6.9433 | 1 | 7.824 | 276 | 35.2761
6.9 | 6.4507 | 1 | 7.824 | 276 | 35.2761
6.5 | 6.0562 | 1 | 7.824 | 276 | 35.2761
6.7 | 6.1567 | 1 | 7.824 | 276 | 35.2761
6.8 | 6.1589 | 1 | 7.824 | 276 | 35.2761
5.7 | 5.3619 | 1 | 7.824 | 276 | 35.2761
5.4 | 5.0651 | 1 | 7.824 | 276 | 35.2761
5.3 | 4.8264 | 1 | 7.824 | 276 | 35.2761
5.2 | 4.6365 | 1 | 7.824 | 276 | 35.2761
6 | 5.0996 | 1 | 7.824 | 276 | 35.2761
8.2 | 6.3537 | 1 | 7.824 | 276 | 35.2761
10.8 | 7.8448 | 1 | 7.824 | 276 | 35.2761
12.5 | 8.9936 | 1 | 7.824 | 276 | 35.2761
13.8 | 9.5429 | 1 | 7.824 | 276 | 35.2761
14.1 | 9.5906 | 1 | 7.824 | 276 | 35.2761
14.7 | 9.7342 | 1 | 7.824 | 276 | 35.2761
14.2 | 9.6357 | 1 | 7.824 | 276 | 35.2761
13.4 | 9.1023 | 1 | 7.824 | 276 | 35.2761
12.7 | 8.996 | 1 | 7.824 | 276 | 35.2761
11.5 | 8.7573 | 1 | 7.824 | 276 | 35.2761
11 | 8.571 | 1 | 7.824 | 276 | 35.2761
10 | 8.1011 | 1 | 7.824 | 276 | 35.2761
8.8 | 7.3845 | 1 | 7.824 | 276 | 35.2761
8 | 6.7575 | 1 | 7.824 | 276 | 35.2761
7.2 | 6.172 | 1 | 7.824 | 276 | 35.2761
6.7 | 5.78 | 1 | 7.824 | 276 | 35.2761
5.7 | 5.1274 | 1 | 7.824 | 276 | 35.2761
5.2 | 4.7743 | 1 | 7.824 | 276 | 35.2761
5 | 4.6693 | 1 | 7.824 | 276 | 35.2761
4.7 | 4.281 | 1 | 7.824 | 276 | 35.2761
4.7 | 4.281 | 1 | 7.824 | 276 | 35.2761
4.4 | 4.2133 | 1 | 7.824 | 276 | 35.2761
4.9 | 4.6633 | 1 | 7.824 | 276 | 35.2761
5.4 | 5.3031 | 1 | 7.824 | 276 | 35.2761
7.2 | 6.8958 | 1 | 7.824 | 276 | 35.2761
10.5 | 9.0622 | 1 | 7.824 | 276 | 35.2761
12.4 | 10.3685 | 1 | 7.824 | 276 | 35.2761
14.5 | 11.1294 | 1 | 7.824 | 276 | 35.2761
15.6 | 11.6895 | 1 | 7.824 | 276 | 35.2761
16.4 | 11.4638 | 1 | 7.824 | 276 | 35.2761
16.1 | 11.1988 | 1 | 7.824 | 276 | 35.2761
14.7 | 10.7796 | 1 | 7.824 | 276 | 35.2761
14.1 | 10.4707 | 1 | 7.824 | 276 | 35.2761
13.1 | 9.7028 | 1 | 7.824 | 276 | 35.2761
12.5 | 10.3065 | 1 | 7.824 | 276 | 35.2761
12.1 | 10.5428 | 1 | 7.824 | 276 | 35.2761
12 | 10.765 | 1 | 7.824 | 276 | 35.2761
12 | 11.0359 | 1 | 7.824 | 276 | 35.2761
11.1 | 10.5379 | 1 | 7.824 | 276 | 35.2761
11 | 10.4391 | 1 | 7.824 | 276 | 35.2761
11 | 10.4389 | 1 | 7.824 | 276 | 35.2761
11.3 | 10.6239 | 1 | 7.824 | 276 | 35.2761
11.1 | 10.5369 | 1 | 7.824 | 276 | 35.2761
11 | 10.4381 | 1 | 7.824 | 276 | 35.2761
11 | 10.5485 | 1 | 7.824 | 276 | 35.2761
10.9 | 10.673 | 1 | 7.824 | 276 | 35.2761
10.9 | 10.786 | 1 | 7.824 | 276 | 35.2761
10.9 | 10.6729 | 1 | 7.824 | 276 | 35.2761
11 | 10.7723 | 1 | 7.824 | 276 | 35.2761
12.6 | 11.73 | 1 | 7.824 | 276 | 35.2761
13.5 | 11.2908 | 1 | 7.824 | 276 | 35.2761
13.2 | 10.8001 | 1 | 7.824 | 276 | 35.2761
14.3 | 11.1162 | 1 | 7.824 | 276 | 35.2761
14.8 | 11.177 | 1 | 7.824 | 276 | 35.2761
13.9 | 10.9425 | 1 | 7.824 | 276 | 35.2761
13.3 | 11.0961 | 1 | 7.824 | 276 | 35.2761
12.7 | 12.0532 | 1 | 7.824 | 276 | 35.2761
11.7 | 10.8458 | 1 | 7.824 | 276 | 35.2761
11.5 | 10.1635 | 1 | 7.824 | 276 | 35.2761
11.2 | 9.9789 | 1 | 7.824 | 276 | 35.2761
11.1 | 9.9879 | 1 | 7.824 | 276 | 35.2761
11.2 | 9.9784 | 1 | 7.824 | 276 | 35.2761
11.1 | 9.8805 | 1 | 7.824 | 276 | 35.2761
11.3 | 9.8628 | 1 | 7.824 | 276 | 35.2761
11.4 | 9.906 | 1 | 7.824 | 276 | 35.2761
10.4 | 9.3066 | 1 | 7.824 | 276 | 35.2761
9.1 | 8.1976 | 1 | 7.824 | 276 | 35.2761
8.1 | 6.9771 | 1 | 7.824 | 276 | 35.2761
6.9 | 5.864 | 1 | 7.824 | 276 | 35.2761
6.2 | 4.8707 | 1 | 7.824 | 276 | 35.2761
6.2 | 4.6949 | 1 | 7.824 | 276 | 35.2761
6.9 | 5.0557 | 1 | 7.824 | 276 | 35.2761
8.8 | 6.3546 | 1 | 7.824 | 276 | 35.2761
10.1 | 7.2033 | 1 | 7.824 | 276 | 35.2761
11.3 | 7.2732 | 1 | 7.824 | 276 | 35.2761
11.2 | 7.1048 | 1 | 7.824 | 276 | 35.2761
12.3 | 7.7057 | 1 | 7.824 | 276 | 35.2761
10.9 | 8.1614 | 1 | 7.824 | 276 | 35.2761
10.9 | 7.3274 | 1 | 7.824 | 276 | 35.2761
9.3 | 7.2704 | 1 | 7.824 | 276 | 35.2761
8.6 | 6.7946 | 1 | 7.824 | 276 | 35.2761
8.8 | 6.9376 | 1 | 7.824 | 276 | 35.2761
8.1 | 6.3222 | 1 | 7.824 | 276 | 35.2761
8.8 | 6.9385 | 1 | 7.824 | 276 | 35.2761
8.6 | 7.0763 | 1 | 7.824 | 276 | 35.2761
8.5 | 7.1717 | 1 | 7.824 | 276 | 35.2761
8.4 | 7.0749 | 1 | 7.824 | 276 | 35.2761
8.8 | 7.1716 | 1 | 7.824 | 276 | 35.2761
8.8 | 7.6554 | 1 | 7.824 | 276 | 35.2761
8.8 | 7.6548 | 1 | 7.824 | 276 | 35.2761
8.7 | 7.7572 | 1 | 7.824 | 276 | 35.2761
8.3 | 7.8243 | 1 | 7.824 | 276 | 35.2761
8.2 | 7.9865 | 1 | 7.824 | 276 | 35.2761
9 | 8.7815 | 1 | 7.824 | 276 | 35.2761
12.2 | 11.9628 | 1 | 7.824 | 276 | 35.2761
14.7 | 13.2465 | 1 | 7.824 | 276 | 35.2761
14.9 | 13.3813 | 1 | 7.824 | 276 | 35.2761
15.8 | 12.6769 | 1 | 7.824 | 276 | 35.2761
13.5 | 9.0191 | 1 | 7.824 | 276 | 35.2761
12.9 | 8.8833 | 1 | 7.824 | 276 | 35.2761
12.2 | 8.3934 | 1 | 7.824 | 276 | 35.2761
12.8 | 8.3334 | 1 | 7.824 | 276 | 35.2761
11 | 8.2038 | 1 | 7.824 | 276 | 35.2761
11.8 | 7.7518 | 1 | 7.824 | 276 | 35.2761
11.1 | 6.3719 | 1 | 7.824 | 276 | 35.2761
10 | 6.2102 | 1 | 7.824 | 276 | 35.2761
8.2 | 5.5952 | 1 | 7.824 | 276 | 35.2761
7.7 | 5.2601 | 1 | 7.824 | 276 | 35.2761
8.2 | 5.8926 | 1 | 7.824 | 276 | 35.2761
7.9 | 5.5728 | 1 | 7.824 | 276 | 35.2761
7.2 | 5.4328 | 1 | 7.824 | 276 | 35.2761
7.3 | 5.7052 | 1 | 7.824 | 276 | 35.2761
7.1 | 5.8771 | 1 | 7.824 | 276 | 35.2761
7.4 | 5.9821 | 1 | 7.824 | 276 | 35.2761
8 | 6.3252 | 1 | 7.824 | 276 | 35.2761
8.1 | 6.5119 | 1 | 7.824 | 276 | 35.2761
9 | 7.1349 | 1 | 7.824 | 276 | 35.2761
9.7 | 7.5617 | 1 | 7.824 | 276 | 35.2761
10 | 7.7503 | 1 | 7.824 | 276 | 35.2761
11.2 | 8.5413 | 1 | 7.824 | 276 | 35.2761
11.8 | 9.2405 | 1 | 7.824 | 276 | 35.2761
12.8 | 10.2205 | 1 | 7.824 | 276 | 35.2761
13.8 | 10.8999 | 1 | 7.824 | 276 | 35.2761
12.9 | 11.2457 | 1 | 7.824 | 276 | 35.2761
12.4 | 11.4193 | 1 | 7.824 | 276 | 35.2761
11.8 | 10.8883 | 1 | 7.824 | 276 | 35.2761
11 | 10.7712 | 1 | 7.824 | 276 | 35.2761
11 | 10.771 | 1 | 7.824 | 276 | 35.2761
10.8 | 10.5721 | 1 | 7.824 | 276 | 35.2761
10.8 | 10.572 | 1 | 7.824 | 276 | 35.2761
12.5 | 12.2033 | 1 | 7.824 | 276 | 35.2761
14.3 | 13.6873 | 1 | 7.824 | 276 | 35.2761
14.9 | 14.0972 | 1 | 7.824 | 276 | 35.2761
14.8 | 14.2415 | 1 | 7.824 | 276 | 35.2761
14.9 | 14.4017 | 1 | 7.824 | 276 | 35.2761
13.5 | 12.9573 | 1 | 7.824 | 276 | 35.2761
13 | 12.6998 | 1 | 7.824 | 276 | 35.2761
12.6 | 12.3617 | 1 | 7.824 | 276 | 35.2761
12.4 | 11.9291 | 1 | 7.824 | 276 | 35.2761
11.6 | 11.0251 | 1 | 7.824 | 276 | 35.2761
11.3 | 10.6177 | 1 | 7.824 | 276 | 35.2761
11.1 | 10.4211 | 1 | 7.824 | 276 | 35.2761
10.9 | 10.4461 | 1 | 7.824 | 276 | 35.2761
11 | 10.6009 | 1 | 7.824 | 276 | 35.2761
11.5 | 10.9261 | 1 | 7.824 | 276 | 35.2761
11.8 | 11.3355 | 1 | 7.824 | 276 | 35.2761
12.4 | 11.2484 | 1 | 7.824 | 276 | 35.2761
12.6 | 11.4986 | 1 | 7.824 | 276 | 35.2761
14.4 | 11.6494 | 1 | 7.824 | 276 | 35.2761
12.9 | 10.1991 | 1 | 7.824 | 276 | 35.2761
11.2 | 9.2025 | 1 | 7.824 | 276 | 35.2761
10.8 | 8.2011 | 1 | 7.824 | 276 | 35.2761
10.2 | 7.7364 | 1 | 7.824 | 276 | 35.2761
9.1 | 6.4954 | 1 | 7.824 | 276 | 35.2761
8.8 | 6.5245 | 1 | 7.824 | 276 | 35.2761
8.7 | 6.6554 | 1 | 7.824 | 276 | 35.2761
6.1 | 5.1799 | 1 | 7.824 | 276 | 35.2761
6 | 5.2222 | 1 | 7.824 | 276 | 35.2761
5.4 | 4.41 | 1 | 7.824 | 276 | 35.2761
6 | 4.9914 | 1 | 7.824 | 276 | 35.2761
6 | 4.8554 | 1 | 7.824 | 276 | 35.2761
5.2 | 3.9539 | 1 | 7.824 | 276 | 35.2761
5 | 3.8923 | 1 | 7.824 | 276 | 35.2761
4.9 | 3.8836 | 1 | 7.824 | 276 | 35.2761
4.8 | 3.8751 | 1 | 7.824 | 276 | 35.2761
4.6 | 3.5947 | 1 | 7.824 | 276 | 35.2761
4.7 | 3.5627 | 1 | 7.824 | 276 | 35.2761
6 | 4.293 | 1 | 7.824 | 276 | 35.2761
7.5 | 5.2366 | 1 | 7.824 | 276 | 35.2761
9.2 | 6.0116 | 1 | 7.824 | 276 | 35.2761
10.4 | 6.6072 | 1 | 7.824 | 276 | 35.2761
10.5 | 6.5793 | 1 | 7.824 | 276 | 35.2761
10.3 | 6.0237 | 1 | 7.824 | 276 | 35.2761
10.9 | 6.4343 | 1 | 7.824 | 276 | 35.2761
10.7 | 6.5649 | 1 | 7.824 | 276 | 35.2761
10.4 | 6.6147 | 1 | 7.824 | 276 | 35.2761
9.5 | 5.9742 | 1 | 7.824 | 276 | 35.2761
8 | 4.9806 | 1 | 7.824 | 276 | 35.2761
7 | 4.5019 | 1 | 7.824 | 276 | 35.2761
6.9 | 4.6514 | 1 | 7.824 | 276 | 35.2761
5 | 3.6469 | 1 | 7.824 | 276 | 35.2761
5.2 | 3.8385 | 1 | 7.824 | 276 | 35.2761
5 | 3.3199 | 1 | 7.824 | 276 | 35.2761
3.9 | 2.8839 | 1 | 7.824 | 276 | 35.2761
3.6 | 3.1485 | 1 | 7.824 | 276 | 35.2761
3.1 | 2.6561 | 1 | 7.824 | 276 | 35.2761
4.2 | 3.5169 | 1 | 7.824 | 276 | 35.2761
2.8 | 2.4466 | 1 | 7.824 | 276 | 35.2761
3.9 | 3.311 | 1 | 7.824 | 276 | 35.2761
4.5 | 3.9437 | 1 | 7.824 | 276 | 35.2761
5.2 | 4.6309 | 1 | 7.824 | 276 | 35.2761
7.2 | 6.2085 | 1 | 7.824 | 276 | 35.2761
7.6 | 6.9372 | 1 | 7.824 | 276 | 35.2761
9.8 | 8.3277 | 1 | 7.824 | 276 | 35.2761
11 | 8.7833 | 1 | 7.824 | 276 | 35.2761
11.6 | 8.8194 | 1 | 7.824 | 276 | 35.2761
12 | 8.9063 | 1 | 7.824 | 276 | 35.2761
10.6 | 9.2455 | 1 | 7.824 | 276 | 35.2761
11 | 9.3216 | 1 | 7.824 | 276 | 35.2761
11 | 9.6814 | 1 | 7.824 | 276 | 35.2761
10.5 | 9.9416 | 1 | 7.824 | 276 | 35.2761
10.9 | 10.2254 | 1 | 7.824 | 276 | 35.2761
11 | 10.4337 | 1 | 7.824 | 276 | 35.2761
11.5 | 10.9827 | 1 | 7.824 | 276 | 35.2761
11.5 | 10.9827 | 1 | 7.824 | 276 | 35.2761
11.5 | 10.3749 | 1 | 7.824 | 276 | 35.2761
11 | 9.3673 | 1 | 7.824 | 276 | 35.2761
10.5 | 8.2527 | 1 | 7.824 | 276 | 35.2761
10 | 7.7841 | 1 | 7.824 | 276 | 35.2761
9.5 | 7.4537 | 1 | 7.824 | 276 | 35.2761
10 | 7.5975 | 1 | 7.824 | 276 | 35.2761
9.8 | 7.5481 | 1 | 7.824 | 276 | 35.2761
10 | 7.5963 | 1 | 7.824 | 276 | 35.2761
9.7 | 8.4726 | 1 | 7.824 | 276 | 35.2761
8.5 | 7.7122 | 1 | 7.824 | 276 | 35.2761
8.5 | 7.6109 | 1 | 7.824 | 276 | 35.2761
8.8 | 7.6025 | 1 | 7.824 | 276 | 35.2761
9.7 | 8.0237 | 1 | 7.824 | 276 | 35.2761
10.3 | 8.0631 | 1 | 7.824 | 276 | 35.2761
11 | 8.7679 | 1 | 7.824 | 276 | 35.2761
11.4 | 8.8541 | 1 | 7.824 | 276 | 35.2761
11.9 | 8.8932 | 1 | 7.824 | 276 | 35.2761
11.6 | 8.7118 | 1 | 7.824 | 276 | 35.2761
11.4 | 8.302 | 1 | 7.824 | 276 | 35.2761
11.1 | 7.5524 | 1 | 7.824 | 276 | 35.2761
10.5 | 7.2698 | 1 | 7.824 | 276 | 35.2761
9.5 | 6.5762 | 1 | 7.824 | 276 | 35.2761
8.8 | 5.7759 | 1 | 7.824 | 276 | 35.2761
8.3 | 5.5661 | 1 | 7.824 | 276 | 35.2761
7.5 | 5.2447 | 1 | 7.824 | 276 | 35.2761
7.1 | 4.9157 | 1 | 7.824 | 276 | 35.2761
6.8 | 5.0147 | 1 | 7.824 | 276 | 35.2761
6.7 | 5.007 | 1 | 7.824 | 276 | 35.2761
6 | 4.5585 | 1 | 7.824 | 276 | 35.2761
5.6 | 4.2205 | 1 | 7.824 | 276 | 35.2761
5.4 | 3.9459 | 1 | 7.824 | 276 | 35.2761
5.5 | 3.9166 | 1 | 7.824 | 276 | 35.2761
5 | 3.7759 | 1 | 7.824 | 276 | 35.2761
4.6 | 3.4769 | 1 | 7.824 | 276 | 35.2761
5.8 | 4.4587 | 1 | 7.824 | 276 | 35.2761
8.1 | 5.986 | 1 | 7.824 | 276 | 35.2761
9.9 | 7.2227 | 1 | 7.824 | 276 | 35.2761
11.6 | 7.7434 | 1 | 7.824 | 276 | 35.2761
12.5 | 8.1693 | 1 | 7.824 | 276 | 35.2761
12.7 | 8.0653 | 1 | 7.824 | 276 | 35.2761
12.1 | 8.0236 | 1 | 7.824 | 276 | 35.2761
12.4 | 8.0857 | 1 | 7.824 | 276 | 35.2761
11.5 | 8.2099 | 1 | 7.824 | 276 | 35.2761
9.6 | 7.259 | 1 | 7.824 | 276 | 35.2761
10 | 7.3651 | 1 | 7.824 | 276 | 35.2761
9.6 | 7.3049 | 1 | 7.824 | 276 | 35.2761
8.3 | 6.8545 | 1 | 7.824 | 276 | 35.2761
8.8 | 7.0989 | 1 | 7.824 | 276 | 35.2761
8.8 | 7.2387 | 1 | 7.824 | 276 | 35.2761
8.5 | 7.0929 | 1 | 7.824 | 276 | 35.2761
8.1 | 7.0408 | 1 | 7.824 | 276 | 35.2761
8.5 | 7.7742 | 1 | 7.824 | 276 | 35.2761
9 | 8.3663 | 1 | 7.824 | 276 | 35.2761
9.7 | 8.9491 | 1 | 7.824 | 276 | 35.2761
10.3 | 9.5369 | 1 | 7.824 | 276 | 35.2761
11 | 10.0086 | 1 | 7.824 | 276 | 35.2761
11.2 | 10.4183 | 1 | 7.824 | 276 | 35.2761
11.7 | 10.908 | 1 | 7.824 | 276 | 35.2761
12.1 | 11.2446 | 1 | 7.824 | 276 | 35.2761
12.4 | 11.6502 | 1 | 7.824 | 276 | 35.2761
12.6 | 11.9029 | 1 | 7.824 | 276 | 35.2761
12.5 | 11.9183 | 1 | 7.824 | 276 | 35.2761
13 | 12.3534 | 1 | 7.824 | 276 | 35.2761
13.1 | 12.5675 | 1 | 7.824 | 276 | 35.2761
13.2 | 12.0941 | 1 | 7.824 | 276 | 35.2761
13.5 | 12.8453 | 1 | 7.824 | 276 | 35.2761
13.7 | 13.0422 | 1 | 7.824 | 276 | 35.2761
14.1 | 13.4362 | 1 | 7.824 | 276 | 35.2761
14.4 | 13.8513 | 1 | 7.824 | 276 | 35.2761
14.6 | 14.2916 | 1 | 7.824 | 276 | 35.2761
15.1 | 14.482 | 1 | 7.824 | 276 | 35.2761
15.1 | 14.482 | 1 | 7.824 | 276 | 35.2761
15.1 | 14.4214 | 1 | 7.824 | 276 | 35.2761
15 | 14.444 | 1 | 7.824 | 276 | 35.2761
15 | 14.444 | 1 | 7.824 | 276 | 35.2761
15 | 14.3229 | 1 | 7.824 | 276 | 35.2761
15 | 14.3229 | 1 | 7.824 | 276 | 35.2761
15 | 14.2626 | 1 | 7.824 | 276 | 35.2761
15 | 14.3229 | 1 | 7.824 | 276 | 35.2761
14.7 | 14.2689 | 1 | 7.824 | 276 | 35.2761
14.6 | 14.1697 | 1 | 7.824 | 276 | 35.2761
14.6 | 14.1697 | 1 | 7.824 | 276 | 35.2761
15.1 | 14.5426 | 1 | 7.824 | 276 | 35.2761
15.2 | 14.6414 | 1 | 7.824 | 276 | 35.2761
15.6 | 14.8527 | 1 | 7.824 | 276 | 35.2761
15.5 | 14.8762 | 1 | 7.824 | 276 | 35.2761
15.9 | 14.9034 | 1 | 7.824 | 276 | 35.2761
15.6 | 14.4898 | 1 | 7.824 | 276 | 35.2761
15.8 | 14.3871 | 1 | 7.824 | 276 | 35.2761
15.4 | 14.3534 | 1 | 7.824 | 276 | 35.2761
15 | 14.2612 | 1 | 7.824 | 276 | 35.2761
14.7 | 14.2681 | 1 | 7.824 | 276 | 35.2761
14.8 | 14.1242 | 1 | 7.824 | 276 | 35.2761
14.8 | 14.1242 | 1 | 7.824 | 276 | 35.2761
14.2 | 13.9545 | 1 | 7.824 | 276 | 35.2761
13.3 | 12.5311 | 1 | 7.824 | 276 | 35.2761
12.4 | 11.2582 | 1 | 7.824 | 276 | 35.2761
11.6 | 10.0581 | 1 | 7.824 | 276 | 35.2761
10.5 | 8.6083 | 1 | 7.824 | 276 | 35.2761
9.5 | 6.8491 | 1 | 7.824 | 276 | 35.2761
8.2 | 6.3419 | 1 | 7.824 | 276 | 35.2761
6.5 | 5.4875 | 1 | 7.824 | 276 | 35.2761
5.7 | 4.8933 | 1 | 7.824 | 276 | 35.2761
5.4 | 4.7377 | 1 | 7.824 | 276 | 35.2761
5.7 | 4.7586 | 1 | 7.824 | 276 | 35.2761
5.4 | 4.5122 | 1 | 7.824 | 276 | 35.2761
6.3 | 5.0706 | 1 | 7.824 | 276 | 35.2761
7.6 | 6.0465 | 1 | 7.824 | 276 | 35.2761
9.6 | 7.1678 | 1 | 7.824 | 276 | 35.2761
11.1 | 7.889 | 1 | 7.824 | 276 | 35.2761
12 | 8.269 | 1 | 7.824 | 276 | 35.2761
11.8 | 8.1751 | 1 | 7.824 | 276 | 35.2761
12.2 | 8.3203 | 1 | 7.824 | 276 | 35.2761
11.2 | 7.9349 | 1 | 7.824 | 276 | 35.2761
10.8 | 7.8323 | 1 | 7.824 | 276 | 35.2761
10.7 | 7.6971 | 1 | 7.824 | 276 | 35.2761
10.8 | 7.7029 | 1 | 7.824 | 276 | 35.2761
10.2 | 7.5029 | 1 | 7.824 | 276 | 35.2761
9.8 | 7.811 | 1 | 7.824 | 276 | 35.2761
9.6 | 7.8572 | 1 | 7.824 | 276 | 35.2761
9.5 | 7.6202 | 1 | 7.824 | 276 | 35.2761
9.2 | 7.5234 | 1 | 7.824 | 276 | 35.2761
9.3 | 7.7607 | 1 | 7.824 | 276 | 35.2761
9.8 | 8.3852 | 1 | 7.824 | 276 | 35.2761
9.6 | 8.4912 | 1 | 7.824 | 276 | 35.2761
9.8 | 8.6845 | 1 | 7.824 | 276 | 35.2761
10 | 8.8778 | 1 | 7.824 | 276 | 35.2761
10.5 | 8.9551 | 1 | 7.824 | 276 | 35.2761
10.9 | 9.2359 | 1 | 7.824 | 276 | 35.2761
11.2 | 9.4719 | 1 | 7.824 | 276 | 35.2761
12 | 10.0296 | 1 | 7.824 | 276 | 35.2761
12.6 | 10.1928 | 1 | 7.824 | 276 | 35.2761
12.8 | 10.5818 | 1 | 7.824 | 276 | 35.2761
13.3 | 10.8482 | 1 | 7.824 | 276 | 35.2761
13.1 | 11.3364 | 1 | 7.824 | 276 | 35.2761
13 | 11.674 | 1 | 7.824 | 276 | 35.2761
13.1 | 12.2199 | 1 | 7.824 | 276 | 35.2761
12.5 | 11.9735 | 1 | 7.824 | 276 | 35.2761
11.5 | 10.9302 | 1 | 7.824 | 276 | 35.2761
11.3 | 9.873 | 1 | 7.824 | 276 | 35.2761
10.3 | 8.5142 | 1 | 7.824 | 276 | 35.2761
9.9 | 8.134 | 1 | 7.824 | 276 | 35.2761
9.1 | 7.7576 | 1 | 7.824 | 276 | 35.2761
8.5 | 7.3744 | 1 | 7.824 | 276 | 35.2761
7.9 | 6.8901 | 1 | 7.824 | 276 | 35.2761
6.6 | 5.9109 | 1 | 7.824 | 276 | 35.2761
6.4 | 5.7155 | 1 | 7.824 | 276 | 35.2761
6 | 5.4651 | 1 | 7.824 | 276 | 35.2761
7 | 6.3512 | 1 | 7.824 | 276 | 35.2761
7.2 | 6.5472 | 1 | 7.824 | 276 | 35.2761
8.1 | 7.1821 | 1 | 7.824 | 276 | 35.2761
7.9 | 7.0362 | 1 | 7.824 | 276 | 35.2761
8.1 | 7.1332 | 1 | 7.824 | 276 | 35.2761
8.4 | 7.1815 | 1 | 7.824 | 276 | 35.2761
8.6 | 7.5206 | 1 | 7.824 | 276 | 35.2761
9.1 | 7.5666 | 1 | 7.824 | 276 | 35.2761
10.2 | 7.9935 | 1 | 7.824 | 276 | 35.2761
10.8 | 8.0468 | 1 | 7.824 | 276 | 35.2761
11.7 | 9.064 | 1 | 7.824 | 276 | 35.2761
13 | 9.6491 | 1 | 7.824 | 276 | 35.2761
12 | 9.0125 | 1 | 7.824 | 276 | 35.2761
12.3 | 9.1937 | 1 | 7.824 | 276 | 35.2761
12.3 | 9.1923 | 1 | 7.824 | 276 | 35.2761
11 | 9.5849 | 1 | 7.824 | 276 | 35.2761
10.6 | 9.827 | 1 | 7.824 | 276 | 35.2761
10.5 | 9.8362 | 1 | 7.824 | 276 | 35.2761
10.4 | 9.7385 | 1 | 7.824 | 276 | 35.2761
10.1 | 9.2855 | 1 | 7.824 | 276 | 35.2761
10 | 9.1884 | 1 | 7.824 | 276 | 35.2761
9.8 | 8.9935 | 1 | 7.824 | 276 | 35.2761
9.1 | 8.2591 | 1 | 7.824 | 276 | 35.2761
7.1 | 6.5985 | 1 | 7.824 | 276 | 35.2761
7.2 | 6.455 | 1 | 7.824 | 276 | 35.2761
5.6 | 5.0298 | 1 | 7.824 | 276 | 35.2761
4.7 | 4.237 | 1 | 7.824 | 276 | 35.2761
5.4 | 4.6532 | 1 | 7.824 | 276 | 35.2761
5 | 4.352 | 1 | 7.824 | 276 | 35.2761
5 | 4.3523 | 1 | 7.824 | 276 | 35.2761
5.6 | 4.8944 | 1 | 7.824 | 276 | 35.2761
7.4 | 6.2762 | 1 | 7.824 | 276 | 35.2761
8.9 | 7.067 | 1 | 7.824 | 276 | 35.2761
10.6 | 8.0245 | 1 | 7.824 | 276 | 35.2761
12.2 | 8.9549 | 1 | 7.824 | 276 | 35.2761
13.2 | 9.1105 | 1 | 7.824 | 276 | 35.2761
13.8 | 9.1766 | 1 | 7.824 | 276 | 35.2761
13.4 | 8.6645 | 1 | 7.824 | 276 | 35.2761
13 | 8.807 | 1 | 7.824 | 276 | 35.2761
10.1 | 7.5163 | 1 | 7.824 | 276 | 35.2761
10.1 | 7.7403 | 1 | 7.824 | 276 | 35.2761
9.8 | 7.5968 | 1 | 7.824 | 276 | 35.2761
8.7 | 7.1536 | 1 | 7.824 | 276 | 35.2761
8 | 6.5771 | 1 | 7.824 | 276 | 35.2761
7.8 | 6.71 | 1 | 7.824 | 276 | 35.2761
7.2 | 6.2231 | 1 | 7.824 | 276 | 35.2761
6.2 | 5.4815 | 1 | 7.824 | 276 | 35.2761
6.3 | 5.6257 | 1 | 7.824 | 276 | 35.2761
5.9 | 5.3266 | 1 | 7.824 | 276 | 35.2761
5.5 | 5.0724 | 1 | 7.824 | 276 | 35.2761
4.4 | 4.1228 | 1 | 7.824 | 276 | 35.2761
4.5 | 4.0859 | 1 | 7.824 | 276 | 35.2761
5 | 4.7175 | 1 | 7.824 | 276 | 35.2761
4.5 | 4.1765 | 1 | 7.824 | 276 | 35.2761
5.5 | 4.8885 | 1 | 7.824 | 276 | 35.2761
6.8 | 6.0683 | 1 | 7.824 | 276 | 35.2761
8.7 | 7.5811 | 1 | 7.824 | 276 | 35.2761
11.1 | 9.0529 | 1 | 7.824 | 276 | 35.2761
12.6 | 9.928 | 1 | 7.824 | 276 | 35.2761
13.7 | 10.2754 | 1 | 7.824 | 276 | 35.2761
14.1 | 10.1778 | 1 | 7.824 | 276 | 35.2761
13.1 | 9.8217 | 1 | 7.824 | 276 | 35.2761
12.6 | 9.8789 | 1 | 7.824 | 276 | 35.2761
11.7 | 9.5684 | 1 | 7.824 | 276 | 35.2761
11 | 9.005 | 1 | 7.824 | 276 | 35.2761
9.9 | 8.3465 | 1 | 7.824 | 276 | 35.2761
9.4 | 7.8202 | 1 | 7.824 | 276 | 35.2761
8.7 | 7.726 | 1 | 7.824 | 276 | 35.2761
8.1 | 7.2399 | 1 | 7.824 | 276 | 35.2761
8.3 | 7.3859 | 1 | 7.824 | 276 | 35.2761
7 | 6.4539 | 1 | 7.824 | 276 | 35.2761
5.8 | 5.3675 | 1 | 7.824 | 276 | 35.2761
5.3 | 5.0142 | 1 | 7.824 | 276 | 35.2761
4.7 | 4.3735 | 1 | 7.824 | 276 | 35.2761
4.5 | 4.4062 | 1 | 7.824 | 276 | 35.2761
3.6 | 3.6 | 1 | 7.824 | 276 | 35.2761
4.4 | 4.3531 | 1 | 7.824 | 276 | 35.2761
3.6 | 3.5089 | 1 | 7.824 | 276 | 35.2761
3.6 | 3.5089 | 1 | 7.824 | 276 | 35.2761
4.7 | 4.6527 | 1 | 7.824 | 276 | 35.2761
5.9 | 5.6564 | 1 | 7.824 | 276 | 35.2761
9.1 | 8.213 | 1 | 7.824 | 276 | 35.2761
11.5 | 9.5223 | 1 | 7.824 | 276 | 35.2761
12.6 | 10.0641 | 1 | 7.824 | 276 | 35.2761
12.9 | 9.9081 | 1 | 7.824 | 276 | 35.2761
12.8 | 9.9097 | 1 | 7.824 | 276 | 35.2761
11.9 | 9.4569 | 1 | 7.824 | 276 | 35.2761
10.7 | 8.9083 | 1 | 7.824 | 276 | 35.2761
10.2 | 8.6768 | 1 | 7.824 | 276 | 35.2761
8.8 | 7.721 | 1 | 7.824 | 276 | 35.2761
8.7 | 7.8709 | 1 | 7.824 | 276 | 35.2761
7.6 | 7.0418 | 1 | 7.824 | 276 | 35.2761
6.4 | 6.0058 | 1 | 7.824 | 276 | 35.2761
7.4 | 6.944 | 1 | 7.824 | 276 | 35.2761
8 | 7.385 | 1 | 7.824 | 276 | 35.2761
8.1 | 7.6344 | 1 | 7.824 | 276 | 35.2761
8.1 | 7.6341 | 1 | 7.824 | 276 | 35.2761
8.3 | 7.8826 | 1 | 7.824 | 276 | 35.2761
8.6 | 8.0758 | 1 | 7.824 | 276 | 35.2761
8.4 | 8.2413 | 1 | 7.824 | 276 | 35.2761
8.8 | 8.481 | 1 | 7.824 | 276 | 35.2761
9.2 | 8.7193 | 1 | 7.824 | 276 | 35.2761
9.5 | 8.8578 | 1 | 7.824 | 276 | 35.2761
9.9 | 9.2508 | 1 | 7.824 | 276 | 35.2761
10.2 | 9.2304 | 1 | 7.824 | 276 | 35.2761
9.9 | 9.0415 | 1 | 7.824 | 276 | 35.2761
10.6 | 9.3087 | 1 | 7.824 | 276 | 35.2761
11.4 | 8.6549 | 1 | 7.824 | 276 | 35.2761
12.1 | 8.0666 | 1 | 7.824 | 276 | 35.2761
11.9 | 7.8064 | 1 | 7.824 | 276 | 35.2761
10.7 | 7.6104 | 1 | 7.824 | 276 | 35.2761
9.3 | 6.8893 | 1 | 7.824 | 276 | 35.2761
8.8 | 6.8674 | 1 | 7.824 | 276 | 35.2761
7.8 | 6.3746 | 1 | 7.824 | 276 | 35.2761
7.9 | 6.5165 | 1 | 7.824 | 276 | 35.2761
6.6 | 5.7256 | 1 | 7.824 | 276 | 35.2761
7.3 | 6.2185 | 1 | 7.824 | 276 | 35.2761
7.2 | 6.3098 | 1 | 7.824 | 276 | 35.2761
6.8 | 6.2057 | 1 | 7.824 | 276 | 35.2761
7 | 6.4021 | 1 | 7.824 | 276 | 35.2761
6.4 | 5.9569 | 1 | 7.824 | 276 | 35.2761
5.9 | 5.2756 | 1 | 7.824 | 276 | 35.2761
5.6 | 4.5753 | 1 | 7.824 | 276 | 35.2761
4.7 | 3.922 | 1 | 7.824 | 276 | 35.2761
4.9 | 4.1611 | 1 | 7.824 | 276 | 35.2761
4.5 | 4.0379 | 1 | 7.824 | 276 | 35.2761
4.8 | 4.1087 | 1 | 7.824 | 276 | 35.2761
5.8 | 4.6814 | 1 | 7.824 | 276 | 35.2761
7.8 | 6.0176 | 1 | 7.824 | 276 | 35.2761
9.1 | 6.0408 | 1 | 7.824 | 276 | 35.2761
10.1 | 6.305 | 1 | 7.824 | 276 | 35.2761
10.6 | 6.7057 | 1 | 7.824 | 276 | 35.2761
11 | 7.0962 | 1 | 7.824 | 276 | 35.2761
10.8 | 7.2821 | 1 | 7.824 | 276 | 35.2761
10.3 | 6.7519 | 1 | 7.824 | 276 | 35.2761
9.3 | 6.4625 | 1 | 7.824 | 276 | 35.2761
8.9 | 6.4749 | 1 | 7.824 | 276 | 35.2761
8.6 | 6.2816 | 1 | 7.824 | 276 | 35.2761
7.8 | 5.9672 | 1 | 7.824 | 276 | 35.2761
7.9 | 6.1059 | 1 | 7.824 | 276 | 35.2761
8.7 | 6.7703 | 1 | 7.824 | 276 | 35.2761
9.8 | 7.9477 | 1 | 7.824 | 276 | 35.2761
9.5 | 7.9975 | 1 | 7.824 | 276 | 35.2761
9.6 | 8.2893 | 1 | 7.824 | 276 | 35.2761
10.3 | 8.8622 | 1 | 7.824 | 276 | 35.2761
10.7 | 9.1446 | 1 | 7.824 | 276 | 35.2761
10.4 | 9.161 | 1 | 7.824 | 276 | 35.2761
10.5 | 9.5177 | 1 | 7.824 | 276 | 35.2761
10.5 | 9.57 | 1 | 7.824 | 276 | 35.2761
11 | 9.7928 | 1 | 7.824 | 276 | 35.2761
10.8 | 9.8626 | 1 | 7.824 | 276 | 35.2761
11.8 | 10.0436 | 1 | 7.824 | 276 | 35.2761
12.7 | 10.1363 | 1 | 7.824 | 276 | 35.2761
13.3 | 9.0684 | 1 | 7.824 | 276 | 35.2761
10.5 | 9.57 | 1 | 7.824 | 276 | 35.2761
13.8 | 9.3357 | 1 | 7.824 | 276 | 35.2761
13.7 | 9.0788 | 1 | 7.824 | 276 | 35.2761
13.5 | 9.3301 | 1 | 7.824 | 276 | 35.2761
12.9 | 9.5999 | 1 | 7.824 | 276 | 35.2761
12.5 | 9.7054 | 1 | 7.824 | 276 | 35.2761
12.4 | 9.9536 | 1 | 7.824 | 276 | 35.2761
11.9 | 10.4507 | 1 | 7.824 | 276 | 35.2761
11.5 | 10.6541 | 1 | 7.824 | 276 | 35.2761
11.5 | 10.6541 | 1 | 7.824 | 276 | 35.2761
11.2 | 10.5244 | 1 | 7.824 | 276 | 35.2761
11.4 | 10.7763 | 1 | 7.824 | 276 | 35.2761
11 | 10.6599 | 1 | 7.824 | 276 | 35.2761
11.5 | 10.8193 | 1 | 7.824 | 276 | 35.2761
10.2 | 9.7575 | 1 | 7.824 | 276 | 35.2761
10.4 | 9.955 | 1 | 7.824 | 276 | 35.2761
10.5 | 9.9446 | 1 | 7.824 | 276 | 35.2761
10 | 9.3449 | 1 | 7.824 | 276 | 35.2761
10.1 | 9.3368 | 1 | 7.824 | 276 | 35.2761
10.4 | 9.419 | 1 | 7.824 | 276 | 35.2761
11 | 9.9501 | 1 | 7.824 | 276 | 35.2761
11 | 10.2183 | 1 | 7.824 | 276 | 35.2761
11.7 | 10.9043 | 1 | 7.824 | 276 | 35.2761
12.8 | 11.645 | 1 | 7.824 | 276 | 35.2761
13.6 | 11.5431 | 1 | 7.824 | 276 | 35.2761
14 | 11.0903 | 1 | 7.824 | 276 | 35.2761
13.6 | 10.7182 | 1 | 7.824 | 276 | 35.2761
13 | 10.5604 | 1 | 7.824 | 276 | 35.2761
13 | 10.31 | 1 | 7.824 | 276 | 35.2761
12.1 | 9.8158 | 1 | 7.824 | 276 | 35.2761
12.2 | 9.6142 | 1 | 7.824 | 276 | 35.2761
11.3 | 10.0796 | 1 | 7.824 | 276 | 35.2761
10.9 | 10.1186 | 1 | 7.824 | 276 | 35.2761
11 | 10.1074 | 1 | 7.824 | 276 | 35.2761
11.4 | 10.5522 | 1 | 7.824 | 276 | 35.2761
11.3 | 10.6192 | 1 | 7.824 | 276 | 35.2761
11.3 | 10.6744 | 1 | 7.824 | 276 | 35.2761
11.4 | 10.6614 | 1 | 7.824 | 276 | 35.2761
11.3 | 10.618 | 1 | 7.824 | 276 | 35.2761
11.4 | 10.4951 | 1 | 7.824 | 276 | 35.2761
10.1 | 8.8085 | 1 | 7.824 | 276 | 35.2761
8.5 | 6.1585 | 1 | 7.824 | 276 | 35.2761
8.6 | 6.2079 | 1 | 7.824 | 276 | 35.2761
7.6 | 5.3648 | 1 | 7.824 | 276 | 35.2761
7.1 | 4.3375 | 1 | 7.824 | 276 | 35.2761
6.6 | 4.6025 | 1 | 7.824 | 276 | 35.2761
5.5 | 4.157 | 1 | 7.824 | 276 | 35.2761
5.2 | 3.8298 | 1 | 7.824 | 276 | 35.2761
5.7 | 3.9699 | 1 | 7.824 | 276 | 35.2761
6.4 | 4.1372 | 1 | 7.824 | 276 | 35.2761
6.2 | 3.3688 | 1 | 7.824 | 276 | 35.2761
4.4 | 2.9474 | 1 | 7.824 | 276 | 35.2761
3.8 | 2.2613 | 1 | 7.824 | 276 | 35.2761
3.7 | 2.0416 | 1 | 7.824 | 276 | 35.2761
4 | 1.2194 | 1 | 7.824 | 276 | 35.2761
3.2 | 0.68569 | 1 | 7.824 | 276 | 35.2761
2.8 | -0.12776 | 1 | 7.824 | 276 | 35.2761
2.4 | -0.32162 | 1 | 7.824 | 276 | 35.2761
2 | -0.64235 | 1 | 7.824 | 276 | 35.2761
1.6 | -0.81018 | 1 | 7.824 | 276 | 35.2761
1.9 | -0.6359 | 1 | 7.824 | 276 | 35.2761
1.4 | -0.31752 | 1 | 7.824 | 276 | 35.2761
1.3 | 0.076542 | 1 | 7.824 | 276 | 35.2761
1.2 | -0.021056 | 1 | 7.824 | 276 | 35.2761
1.6 | 0.25548 | 1 | 7.824 | 276 | 35.2761
2.1 | 1.4675 | 1 | 7.824 | 276 | 35.2761
2.5 | 1.4577 | 1 | 7.824 | 276 | 35.2761
2.3 | 1.1255 | 1 | 7.824 | 276 | 35.2761
2.8 | 1.4131 | 1 | 7.824 | 276 | 35.2761
3.3 | 1.8275 | 1 | 7.824 | 276 | 35.2761
4.2 | 2.4975 | 1 | 7.824 | 276 | 35.2761
5 | 3.0558 | 1 | 7.824 | 276 | 35.2761
5.7 | 3.5527 | 1 | 7.824 | 276 | 35.2761
6.2 | 3.7838 | 1 | 7.824 | 276 | 35.2761
6.6 | 4.0375 | 1 | 7.824 | 276 | 35.2761
6.5 | 3.872 | 1 | 7.824 | 276 | 35.2761
5.8 | 3.5706 | 1 | 7.824 | 276 | 35.2761
5.2 | 3.2842 | 1 | 7.824 | 276 | 35.2761
4.7 | 3.0112 | 1 | 7.824 | 276 | 35.2761
4.5 | 2.7851 | 1 | 7.824 | 276 | 35.2761
4.1 | 2.5249 | 1 | 7.824 | 276 | 35.2761
3.1 | 1.8066 | 1 | 7.824 | 276 | 35.2761
2.4 | 1.1894 | 1 | 7.824 | 276 | 35.2761
2.1 | 1.0154 | 1 | 7.824 | 276 | 35.2761
1.1 | 0.2158 | 1 | 7.824 | 276 | 35.2761
0.7 | -0.14088 | 1 | 7.824 | 276 | 35.2761
0.3 | -0.40903 | 1 | 7.824 | 276 | 35.2761
-0.3 | -0.79517 | 1 | 7.824 | 276 | 35.2761
0.2 | -0.38673 | 1 | 7.824 | 276 | 35.2761
0.9 | -0.066511 | 1 | 7.824 | 276 | 35.2761
1.2 | -0.012256 | 1 | 7.824 | 276 | 35.2761
1.4 | 0.18725 | 1 | 7.824 | 276 | 35.2761
1.6 | 0.42789 | 1 | 7.824 | 276 | 35.2761
2.4 | 1.1476 | 1 | 7.824 | 276 | 35.2761
4.9 | 2.6926 | 1 | 7.824 | 276 | 35.2761
6.3 | 3.8466 | 1 | 7.824 | 276 | 35.2761
7.8 | 4.9073 | 1 | 7.824 | 276 | 35.2761
8 | 5.0099 | 1 | 7.824 | 276 | 35.2761
8.1 | 5.4147 | 1 | 7.824 | 276 | 35.2761
9 | 5.7171 | 1 | 7.824 | 276 | 35.2761
7.7 | 5.0488 | 1 | 7.824 | 276 | 35.2761
7.4 | 5.1348 | 1 | 7.824 | 276 | 35.2761
7.3 | 5.1241 | 1 | 7.824 | 276 | 35.2761
7.2 | 5.2813 | 1 | 7.824 | 276 | 35.2761
6.6 | 5.8685 | 1 | 7.824 | 276 | 35.2761
7.1 | 6.0278 | 1 | 7.824 | 276 | 35.2761
6.9 | 6.1143 | 1 | 7.824 | 276 | 35.2761
6.7 | 6.1087 | 1 | 7.824 | 276 | 35.2761
6.7 | 6.3022 | 1 | 7.824 | 276 | 35.2761
6.8 | 6.3519 | 1 | 7.824 | 276 | 35.2761
6.8 | 6.4008 | 1 | 7.824 | 276 | 35.2761
7 | 6.5489 | 1 | 7.824 | 276 | 35.2761
7.5 | 6.7957 | 1 | 7.824 | 276 | 35.2761
7.8 | 7.0895 | 1 | 7.824 | 276 | 35.2761
8 | 7.3346 | 1 | 7.824 | 276 | 35.2761
7.9 | 7.2862 | 1 | 7.824 | 276 | 35.2761
8 | 7.4847 | 1 | 7.824 | 276 | 35.2761
9.1 | 8.2097 | 1 | 7.824 | 276 | 35.2761
9.9 | 8.8869 | 1 | 7.824 | 276 | 35.2761
10.9 | 9.7029 | 1 | 7.824 | 276 | 35.2761
12.2 | 10.8008 | 1 | 7.824 | 276 | 35.2761
12.6 | 10.7635 | 1 | 7.824 | 276 | 35.2761
12.8 | 10.8491 | 1 | 7.824 | 276 | 35.2761
12.7 | 10.9628 | 1 | 7.824 | 276 | 35.2761
12.8 | 11.2171 | 1 | 7.824 | 276 | 35.2761
12.6 | 11.1855 | 1 | 7.824 | 276 | 35.2761
12.2 | 11.1231 | 1 | 7.824 | 276 | 35.2761
12.1 | 11.0258 | 1 | 7.824 | 276 | 35.2761
11.8 | 10.8419 | 1 | 7.824 | 276 | 35.2761
11.5 | 10.6034 | 1 | 7.824 | 276 | 35.2761
10.9 | 10.0171 | 1 | 7.824 | 276 | 35.2761
10.5 | 9.5733 | 1 | 7.824 | 276 | 35.2761
8.9 | 8.4224 | 1 | 7.824 | 276 | 35.2761
8.5 | 8.3404 | 1 | 7.824 | 276 | 35.2761
8.6 | 8.3344 | 1 | 7.824 | 276 | 35.2761
7.7 | 7.4924 | 1 | 7.824 | 276 | 35.2761
7.8 | 7.5402 | 1 | 7.824 | 276 | 35.2761
8 | 7.687 | 1 | 7.824 | 276 | 35.2761
8.4 | 7.8766 | 1 | 7.824 | 276 | 35.2761
9.1 | 8.2568 | 1 | 7.824 | 276 | 35.2761
9.2 | 8.4566 | 1 | 7.824 | 276 | 35.2761
9.4 | 8.7045 | 1 | 7.824 | 276 | 35.2761
10.2 | 9.3833 | 1 | 7.824 | 276 | 35.2761
10.6 | 9.721 | 1 | 7.824 | 276 | 35.2761
10.4 | 10.0102 | 1 | 7.824 | 276 | 35.2761
10.4 | 10.0651 | 1 | 7.824 | 276 | 35.2761
10.7 | 10.1967 | 1 | 7.824 | 276 | 35.2761
10.9 | 10.4495 | 1 | 7.824 | 276 | 35.2761
11.3 | 10.789 | 1 | 7.824 | 276 | 35.2761
10.8 | 10.4616 | 1 | 7.824 | 276 | 35.2761
10.5 | 10.1643 | 1 | 7.824 | 276 | 35.2761
10.6 | 10.1533 | 1 | 7.824 | 276 | 35.2761
10.5 | 9.9998 | 1 | 7.824 | 276 | 35.2761
10.5 | 9.9456 | 1 | 7.824 | 276 | 35.2761
9.5 | 9.0665 | 1 | 7.824 | 276 | 35.2761
8.5 | 7.7215 | 1 | 7.824 | 276 | 35.2761
7.6 | 6.4583 | 1 | 7.824 | 276 | 35.2761
7.3 | 6.0758 | 1 | 7.824 | 276 | 35.2761
7.1 | 5.7472 | 1 | 7.824 | 276 | 35.2761
6.7 | 5.728 | 1 | 7.824 | 276 | 35.2761
6.4 | 5.3002 | 1 | 7.824 | 276 | 35.2761
6.4 | 5.0333 | 1 | 7.824 | 276 | 35.2761
6.1 | 4.6605 | 1 | 7.824 | 276 | 35.2761
5.7 | 4.3645 | 1 | 7.824 | 276 | 35.2761
5.7 | 4.2376 | 1 | 7.824 | 276 | 35.2761
5.6 | 4.018 | 1 | 7.824 | 276 | 35.2761
5.7 | 4.1971 | 1 | 7.824 | 276 | 35.2761
5.9 | 4.1375 | 1 | 7.824 | 276 | 35.2761
7 | 4.6775 | 1 | 7.824 | 276 | 35.2761
6.9 | 4.3879 | 1 | 7.824 | 276 | 35.2761
6.8 | 4.1441 | 1 | 7.824 | 276 | 35.2761
6.4 | 3.6324 | 1 | 7.824 | 276 | 35.2761
6.2 | 3.7864 | 1 | 7.824 | 276 | 35.2761
6.1 | 3.5087 | 1 | 7.824 | 276 | 35.2761
5.4 | 3.2791 | 1 | 7.824 | 276 | 35.2761
5 | 3.0228 | 1 | 7.824 | 276 | 35.2761
4.5 | 2.7466 | 1 | 7.824 | 276 | 35.2761
4 | 2.3921 | 1 | 7.824 | 276 | 35.2761
3.8 | 2.1174 | 1 | 7.824 | 276 | 35.2761
3.3 | 1.7489 | 1 | 7.824 | 276 | 35.2761
2.5 | 1.0798 | 1 | 7.824 | 276 | 35.2761
2.2 | 0.78138 | 1 | 7.824 | 276 | 35.2761
1.8 | 0.50553 | 1 | 7.824 | 276 | 35.2761
1.6 | 0.22633 | 1 | 7.824 | 276 | 35.2761
1.4 | 0.066627 | 1 | 7.824 | 276 | 35.2761
1 | -0.20062 | 1 | 7.824 | 276 | 35.2761
0.7 | -0.37231 | 1 | 7.824 | 276 | 35.2761
0.6 | -0.46769 | 1 | 7.824 | 276 | 35.2761
1.4 | 0.18866 | 1 | 7.824 | 276 | 35.2761
2.6 | 1.1395 | 1 | 7.824 | 276 | 35.2761
4.9 | 2.8961 | 1 | 7.824 | 276 | 35.2761
6.5 | 3.8444 | 1 | 7.824 | 276 | 35.2761
7.7 | 4.5952 | 1 | 7.824 | 276 | 35.2761
8.3 | 4.9855 | 1 | 7.824 | 276 | 35.2761
7.8 | 5.147 | 1 | 7.824 | 276 | 35.2761
7.8 | 5.4291 | 1 | 7.824 | 276 | 35.2761
7.1 | 5.4053 | 1 | 7.824 | 276 | 35.2761
6.3 | 4.7335 | 1 | 7.824 | 276 | 35.2761
6.1 | 4.7574 | 1 | 7.824 | 276 | 35.2761
5.2 | 4.3698 | 1 | 7.824 | 276 | 35.2761
4.7 | 4.0145 | 1 | 7.824 | 276 | 35.2761
3.9 | 3.3623 | 1 | 7.824 | 276 | 35.2761
3.5 | 3.056 | 1 | 7.824 | 276 | 35.2761
3 | 2.5212 | 1 | 7.824 | 276 | 35.2761
2.5 | 2.1132 | 1 | 7.824 | 276 | 35.2761
2.1 | 1.6364 | 1 | 7.824 | 276 | 35.2761
1.8 | 1.2608 | 1 | 7.824 | 276 | 35.2761
1.6 | 1.1851 | 1 | 7.824 | 276 | 35.2761
1.2 | 0.83108 | 1 | 7.824 | 276 | 35.2761
1 | 0.63383 | 1 | 7.824 | 276 | 35.2761
1.2 | 0.79116 | 1 | 7.824 | 276 | 35.2761
1 | 0.59392 | 1 | 7.824 | 276 | 35.2761
1.2 | 0.57914 | 1 | 7.824 | 276 | 35.2761
1.2 | 0.712 | 1 | 7.824 | 276 | 35.2761
3.3 | 2.3598 | 1 | 7.824 | 276 | 35.2761
5.3 | 3.8705 | 1 | 7.824 | 276 | 35.2761
7 | 5.0199 | 1 | 7.824 | 276 | 35.2761
7.7 | 5.2212 | 1 | 7.824 | 276 | 35.2761
8.9 | 5.7194 | 1 | 7.824 | 276 | 35.2761
9 | 5.9271 | 1 | 7.824 | 276 | 35.2761
7.3 | 5.2154 | 1 | 7.824 | 276 | 35.2761
6.6 | 4.6855 | 1 | 7.824 | 276 | 35.2761
6.6 | 4.3243 | 1 | 7.824 | 276 | 35.2761
6.5 | 4.4297 | 1 | 7.824 | 276 | 35.2761
6.1 | 4.2572 | 1 | 7.824 | 276 | 35.2761
5.7 | 4.208 | 1 | 7.824 | 276 | 35.2761
5.8 | 4.5153 | 1 | 7.824 | 276 | 35.2761
5.9 | 4.9612 | 1 | 7.824 | 276 | 35.2761
6.6 | 5.595 | 1 | 7.824 | 276 | 35.2761
7 | 6.1217 | 1 | 7.824 | 276 | 35.2761
7.7 | 6.8029 | 1 | 7.824 | 276 | 35.2761
7.8 | 6.9966 | 1 | 7.824 | 276 | 35.2761
7.8 | 7.0448 | 1 | 7.824 | 276 | 35.2761
8 | 7.2403 | 1 | 7.824 | 276 | 35.2761
8.2 | 7.4358 | 1 | 7.824 | 276 | 35.2761
8.4 | 7.6317 | 1 | 7.824 | 276 | 35.2761
8.6 | 7.8273 | 1 | 7.824 | 276 | 35.2761
8.9 | 8.0209 | 1 | 7.824 | 276 | 35.2761
9.3 | 8.4109 | 1 | 7.824 | 276 | 35.2761
9.7 | 8.6489 | 1 | 7.824 | 276 | 35.2761
10.4 | 9.0745 | 1 | 7.824 | 276 | 35.2761
10.9 | 9.5049 | 1 | 7.824 | 276 | 35.2761
11.2 | 9.4903 | 1 | 7.824 | 276 | 35.2761
11.3 | 9.1923 | 1 | 7.824 | 276 | 35.2761
10.9 | 8.9114 | 1 | 7.824 | 276 | 35.2761
10.6 | 8.7238 | 1 | 7.824 | 276 | 35.2761
10.6 | 8.5329 | 1 | 7.824 | 276 | 35.2761
10.4 | 8.4865 | 1 | 7.824 | 276 | 35.2761
10.5 | 8.0673 | 1 | 7.824 | 276 | 35.2761
10.4 | 7.9743 | 1 | 7.824 | 276 | 35.2761
10.3 | 8.0177 | 1 | 7.824 | 276 | 35.2761
10.3 | 8.0177 | 1 | 7.824 | 276 | 35.2761
10.1 | 8.1538 | 1 | 7.824 | 276 | 35.2761
10.1 | 8.2009 | 1 | 7.824 | 276 | 35.2761
10.1 | 8.2009 | 1 | 7.824 | 276 | 35.2761
9.9 | 8.1053 | 1 | 7.824 | 276 | 35.2761
9.7 | 8.1532 | 1 | 7.824 | 276 | 35.2761
9.5 | 8.2044 | 1 | 7.824 | 276 | 35.2761
8.8 | 8.2753 | 1 | 7.824 | 276 | 35.2761
8.6 | 8.1808 | 1 | 7.824 | 276 | 35.2761
8.5 | 8.1335 | 1 | 7.824 | 276 | 35.2761
8.8 | 8.2751 | 1 | 7.824 | 276 | 35.2761
8.8 | 8.4823 | 1 | 7.824 | 276 | 35.2761
9.1 | 8.5706 | 1 | 7.824 | 276 | 35.2761
9.5 | 8.7052 | 1 | 7.824 | 276 | 35.2761
9.8 | 8.9982 | 1 | 7.824 | 276 | 35.2761
9.9 | 8.8897 | 1 | 7.824 | 276 | 35.2761
10 | 8.8343 | 1 | 7.824 | 276 | 35.2761
9.6 | 8.4472 | 1 | 7.824 | 276 | 35.2761
9.6 | 8.4467 | 1 | 7.824 | 276 | 35.2761
9.2 | 8.4107 | 1 | 7.824 | 276 | 35.2761
9.2 | 8.4107 | 1 | 7.824 | 276 | 35.2761
9 | 8.2659 | 1 | 7.824 | 276 | 35.2761
9.1 | 8.1611 | 1 | 7.824 | 276 | 35.2761
8.9 | 7.9664 | 1 | 7.824 | 276 | 35.2761
8.7 | 7.7219 | 1 | 7.824 | 276 | 35.2761
8.5 | 7.5275 | 1 | 7.824 | 276 | 35.2761
8.4 | 7.3324 | 1 | 7.824 | 276 | 35.2761
8.2 | 7.2842 | 1 | 7.824 | 276 | 35.2761
8.1 | 7.1379 | 1 | 7.824 | 276 | 35.2761
7.7 | 7.1895 | 1 | 7.824 | 276 | 35.2761
7.5 | 7.1926 | 1 | 7.824 | 276 | 35.2761
7.5 | 6.9427 | 1 | 7.824 | 276 | 35.2761
7.6 | 7.041 | 1 | 7.824 | 276 | 35.2761
7.6 | 6.8445 | 1 | 7.824 | 276 | 35.2761
7.8 | 6.9912 | 1 | 7.824 | 276 | 35.2761
8.2 | 7.0895 | 1 | 7.824 | 276 | 35.2761
8.6 | 7.3797 | 1 | 7.824 | 276 | 35.2761
9.1 | 7.6674 | 1 | 7.824 | 276 | 35.2761
9.3 | 7.5261 | 1 | 7.824 | 276 | 35.2761
9 | 7.4754 | 1 | 7.824 | 276 | 35.2761
8.7 | 7.4267 | 1 | 7.824 | 276 | 35.2761
8.4 | 7.2819 | 1 | 7.824 | 276 | 35.2761
8.4 | 7.1378 | 1 | 7.824 | 276 | 35.2761
8.3 | 7.3308 | 1 | 7.824 | 276 | 35.2761
8.3 | 7.429 | 1 | 7.824 | 276 | 35.2761
8.2 | 7.4304 | 1 | 7.824 | 276 | 35.2761
8.2 | 7.5301 | 1 | 7.824 | 276 | 35.2761
8.1 | 7.2341 | 1 | 7.824 | 276 | 35.2761
7.9 | 7.1864 | 1 | 7.824 | 276 | 35.2761
7.6 | 6.9417 | 1 | 7.824 | 276 | 35.2761
7.4 | 6.7946 | 1 | 7.824 | 276 | 35.2761
7.2 | 6.7952 | 1 | 7.824 | 276 | 35.2761
7.1 | 6.5 | 1 | 7.824 | 276 | 35.2761
6.8 | 6.351 | 1 | 7.824 | 276 | 35.2761
6.8 | 6.3025 | 1 | 7.824 | 276 | 35.2761
6.8 | 6.1576 | 1 | 7.824 | 276 | 35.2761
6.9 | 6.1124 | 1 | 7.824 | 276 | 35.2761
6.9 | 6.1127 | 1 | 7.824 | 276 | 35.2761
7.6 | 6.3688 | 1 | 7.824 | 276 | 35.2761
7.5 | 6.1346 | 1 | 7.824 | 276 | 35.2761
8.4 | 6.2728 | 1 | 7.824 | 276 | 35.2761
8.8 | 6.1324 | 1 | 7.824 | 276 | 35.2761
9.1 | 6.2016 | 1 | 7.824 | 276 | 35.2761
9.2 | 6.2516 | 1 | 7.824 | 276 | 35.2761
9 | 6.3173 | 1 | 7.824 | 276 | 35.2761
8.8 | 6.051 | 1 | 7.824 | 276 | 35.2761
8.4 | 6.1026 | 1 | 7.824 | 276 | 35.2761
8.3 | 5.925 | 1 | 7.824 | 276 | 35.2761
7.9 | 5.7234 | 1 | 7.824 | 276 | 35.2761
7.9 | 5.5557 | 1 | 7.824 | 276 | 35.2761
7.2 | 5.5821 | 1 | 7.824 | 276 | 35.2761
7.2 | 5.6261 | 1 | 7.824 | 276 | 35.2761
6.9 | 5.2982 | 1 | 7.824 | 276 | 35.2761
5.9 | 5.0927 | 1 | 7.824 | 276 | 35.2761
5.9 | 4.9121 | 1 | 7.824 | 276 | 35.2761
5.1 | 4.3133 | 1 | 7.824 | 276 | 35.2761
3.8 | 3.1752 | 1 | 7.824 | 276 | 35.2761
4.2 | 3.6545 | 1 | 7.824 | 276 | 35.2761
4.6 | 4.0472 | 1 | 7.824 | 276 | 35.2761
5.3 | 4.2012 | 1 | 7.824 | 276 | 35.2761
6.3 | 4.4373 | 1 | 7.824 | 276 | 35.2761
5.8 | 4.3389 | 1 | 7.824 | 276 | 35.2761
5.8 | 4.5958 | 1 | 7.824 | 276 | 35.2761
7.1 | 5.5766 | 1 | 7.824 | 276 | 35.2761
8 | 6.3432 | 1 | 7.824 | 276 | 35.2761
9.9 | 7.8188 | 1 | 7.824 | 276 | 35.2761
9.6 | 7.5818 | 1 | 7.824 | 276 | 35.2761
9.6 | 7.3993 | 1 | 7.824 | 276 | 35.2761
9.7 | 7.4026 | 1 | 7.824 | 276 | 35.2761
9.6 | 7.2646 | 1 | 7.824 | 276 | 35.2761
8.7 | 6.9621 | 1 | 7.824 | 276 | 35.2761
8.7 | 7.0541 | 1 | 7.824 | 276 | 35.2761
8.7 | 7.1938 | 1 | 7.824 | 276 | 35.2761
8.8 | 7.2893 | 1 | 7.824 | 276 | 35.2761
8.9 | 7.291 | 1 | 7.824 | 276 | 35.2761
8.9 | 7.3849 | 1 | 7.824 | 276 | 35.2761
9 | 7.4805 | 1 | 7.824 | 276 | 35.2761
8.7 | 7.2873 | 1 | 7.824 | 276 | 35.2761
8.5 | 7.1428 | 1 | 7.824 | 276 | 35.2761
8 | 7.0421 | 1 | 7.824 | 276 | 35.2761
8.2 | 7.2851 | 1 | 7.824 | 276 | 35.2761
8.1 | 7.1874 | 1 | 7.824 | 276 | 35.2761
8 | 7.1387 | 1 | 7.824 | 276 | 35.2761
8.9 | 7.4784 | 1 | 7.824 | 276 | 35.2761
9.3 | 7.7658 | 1 | 7.824 | 276 | 35.2761
9.9 | 8.3394 | 1 | 7.824 | 276 | 35.2761
10.4 | 8.6215 | 1 | 7.824 | 276 | 35.2761
10.9 | 8.9978 | 1 | 7.824 | 276 | 35.2761
11.4 | 9.3731 | 1 | 7.824 | 276 | 35.2761
11.8 | 9.6512 | 1 | 7.824 | 276 | 35.2761
11.8 | 9.7503 | 1 | 7.824 | 276 | 35.2761
12 | 9.9887 | 1 | 7.824 | 276 | 35.2761
12 | 10.0383 | 1 | 7.824 | 276 | 35.2761
12 | 10.1908 | 1 | 7.824 | 276 | 35.2761
12 | 10.2937 | 1 | 7.824 | 276 | 35.2761
11.9 | 10.0446 | 1 | 7.824 | 276 | 35.2761
11.8 | 9.9995 | 1 | 7.824 | 276 | 35.2761
11.7 | 9.8536 | 1 | 7.824 | 276 | 35.2761
11.5 | 9.7635 | 1 | 7.824 | 276 | 35.2761
11.6 | 9.8082 | 1 | 7.824 | 276 | 35.2761
11.7 | 9.9536 | 1 | 7.824 | 276 | 35.2761
11.4 | 10.027 | 1 | 7.824 | 276 | 35.2761
11.6 | 10.2724 | 1 | 7.824 | 276 | 35.2761
11.8 | 10.4649 | 1 | 7.824 | 276 | 35.2761
11.6 | 10.7549 | 1 | 7.824 | 276 | 35.2761
11.9 | 10.7213 | 1 | 7.824 | 276 | 35.2761
12.6 | 10.7067 | 1 | 7.824 | 276 | 35.2761
11.5 | 10.6566 | 1 | 7.824 | 276 | 35.2761
11.5 | 10.6022 | 1 | 7.824 | 276 | 35.2761
9.8 | 8.7874 | 1 | 7.824 | 276 | 35.2761
9.4 | 8.1484 | 1 | 7.824 | 276 | 35.2761
9.8 | 7.5314 | 1 | 7.824 | 276 | 35.2761
10.5 | 7.1733 | 1 | 7.824 | 276 | 35.2761
11 | 7.2899 | 1 | 7.824 | 276 | 35.2761
10.8 | 7.1932 | 1 | 7.824 | 276 | 35.2761
10.8 | 7.2754 | 1 | 7.824 | 276 | 35.2761
10 | 6.3232 | 1 | 7.824 | 276 | 35.2761
9.1 | 6.0332 | 1 | 7.824 | 276 | 35.2761
8.7 | 5.4768 | 1 | 7.824 | 276 | 35.2761
8.3 | 4.2099 | 1 | 7.824 | 276 | 35.2761
7 | 3.5921 | 1 | 7.824 | 276 | 35.2761
5.5 | 3.058 | 1 | 7.824 | 276 | 35.2761
4.8 | 2.3058 | 1 | 7.824 | 276 | 35.2761
4.2 | 1.8489 | 1 | 7.824 | 276 | 35.2761
3.4 | 1.7181 | 1 | 7.824 | 276 | 35.2761
2.7 | 1.4023 | 1 | 7.824 | 276 | 35.2761
2.3 | 0.79487 | 1 | 7.824 | 276 | 35.2761
1.9 | 0.20373 | 1 | 7.824 | 276 | 35.2761
1.4 | -0.12554 | 1 | 7.824 | 276 | 35.2761
0.7 | -0.63618 | 1 | 7.824 | 276 | 35.2761
0.7 | -0.37532 | 1 | 7.824 | 276 | 35.2761
0.6 | -0.23871 | 1 | 7.824 | 276 | 35.2761
0.4 | -0.88271 | 1 | 7.824 | 276 | 35.2761
0.8 | -0.46761 | 1 | 7.824 | 276 | 35.2761
1.4 | 0.064293 | 1 | 7.824 | 276 | 35.2761
2.7 | 0.7533 | 1 | 7.824 | 276 | 35.2761
3.7 | 1.808 | 1 | 7.824 | 276 | 35.2761
5.4 | 2.8415 | 1 | 7.824 | 276 | 35.2761
5.8 | 3.0218 | 1 | 7.824 | 276 | 35.2761
6 | 3.2917 | 1 | 7.824 | 276 | 35.2761
6 | 3.4531 | 1 | 7.824 | 276 | 35.2761
6 | 3.6406 | 1 | 7.824 | 276 | 35.2761
5.8 | 4.0035 | 1 | 7.824 | 276 | 35.2761
5.9 | 4.3879 | 1 | 7.824 | 276 | 35.2761
6 | 4.6975 | 1 | 7.824 | 276 | 35.2761
6.1 | 5.014 | 1 | 7.824 | 276 | 35.2761
6.5 | 5.2646 | 1 | 7.824 | 276 | 35.2761
6.7 | 5.6383 | 1 | 7.824 | 276 | 35.2761
7.1 | 6.355 | 1 | 7.824 | 276 | 35.2761
7.6 | 7.1904 | 1 | 7.824 | 276 | 35.2761
7.8 | 7.3375 | 1 | 7.824 | 276 | 35.2761
7.3 | 6.9941 | 1 | 7.824 | 276 | 35.2761
7.1 | 6.7959 | 1 | 7.824 | 276 | 35.2761
7.1 | 6.8459 | 1 | 7.824 | 276 | 35.2761
6.3 | 6.1011 | 1 | 7.824 | 276 | 35.2761
6.6 | 6.3993 | 1 | 7.824 | 276 | 35.2761
8.2 | 7.5297 | 1 | 7.824 | 276 | 35.2761
8.3 | 7.8306 | 1 | 7.824 | 276 | 35.2761
9.2 | 8.5622 | 1 | 7.824 | 276 | 35.2761
10.2 | 9.2295 | 1 | 7.824 | 276 | 35.2761
11.2 | 9.9913 | 1 | 7.824 | 276 | 35.2761
12.5 | 10.4087 | 1 | 7.824 | 276 | 35.2761
13 | 10.2784 | 1 | 7.824 | 276 | 35.2761
13.9 | 10.9639 | 1 | 7.824 | 276 | 35.2761
13.3 | 10.6056 | 1 | 7.824 | 276 | 35.2761
12.8 | 10.5387 | 1 | 7.824 | 276 | 35.2761
12.3 | 10.3203 | 1 | 7.824 | 276 | 35.2761
12.2 | 10.4826 | 1 | 7.824 | 276 | 35.2761
12.1 | 10.5435 | 1 | 7.824 | 276 | 35.2761
12 | 10.712 | 1 | 7.824 | 276 | 35.2761
12.4 | 10.9379 | 1 | 7.824 | 276 | 35.2761
12.3 | 11.1104 | 1 | 7.824 | 276 | 35.2761
11.4 | 10.614 | 1 | 7.824 | 276 | 35.2761
10.2 | 9.7591 | 1 | 7.824 | 276 | 35.2761
10.7 | 10.1439 | 1 | 7.824 | 276 | 35.2761
11 | 10.2755 | 1 | 7.824 | 276 | 35.2761
11.4 | 10.4504 | 1 | 7.824 | 276 | 35.2761
11 | 10.1133 | 1 | 7.824 | 276 | 35.2761
10.9 | 10.0156 | 1 | 7.824 | 276 | 35.2761
10.4 | 9.7397 | 1 | 7.824 | 276 | 35.2761
10.3 | 9.6414 | 1 | 7.824 | 276 | 35.2761
10.5 | 9.6775 | 1 | 7.824 | 276 | 35.2761
11.3 | 10.4056 | 1 | 7.824 | 276 | 35.2761
11.8 | 11.2272 | 1 | 7.824 | 276 | 35.2761
12.6 | 11.7318 | 1 | 7.824 | 276 | 35.2761
13.1 | 12.0511 | 1 | 7.824 | 276 | 35.2761
13.7 | 12.4089 | 1 | 7.824 | 276 | 35.2761
14 | 12.6998 | 1 | 7.824 | 276 | 35.2761
14.1 | 12.6266 | 1 | 7.824 | 276 | 35.2761
13.4 | 12.514 | 1 | 7.824 | 276 | 35.2761
8 | 7.0351 | 1 | 7.824 | 276 | 35.2761
7.6 | 6.7916 | 1 | 7.824 | 276 | 35.2761
7.4 | 6.5005 | 1 | 7.824 | 276 | 35.2761
7 | 6.2064 | 1 | 7.824 | 276 | 35.2761
7.2 | 6.3536 | 1 | 7.824 | 276 | 35.2761
7 | 6.2547 | 1 | 7.824 | 276 | 35.2761
6.9 | 6.2049 | 1 | 7.824 | 276 | 35.2761
6.6 | 5.9112 | 1 | 7.824 | 276 | 35.2761
5.6 | 5.1658 | 1 | 7.824 | 276 | 35.2761
4.2 | 4.0132 | 1 | 7.824 | 276 | 35.2761
3.3 | 3.2089 | 1 | 7.824 | 276 | 35.2761
2.8 | 2.6218 | 1 | 7.824 | 276 | 35.2761
2.4 | 2.0523 | 1 | 7.824 | 276 | 35.2761
3 | 2.5584 | 1 | 7.824 | 276 | 35.2761
2.5 | 2.0661 | 1 | 7.824 | 276 | 35.2761
2.3 | 1.9112 | 1 | 7.824 | 276 | 35.2761
2.9 | 2.3322 | 1 | 7.824 | 276 | 35.2761
4.4 | 3.4106 | 1 | 7.824 | 276 | 35.2761
5.5 | 4.2556 | 1 | 7.824 | 276 | 35.2761
7.1 | 5.6543 | 1 | 7.824 | 276 | 35.2761
7.9 | 6.2813 | 1 | 7.824 | 276 | 35.2761
8 | 6.1504 | 1 | 7.824 | 276 | 35.2761
8.3 | 6.1242 | 1 | 7.824 | 276 | 35.2761
7.2 | 5.4827 | 1 | 7.824 | 276 | 35.2761
6.2 | 4.9258 | 1 | 7.824 | 276 | 35.2761
5.7 | 4.5775 | 1 | 7.824 | 276 | 35.2761
4.8 | 4.0149 | 1 | 7.824 | 276 | 35.2761
3.9 | 3.3117 | 1 | 7.824 | 276 | 35.2761
4 | 3.3222 | 1 | 7.824 | 276 | 35.2761
3.1 | 2.6997 | 1 | 7.824 | 276 | 35.2761
2.1 | 1.7977 | 1 | 7.824 | 276 | 35.2761
1.8 | 1.5009 | 1 | 7.824 | 276 | 35.2761
1.2 | 1.0314 | 1 | 7.824 | 276 | 35.2761
1.3 | 1.0475 | 1 | 7.824 | 276 | 35.2761
0.8 | 0.63376 | 1 | 7.824 | 276 | 35.2761
0.7 | 0.36614 | 1 | 7.824 | 276 | 35.2761
2.2 | 1.562 | 1 | 7.824 | 276 | 35.2761
2.3 | 1.7422 | 1 | 7.824 | 276 | 35.2761
3 | 2.3433 | 1 | 7.824 | 276 | 35.2761
3.8 | 3.1246 | 1 | 7.824 | 276 | 35.2761
4.9 | 4.0211 | 1 | 7.824 | 276 | 35.2761
6.4 | 5.2935 | 1 | 7.824 | 276 | 35.2761
7.3 | 6.1618 | 1 | 7.824 | 276 | 35.2761
8.6 | 6.8452 | 1 | 7.824 | 276 | 35.2761
9.9 | 7.7931 | 1 | 7.824 | 276 | 35.2761
10.5 | 8.2139 | 1 | 7.824 | 276 | 35.2761
10.6 | 8.6917 | 1 | 7.824 | 276 | 35.2761
10.2 | 8.9098 | 1 | 7.824 | 276 | 35.2761
9.3 | 8.499 | 1 | 7.824 | 276 | 35.2761
9.3 | 8.2437 | 1 | 7.824 | 276 | 35.2761
8.8 | 6.3199 | 1 | 7.824 | 276 | 35.2761
6.4 | 5.4311 | 1 | 7.824 | 276 | 35.2761
6 | 5.1353 | 1 | 7.824 | 276 | 35.2761
5.1 | 4.4403 | 1 | 7.824 | 276 | 35.2761
6.1 | 4.8708 | 1 | 7.824 | 276 | 35.2761
6 | 4.7754 | 1 | 7.824 | 276 | 35.2761
5.8 | 4.6273 | 1 | 7.824 | 276 | 35.2761
5 | 3.9444 | 1 | 7.824 | 276 | 35.2761
4.2 | 3.2998 | 1 | 7.824 | 276 | 35.2761
4.6 | 3.4739 | 1 | 7.824 | 276 | 35.2761
3.8 | 2.9547 | 1 | 7.824 | 276 | 35.2761
3.5 | 2.7059 | 1 | 7.824 | 276 | 35.2761
3.5 | 2.7063 | 1 | 7.824 | 276 | 35.2761
3 | 2.4299 | 1 | 7.824 | 276 | 35.2761
4.2 | 3.3022 | 1 | 7.824 | 276 | 35.2761
5.8 | 4.5433 | 1 | 7.824 | 276 | 35.2761
7.1 | 5.4344 | 1 | 7.824 | 276 | 35.2761
8.3 | 6.2146 | 1 | 7.824 | 276 | 35.2761
8.7 | 6.4133 | 1 | 7.824 | 276 | 35.2761
9 | 6.5628 | 1 | 7.824 | 276 | 35.2761
9 | 6.6499 | 1 | 7.824 | 276 | 35.2761
8.6 | 6.5854 | 1 | 7.824 | 276 | 35.2761
8.6 | 6.8113 | 1 | 7.824 | 276 | 35.2761
8.4 | 6.8518 | 1 | 7.824 | 276 | 35.2761
8.9 | 7.1881 | 1 | 7.824 | 276 | 35.2761
8.8 | 7.0931 | 1 | 7.824 | 276 | 35.2761
8.4 | 6.9923 | 1 | 7.824 | 276 | 35.2761
8.5 | 7.2305 | 1 | 7.824 | 276 | 35.2761
9 | 7.9087 | 1 | 7.824 | 276 | 35.2761
9.8 | 8.7344 | 1 | 7.824 | 276 | 35.2761
10.8 | 9.6008 | 1 | 7.824 | 276 | 35.2761
11.3 | 10.0317 | 1 | 7.824 | 276 | 35.2761
11 | 10.4381 | 1 | 7.824 | 276 | 35.2761
11 | 10.3832 | 1 | 7.824 | 276 | 35.2761
11.1 | 10.5364 | 1 | 7.824 | 276 | 35.2761
11.2 | 10.6903 | 1 | 7.824 | 276 | 35.2761
11.7 | 10.7945 | 1 | 7.824 | 276 | 35.2761
11.9 | 10.99 | 1 | 7.824 | 276 | 35.2761
11.9 | 11.1003 | 1 | 7.824 | 276 | 35.2761
12.3 | 11.5486 | 1 | 7.824 | 276 | 35.2761
12.6 | 11.9 | 1 | 7.824 | 276 | 35.2761
13 | 12.1783 | 1 | 7.824 | 276 | 35.2761
13.4 | 12.4556 | 1 | 7.824 | 276 | 35.2761
13.7 | 12.6336 | 1 | 7.824 | 276 | 35.2761
13.8 | 12.7311 | 1 | 7.824 | 276 | 35.2761
13.7 | 12.7486 | 1 | 7.824 | 276 | 35.2761
13.6 | 12.6508 | 1 | 7.824 | 276 | 35.2761
13.7 | 12.6336 | 1 | 7.824 | 276 | 35.2761
13.7 | 12.691 | 1 | 7.824 | 276 | 35.2761
13.3 | 12.5878 | 1 | 7.824 | 276 | 35.2761
13.1 | 12.5654 | 1 | 7.824 | 276 | 35.2761
13.2 | 12.6057 | 1 | 7.824 | 276 | 35.2761
13.1 | 12.6239 | 1 | 7.824 | 276 | 35.2761
13.1 | 12.5654 | 1 | 7.824 | 276 | 35.2761
13.2 | 12.7228 | 1 | 7.824 | 276 | 35.2761
13.3 | 12.7629 | 1 | 7.824 | 276 | 35.2761
13.2 | 12.7817 | 1 | 7.824 | 276 | 35.2761
13.1 | 12.7414 | 1 | 7.824 | 276 | 35.2761
13.2 | 12.7815 | 1 | 7.824 | 276 | 35.2761
13.2 | 12.7226 | 1 | 7.824 | 276 | 35.2761
13.5 | 12.8426 | 1 | 7.824 | 276 | 35.2761
13.5 | 12.726 | 1 | 7.824 | 276 | 35.2761
13.7 | 12.6906 | 1 | 7.824 | 276 | 35.2761
13.9 | 12.8282 | 1 | 7.824 | 276 | 35.2761
14.1 | 12.9655 | 1 | 7.824 | 276 | 35.2761
14.4 | 13.0846 | 1 | 7.824 | 276 | 35.2761
14.6 | 13.1636 | 1 | 7.824 | 276 | 35.2761
14.7 | 13.3179 | 1 | 7.824 | 276 | 35.2761
14.6 | 13.2786 | 1 | 7.824 | 276 | 35.2761
14.5 | 13.2392 | 1 | 7.824 | 276 | 35.2761
14.7 | 13.2604 | 1 | 7.824 | 276 | 35.2761
14.5 | 13.2397 | 1 | 7.824 | 276 | 35.2761
14.3 | 13.2184 | 1 | 7.824 | 276 | 35.2761
12.8 | 11.9251 | 1 | 7.824 | 276 | 35.2761
11.5 | 10.6526 | 1 | 7.824 | 276 | 35.2761
10 | 9.4511 | 1 | 7.824 | 276 | 35.2761
8.8 | 8.0625 | 1 | 7.824 | 276 | 35.2761
7.5 | 6.8388 | 1 | 7.824 | 276 | 35.2761
5.5 | 5.0654 | 1 | 7.824 | 276 | 35.2761
5.2 | 4.5382 | 1 | 7.824 | 276 | 35.2761
4.6 | 3.9063 | 1 | 7.824 | 276 | 35.2761
3.7 | 2.8982 | 1 | 7.824 | 276 | 35.2761
3.6 | 2.9292 | 1 | 7.824 | 276 | 35.2761
4.1 | 3.2013 | 1 | 7.824 | 276 | 35.2761
3 | 2.5564 | 1 | 7.824 | 276 | 35.2761
3.8 | 2.9105 | 1 | 7.824 | 276 | 35.2761
5.3 | 3.5982 | 1 | 7.824 | 276 | 35.2761
5.9 | 3.8783 | 1 | 7.824 | 276 | 35.2761
6.1 | 4.1869 | 1 | 7.824 | 276 | 35.2761
6.5 | 4.2358 | 1 | 7.824 | 276 | 35.2761
6.6 | 4.4495 | 1 | 7.824 | 276 | 35.2761
6.8 | 4.4332 | 1 | 7.824 | 276 | 35.2761
6.9 | 4.4061 | 1 | 7.824 | 276 | 35.2761
5.9 | 4.0813 | 1 | 7.824 | 276 | 35.2761
5.9 | 4.418 | 1 | 7.824 | 276 | 35.2761
5.9 | 4.5473 | 1 | 7.824 | 276 | 35.2761
5.3 | 4.1897 | 1 | 7.824 | 276 | 35.2761
4.5 | 3.5901 | 1 | 7.824 | 276 | 35.2761
4.2 | 3.2993 | 1 | 7.824 | 276 | 35.2761
3.5 | 2.8326 | 1 | 7.824 | 276 | 35.2761
3.1 | 2.5266 | 1 | 7.824 | 276 | 35.2761
2.5 | 2.0648 | 1 | 7.824 | 276 | 35.2761
2.1 | 1.6295 | 1 | 7.824 | 276 | 35.2761
1.8 | 1.4587 | 1 | 7.824 | 276 | 35.2761
2.1 | 1.755 | 1 | 7.824 | 276 | 35.2761
1.5 | 1.2875 | 1 | 7.824 | 276 | 35.2761
1.5 | 1.1624 | 1 | 7.824 | 276 | 35.2761
2.5 | 2.0648 | 1 | 7.824 | 276 | 35.2761
3.3 | 2.6375 | 1 | 7.824 | 276 | 35.2761
3.3 | 2.6375 | 1 | 7.824 | 276 | 35.2761
3.6 | 2.931 | 1 | 7.824 | 276 | 35.2761
4.3 | 3.5274 | 1 | 7.824 | 276 | 35.2761
5.5 | 4.3841 | 1 | 7.824 | 276 | 35.2761
5.8 | 4.6733 | 1 | 7.824 | 276 | 35.2761
6.3 | 5.1998 | 1 | 7.824 | 276 | 35.2761
6.5 | 5.1683 | 1 | 7.824 | 276 | 35.2761
6.7 | 5.4499 | 1 | 7.824 | 276 | 35.2761
6.1 | 5.1888 | 1 | 7.824 | 276 | 35.2761
6.2 | 5.195 | 1 | 7.824 | 276 | 35.2761
6.5 | 5.6244 | 1 | 7.824 | 276 | 35.2761
6.4 | 5.5275 | 1 | 7.824 | 276 | 35.2761
5.7 | 5.03 | 1 | 7.824 | 276 | 35.2761
5.2 | 4.5409 | 1 | 7.824 | 276 | 35.2761
4.5 | 3.9452 | 1 | 7.824 | 276 | 35.2761
4.6 | 4.0437 | 1 | 7.824 | 276 | 35.2761
3.3 | 3.0742 | 1 | 7.824 | 276 | 35.2761
2.8 | 2.6663 | 1 | 7.824 | 276 | 35.2761
2.9 | 2.7658 | 1 | 7.824 | 276 | 35.2761
2.8 | 2.6663 | 1 | 7.824 | 276 | 35.2761
2.5 | 2.5 | 1 | 7.824 | 276 | 35.2761
2.6 | 2.4672 | 1 | 7.824 | 276 | 35.2761
2.8 | 2.6664 | 1 | 7.824 | 276 | 35.2761
2.4 | 2.4 | 1 | 7.824 | 276 | 35.2761
2.5 | 2.5 | 1 | 7.824 | 276 | 35.2761
2.6 | 2.4674 | 1 | 7.824 | 276 | 35.2761
2.3 | 2.3 | 1 | 7.824 | 276 | 35.2761
2.5 | 2.5 | 1 | 7.824 | 276 | 35.2761
3.3 | 3.2093 | 1 | 7.824 | 276 | 35.2761
3.9 | 3.5799 | 1 | 7.824 | 276 | 35.2761
4.3 | 3.7509 | 1 | 7.824 | 276 | 35.2761
4.9 | 4.2497 | 1 | 7.824 | 276 | 35.2761
5.4 | 4.5136 | 1 | 7.824 | 276 | 35.2761
5.4 | 4.6031 | 1 | 7.824 | 276 | 35.2761
5.8 | 4.9025 | 1 | 7.824 | 276 | 35.2761
5.7 | 4.5833 | 1 | 7.824 | 276 | 35.2761
5.8 | 4.903 | 1 | 7.824 | 276 | 35.2761
5.6 | 4.7088 | 1 | 7.824 | 276 | 35.2761
5.4 | 4.6039 | 1 | 7.824 | 276 | 35.2761
5.6 | 4.7088 | 1 | 7.824 | 276 | 35.2761
4.7 | 4.2348 | 1 | 7.824 | 276 | 35.2761
5 | 4.6688 | 1 | 7.824 | 276 | 35.2761
5.2 | 4.7735 | 1 | 7.824 | 276 | 35.2761
5.3 | 4.8723 | 1 | 7.824 | 276 | 35.2761
5.4 | 5.0647 | 1 | 7.824 | 276 | 35.2761
5.6 | 5.1682 | 1 | 7.824 | 276 | 35.2761
4.9 | 4.6632 | 1 | 7.824 | 276 | 35.2761
5.2 | 4.9609 | 1 | 7.824 | 276 | 35.2761
5.2 | 4.961 | 1 | 7.824 | 276 | 35.2761
5.8 | 5.4606 | 1 | 7.824 | 276 | 35.2761
7.2 | 6.5514 | 1 | 7.824 | 276 | 35.2761
7.6 | 6.9436 | 1 | 7.824 | 276 | 35.2761
7.9 | 7.1393 | 1 | 7.824 | 276 | 35.2761
8.9 | 7.8179 | 1 | 7.824 | 276 | 35.2761
9.3 | 8.2055 | 1 | 7.824 | 276 | 35.2761
10 | 8.6825 | 1 | 7.824 | 276 | 35.2761
9.8 | 8.6901 | 1 | 7.824 | 276 | 35.2761
9.6 | 8.4963 | 1 | 7.824 | 276 | 35.2761
9.3 | 8.6625 | 1 | 7.824 | 276 | 35.2761
9.5 | 8.7556 | 1 | 7.824 | 276 | 35.2761
9.6 | 8.6989 | 1 | 7.824 | 276 | 35.2761
9.6 | 8.6989 | 1 | 7.824 | 276 | 35.2761
9.3 | 8.4064 | 1 | 7.824 | 276 | 35.2761
8.8 | 8.1204 | 1 | 7.824 | 276 | 35.2761
7.8 | 7.2391 | 1 | 7.824 | 276 | 35.2761
7.7 | 7.042 | 1 | 7.824 | 276 | 35.2761
8 | 7.1395 | 1 | 7.824 | 276 | 35.2761
7.5 | 6.6039 | 1 | 7.824 | 276 | 35.2761
6.6 | 6.155 | 1 | 7.824 | 276 | 35.2761
7.6 | 6.7012 | 1 | 7.824 | 276 | 35.2761
6.9 | 6.451 | 1 | 7.824 | 276 | 35.2761
8.1 | 7.2366 | 1 | 7.824 | 276 | 35.2761
8.1 | 7.3348 | 1 | 7.824 | 276 | 35.2761
8.6 | 7.8236 | 1 | 7.824 | 276 | 35.2761
8.9 | 8.0168 | 1 | 7.824 | 276 | 35.2761
9.7 | 8.7968 | 1 | 7.824 | 276 | 35.2761
9.9 | 9.0431 | 1 | 7.824 | 276 | 35.2761
10.3 | 9.5918 | 1 | 7.824 | 276 | 35.2761
10.5 | 9.7345 | 1 | 7.824 | 276 | 35.2761
10.5 | 9.8415 | 1 | 7.824 | 276 | 35.2761
10.6 | 9.7268 | 1 | 7.824 | 276 | 35.2761
10.6 | 9.7268 | 1 | 7.824 | 276 | 35.2761
10.3 | 9.5389 | 1 | 7.824 | 276 | 35.2761
10.2 | 9.4409 | 1 | 7.824 | 276 | 35.2761
10 | 9.3502 | 1 | 7.824 | 276 | 35.2761
10.1 | 9.4484 | 1 | 7.824 | 276 | 35.2761
10 | 9.245 | 1 | 7.824 | 276 | 35.2761
10.1 | 9.2384 | 1 | 7.824 | 276 | 35.2761
9.4 | 8.9702 | 1 | 7.824 | 276 | 35.2761
9.2 | 8.6679 | 1 | 7.824 | 276 | 35.2761
8.8 | 8.3771 | 1 | 7.824 | 276 | 35.2761
9 | 8.3162 | 1 | 7.824 | 276 | 35.2761
8.7 | 8.022 | 1 | 7.824 | 276 | 35.2761
9.2 | 8.41 | 1 | 7.824 | 276 | 35.2761
9.3 | 8.4056 | 1 | 7.824 | 276 | 35.2761
9.8 | 8.5884 | 1 | 7.824 | 276 | 35.2761
9.9 | 8.6856 | 1 | 7.824 | 276 | 35.2761
9.9 | 8.6856 | 1 | 7.824 | 276 | 35.2761
10.5 | 8.4292 | 1 | 7.824 | 276 | 35.2761
10.9 | 8.6149 | 1 | 7.824 | 276 | 35.2761
11.5 | 8.3035 | 1 | 7.824 | 276 | 35.2761
11.1 | 8.0256 | 1 | 7.824 | 276 | 35.2761
11 | 7.9344 | 1 | 7.824 | 276 | 35.2761
10.7 | 7.7042 | 1 | 7.824 | 276 | 35.2761
10.3 | 7.6444 | 1 | 7.824 | 276 | 35.2761
9.9 | 7.3633 | 1 | 7.824 | 276 | 35.2761
9.6 | 7.1736 | 1 | 7.824 | 276 | 35.2761
8.9 | 6.9211 | 1 | 7.824 | 276 | 35.2761
8.2 | 6.5307 | 1 | 7.824 | 276 | 35.2761
7.7 | 6.2817 | 1 | 7.824 | 276 | 35.2761
6.6 | 5.4983 | 1 | 7.824 | 276 | 35.2761
5.5 | 4.8386 | 1 | 7.824 | 276 | 35.2761
5.3 | 4.6429 | 1 | 7.824 | 276 | 35.2761
4.9 | 4.432 | 1 | 7.824 | 276 | 35.2761
3.7 | 3.4724 | 1 | 7.824 | 276 | 35.2761
3.9 | 3.5809 | 1 | 7.824 | 276 | 35.2761
3.3 | 3.2096 | 1 | 7.824 | 276 | 35.2761
3.9 | 3.671 | 1 | 7.824 | 276 | 35.2761
3.8 | 3.5717 | 1 | 7.824 | 276 | 35.2761
5.6 | 5.0286 | 1 | 7.824 | 276 | 35.2761
6.5 | 5.4926 | 1 | 7.824 | 276 | 35.2761
6.6 | 5.7282 | 1 | 7.824 | 276 | 35.2761
7.3 | 6.3148 | 1 | 7.824 | 276 | 35.2761
7.3 | 6.4093 | 1 | 7.824 | 276 | 35.2761
8.7 | 8.0223 | 1 | 7.824 | 276 | 35.2761
8.7 | 7.7219 | 1 | 7.824 | 276 | 35.2761
9 | 8.0134 | 1 | 7.824 | 276 | 35.2761
9.2 | 8.1081 | 1 | 7.824 | 276 | 35.2761
8.8 | 7.9189 | 1 | 7.824 | 276 | 35.2761
8.9 | 7.9167 | 1 | 7.824 | 276 | 35.2761
9 | 8.0139 | 1 | 7.824 | 276 | 35.2761
8.8 | 7.82 | 1 | 7.824 | 276 | 35.2761
9 | 8.1139 | 1 | 7.824 | 276 | 35.2761
9 | 8.1139 | 1 | 7.824 | 276 | 35.2761
8.9 | 8.0168 | 1 | 7.824 | 276 | 35.2761
8.8 | 8.0196 | 1 | 7.824 | 276 | 35.2761
8.7 | 8.0226 | 1 | 7.824 | 276 | 35.2761
8.6 | 7.9246 | 1 | 7.824 | 276 | 35.2761
8.4 | 7.8293 | 1 | 7.824 | 276 | 35.2761
7.5 | 7.1933 | 1 | 7.824 | 276 | 35.2761
8 | 7.6889 | 1 | 7.824 | 276 | 35.2761
8.4 | 7.9822 | 1 | 7.824 | 276 | 35.2761
8.7 | 8.0226 | 1 | 7.824 | 276 | 35.2761
8.8 | 8.1207 | 1 | 7.824 | 276 | 35.2761
9.1 | 8.112 | 1 | 7.824 | 276 | 35.2761
9.3 | 8.3064 | 1 | 7.824 | 276 | 35.2761
9.2 | 8.2092 | 1 | 7.824 | 276 | 35.2761
9.4 | 8.2041 | 1 | 7.824 | 276 | 35.2761
9.3 | 8.2065 | 1 | 7.824 | 276 | 35.2761
9.2 | 8.1091 | 1 | 7.824 | 276 | 35.2761
9.2 | 8.2088 | 1 | 7.824 | 276 | 35.2761
9.2 | 8.2083 | 1 | 7.824 | 276 | 35.2761
9.1 | 8.1111 | 1 | 7.824 | 276 | 35.2761
9.2 | 8.1091 | 1 | 7.824 | 276 | 35.2761
9.3 | 8.206 | 1 | 7.824 | 276 | 35.2761
9.2 | 8.0103 | 1 | 7.824 | 276 | 35.2761
8.6 | 7.7239 | 1 | 7.824 | 276 | 35.2761
7.1 | 6.5503 | 1 | 7.824 | 276 | 35.2761
6.9 | 6.3537 | 1 | 7.824 | 276 | 35.2761
4.9 | 4.6634 | 1 | 7.824 | 276 | 35.2761
6.1 | 6.001 | 1 | 7.824 | 276 | 35.2761
5.9 | 5.8017 | 1 | 7.824 | 276 | 35.2761
5.5 | 5.2587 | 1 | 7.824 | 276 | 35.2761
5.4 | 5.0649 | 1 | 7.824 | 276 | 35.2761
5.5 | 5.1638 | 1 | 7.824 | 276 | 35.2761
5.4 | 4.7404 | 1 | 7.824 | 276 | 35.2761
5.5 | 4.9299 | 1 | 7.824 | 276 | 35.2761
5 | 4.439 | 1 | 7.824 | 276 | 35.2761
3.9 | 3.4468 | 1 | 7.824 | 276 | 35.2761
5.2 | 4.7733 | 1 | 7.824 | 276 | 35.2761
5.1 | 4.3121 | 1 | 7.824 | 276 | 35.2761
5.1 | 4.0925 | 1 | 7.824 | 276 | 35.2761
5.7 | 4.3673 | 1 | 7.824 | 276 | 35.2761
6.4 | 4.8195 | 1 | 7.824 | 276 | 35.2761
6.9 | 5.3369 | 1 | 7.824 | 276 | 35.2761
7.2 | 5.6213 | 1 | 7.824 | 276 | 35.2761
6.7 | 5.7294 | 1 | 7.824 | 276 | 35.2761
6.4 | 5.3927 | 1 | 7.824 | 276 | 35.2761
5.3 | 4.7323 | 1 | 7.824 | 276 | 35.2761
6.2 | 5.4285 | 1 | 7.824 | 276 | 35.2761
5.5 | 4.7001 | 1 | 7.824 | 276 | 35.2761
5.3 | 4.6405 | 1 | 7.824 | 276 | 35.2761
5.1 | 4.2213 | 1 | 7.824 | 276 | 35.2761
4.7 | 3.7894 | 1 | 7.824 | 276 | 35.2761
4.8 | 3.8864 | 1 | 7.824 | 276 | 35.2761
4.2 | 3.4333 | 1 | 7.824 | 276 | 35.2761
4.4 | 3.6281 | 1 | 7.824 | 276 | 35.2761
4.7 | 3.5755 | 1 | 7.824 | 276 | 35.2761
4.5 | 3.7251 | 1 | 7.824 | 276 | 35.2761
4.5 | 3.8133 | 1 | 7.824 | 276 | 35.2761
4.7 | 3.9204 | 1 | 7.824 | 276 | 35.2761
5.2 | 4.1865 | 1 | 7.824 | 276 | 35.2761
5.1 | 4.0904 | 1 | 7.824 | 276 | 35.2761
5.7 | 4.4513 | 1 | 7.824 | 276 | 35.2761
6.2 | 4.7143 | 1 | 7.824 | 276 | 35.2761
6.5 | 4.8282 | 1 | 7.824 | 276 | 35.2761
6.6 | 4.9228 | 1 | 7.824 | 276 | 35.2761
6.7 | 4.5999 | 1 | 7.824 | 276 | 35.2761
6.6 | 4.7121 | 1 | 7.824 | 276 | 35.2761
6.5 | 4.7025 | 1 | 7.824 | 276 | 35.2761
6.5 | 4.6192 | 1 | 7.824 | 276 | 35.2761
6.2 | 4.2967 | 1 | 7.824 | 276 | 35.2761
5.5 | 4.176 | 1 | 7.824 | 276 | 35.2761
5.2 | 3.9736 | 1 | 7.824 | 276 | 35.2761
4.7 | 3.5785 | 1 | 7.824 | 276 | 35.2761
4.5 | 3.5979 | 1 | 7.824 | 276 | 35.2761
4.2 | 3.4353 | 1 | 7.824 | 276 | 35.2761
3.1 | 2.5313 | 1 | 7.824 | 276 | 35.2761
1.9 | 1.5604 | 1 | 7.824 | 276 | 35.2761
1.4 | 1.19 | 1 | 7.824 | 276 | 35.2761
1.4 | 1.0667 | 1 | 7.824 | 276 | 35.2761
0.6 | 0.47706 | 1 | 7.824 | 276 | 35.2761
0.7 | 0.45515 | 1 | 7.824 | 276 | 35.2761
0.2 | -0.058066 | 1 | 7.824 | 276 | 35.2761
0 | -0.25589 | 1 | 7.824 | 276 | 35.2761
-0.4 | -0.56872 | 1 | 7.824 | 276 | 35.2761
-0.4 | -0.56862 | 1 | 7.824 | 276 | 35.2761
0.7 | 0.45529 | 1 | 7.824 | 276 | 35.2761
2.2 | 1.7321 | 1 | 7.824 | 276 | 35.2761
3.9 | 3.1014 | 1 | 7.824 | 276 | 35.2761
5.3 | 4.2001 | 1 | 7.824 | 276 | 35.2761
6.5 | 5.1785 | 1 | 7.824 | 276 | 35.2761
7.8 | 6.1517 | 1 | 7.824 | 276 | 35.2761
7.2 | 5.8491 | 1 | 7.824 | 276 | 35.2761
6.9 | 5.4727 | 1 | 7.824 | 276 | 35.2761
6.4 | 5.3958 | 1 | 7.824 | 276 | 35.2761
6.6 | 5.7278 | 1 | 7.824 | 276 | 35.2761
6.7 | 5.9187 | 1 | 7.824 | 276 | 35.2761
6.7 | 5.9187 | 1 | 7.824 | 276 | 35.2761
6.9 | 6.1139 | 1 | 7.824 | 276 | 35.2761
7.1 | 6.3091 | 1 | 7.824 | 276 | 35.2761
7.1 | 6.453 | 1 | 7.824 | 276 | 35.2761
7.1 | 6.5501 | 1 | 7.824 | 276 | 35.2761
6.9 | 6.2569 | 1 | 7.824 | 276 | 35.2761
6.7 | 6.0132 | 1 | 7.824 | 276 | 35.2761
6.8 | 6.2548 | 1 | 7.824 | 276 | 35.2761
6.7 | 5.6858 | 1 | 7.824 | 276 | 35.2761
6.5 | 5.4921 | 1 | 7.824 | 276 | 35.2761
6.3 | 5.3896 | 1 | 7.824 | 276 | 35.2761
5.9 | 5.138 | 1 | 7.824 | 276 | 35.2761
5.7 | 4.9429 | 1 | 7.824 | 276 | 35.2761
5.7 | 5.0344 | 1 | 7.824 | 276 | 35.2761
5.9 | 5.2302 | 1 | 7.824 | 276 | 35.2761
5.8 | 4.9044 | 1 | 7.824 | 276 | 35.2761
5.7 | 5.0341 | 1 | 7.824 | 276 | 35.2761
5.8 | 5.1319 | 1 | 7.824 | 276 | 35.2761
5.8 | 5.0401 | 1 | 7.824 | 276 | 35.2761
5.8 | 4.8138 | 1 | 7.824 | 276 | 35.2761
5.5 | 4.3923 | 1 | 7.824 | 276 | 35.2761
4.8 | 3.803 | 1 | 7.824 | 276 | 35.2761
4.3 | 3.4044 | 1 | 7.824 | 276 | 35.2761
3.9 | 2.7685 | 1 | 7.824 | 276 | 35.2761
3.3 | 2.0736 | 1 | 7.824 | 276 | 35.2761
3 | 1.7476 | 1 | 7.824 | 276 | 35.2761
2.7 | 1.5764 | 1 | 7.824 | 276 | 35.2761
2.6 | 1.3455 | 1 | 7.824 | 276 | 35.2761
2.2 | 1.1578 | 1 | 7.824 | 276 | 35.2761
1.8 | 0.88215 | 1 | 7.824 | 276 | 35.2761
1.7 | 0.7805 | 1 | 7.824 | 276 | 35.2761
1.5 | 0.70693 | 1 | 7.824 | 276 | 35.2761
1.4 | 0.69215 | 1 | 7.824 | 276 | 35.2761
1.3 | 0.72214 | 1 | 7.824 | 276 | 35.2761
1.4 | 0.82525 | 1 | 7.824 | 276 | 35.2761
1.3 | 0.72214 | 1 | 7.824 | 276 | 35.2761
1.4 | 0.82525 | 1 | 7.824 | 276 | 35.2761
1.5 | 0.92365 | 1 | 7.824 | 276 | 35.2761
1.6 | 1.0218 | 1 | 7.824 | 276 | 35.2761
1.8 | 1.1378 | 1 | 7.824 | 276 | 35.2761
1.9 | 1.235 | 1 | 7.824 | 276 | 35.2761
2.1 | 1.4301 | 1 | 7.824 | 276 | 35.2761
2.2 | 1.4078 | 1 | 7.824 | 276 | 35.2761
2.4 | 1.602 | 1 | 7.824 | 276 | 35.2761
2.2 | 1.4078 | 1 | 7.824 | 276 | 35.2761
2.2 | 1.4078 | 1 | 7.824 | 276 | 35.2761
2.1 | 1.4301 | 1 | 7.824 | 276 | 35.2761
2.3 | 1.7475 | 1 | 7.824 | 276 | 35.2761
2.2 | 1.7318 | 1 | 7.824 | 276 | 35.2761
2.5 | 2.0687 | 1 | 7.824 | 276 | 35.2761
2.6 | 2.1672 | 1 | 7.824 | 276 | 35.2761
2.6 | 2.3809 | 1 | 7.824 | 276 | 35.2761
2.6 | 2.4678 | 1 | 7.824 | 276 | 35.2761
2.8 | 2.6668 | 1 | 7.824 | 276 | 35.2761
3 | 2.8659 | 1 | 7.824 | 276 | 35.2761
3.4 | 3.3092 | 1 | 7.824 | 276 | 35.2761
3.9 | 3.6706 | 1 | 7.824 | 276 | 35.2761
4 | 3.7698 | 1 | 7.824 | 276 | 35.2761
4.8 | 4.4708 | 1 | 7.824 | 276 | 35.2761
5.7 | 5.2664 | 1 | 7.824 | 276 | 35.2761
6.6 | 6.0576 | 1 | 7.824 | 276 | 35.2761
6.8 | 6.2542 | 1 | 7.824 | 276 | 35.2761
7.6 | 6.6995 | 1 | 7.824 | 276 | 35.2761
8.4 | 7.1862 | 1 | 7.824 | 276 | 35.2761
9.1 | 8.2093 | 1 | 7.824 | 276 | 35.2761
9.6 | 8.5944 | 1 | 7.824 | 276 | 35.2761
10.2 | 8.871 | 1 | 7.824 | 276 | 35.2761
10.1 | 8.5755 | 1 | 7.824 | 276 | 35.2761
9.9 | 8.4819 | 1 | 7.824 | 276 | 35.2761
9.9 | 8.4819 | 1 | 7.824 | 276 | 35.2761
9.8 | 8.3858 | 1 | 7.824 | 276 | 35.2761
9.9 | 8.3343 | 1 | 7.824 | 276 | 35.2761
10.1 | 8.5748 | 1 | 7.824 | 276 | 35.2761
10.1 | 8.5741 | 1 | 7.824 | 276 | 35.2761
9.9 | 8.5807 | 1 | 7.824 | 276 | 35.2761
10 | 8.6765 | 1 | 7.824 | 276 | 35.2761
10.1 | 8.7722 | 1 | 7.824 | 276 | 35.2761
10.1 | 8.7722 | 1 | 7.824 | 276 | 35.2761
10 | 8.7767 | 1 | 7.824 | 276 | 35.2761
9.9 | 8.6795 | 1 | 7.824 | 276 | 35.2761
10.3 | 8.6644 | 1 | 7.824 | 276 | 35.2761
10.3 | 8.7635 | 1 | 7.824 | 276 | 35.2761
10.1 | 8.8728 | 1 | 7.824 | 276 | 35.2761
10.2 | 8.9688 | 1 | 7.824 | 276 | 35.2761
10.4 | 9.3174 | 1 | 7.824 | 276 | 35.2761
10.4 | 9.4216 | 1 | 7.824 | 276 | 35.2761
11.1 | 9.7879 | 1 | 7.824 | 276 | 35.2761
11.6 | 9.9575 | 1 | 7.824 | 276 | 35.2761
11.7 | 10.0532 | 1 | 7.824 | 276 | 35.2761
11.9 | 10.0389 | 1 | 7.824 | 276 | 35.2761
11.8 | 9.9438 | 1 | 7.824 | 276 | 35.2761
11.8 | 9.9438 | 1 | 7.824 | 276 | 35.2761
11.4 | 9.6137 | 1 | 7.824 | 276 | 35.2761
11.2 | 9.524 | 1 | 7.824 | 276 | 35.2761
10.5 | 9.3109 | 1 | 7.824 | 276 | 35.2761
9.9 | 8.8832 | 1 | 7.824 | 276 | 35.2761
9.7 | 8.7914 | 1 | 7.824 | 276 | 35.2761
9.6 | 8.8488 | 1 | 7.824 | 276 | 35.2761
9.9 | 9.1426 | 1 | 7.824 | 276 | 35.2761
10 | 9.2402 | 1 | 7.824 | 276 | 35.2761
9.6 | 8.8481 | 1 | 7.824 | 276 | 35.2761
9.6 | 8.8481 | 1 | 7.824 | 276 | 35.2761
10.2 | 8.9666 | 1 | 7.824 | 276 | 35.2761
10.1 | 8.9717 | 1 | 7.824 | 276 | 35.2761
9.8 | 8.7823 | 1 | 7.824 | 276 | 35.2761
9.6 | 8.6897 | 1 | 7.824 | 276 | 35.2761
9.6 | 9.0564 | 1 | 7.824 | 276 | 35.2761
10 | 9.5583 | 1 | 7.824 | 276 | 35.2761
10.4 | 9.8441 | 1 | 7.824 | 276 | 35.2761
11.1 | 10.2047 | 1 | 7.824 | 276 | 35.2761
10.9 | 9.7951 | 1 | 7.824 | 276 | 35.2761
10.1 | 8.8637 | 1 | 7.824 | 276 | 35.2761
9.7 | 8.5783 | 1 | 7.824 | 276 | 35.2761
10.3 | 8.7515 | 1 | 7.824 | 276 | 35.2761
10.3 | 8.3079 | 1 | 7.824 | 276 | 35.2761
10 | 7.8831 | 1 | 7.824 | 276 | 35.2761
9.2 | 6.8594 | 1 | 7.824 | 276 | 35.2761
8.6 | 6.5685 | 1 | 7.824 | 276 | 35.2761
8.2 | 6.2821 | 1 | 7.824 | 276 | 35.2761
7.9 | 6.0004 | 1 | 7.824 | 276 | 35.2761
7.6 | 5.673 | 1 | 7.824 | 276 | 35.2761
7.4 | 5.4859 | 1 | 7.824 | 276 | 35.2761
7 | 5.067 | 1 | 7.824 | 276 | 35.2761
7.5 | 5.2378 | 1 | 7.824 | 276 | 35.2761
7 | 4.9831 | 1 | 7.824 | 276 | 35.2761
6.5 | 4.6828 | 1 | 7.824 | 276 | 35.2761
6.3 | 4.3683 | 1 | 7.824 | 276 | 35.2761
6.6 | 4.9045 | 1 | 7.824 | 276 | 35.2761
7.3 | 5.5219 | 1 | 7.824 | 276 | 35.2761
7.5 | 5.7099 | 1 | 7.824 | 276 | 35.2761
7.2 | 5.7381 | 1 | 7.824 | 276 | 35.2761
7.3 | 5.8321 | 1 | 7.824 | 276 | 35.2761
7.1 | 6.1041 | 1 | 7.824 | 276 | 35.2761
6.9 | 6.2453 | 1 | 7.824 | 276 | 35.2761
6.5 | 6.2965 | 1 | 7.824 | 276 | 35.2761
6.6 | 6.2448 | 1 | 7.824 | 276 | 35.2761
5.9 | 5.4552 | 1 | 7.824 | 276 | 35.2761
6.2 | 5.2751 | 1 | 7.824 | 276 | 35.2761
6.7 | 5.5745 | 1 | 7.824 | 276 | 35.2761
6.8 | 4.9998 | 1 | 7.824 | 276 | 35.2761
6.5 | 4.103 | 1 | 7.824 | 276 | 35.2761
4.9 | 3.4177 | 1 | 7.824 | 276 | 35.2761
4.9 | 3.4185 | 1 | 7.824 | 276 | 35.2761
5.9 | 2.9177 | 1 | 7.824 | 276 | 35.2761
6.1 | 3.1096 | 1 | 7.824 | 276 | 35.2761
5.3 | 2.7984 | 1 | 7.824 | 276 | 35.2761
4.8 | 2.5245 | 1 | 7.824 | 276 | 35.2761
4.1 | 2.1378 | 1 | 7.824 | 276 | 35.2761
3.7 | 1.7064 | 1 | 7.824 | 276 | 35.2761
3.2 | 1.7178 | 1 | 7.824 | 276 | 35.2761
1.2 | 0.48058 | 1 | 7.824 | 276 | 35.2761
1.9 | 0.97541 | 1 | 7.824 | 276 | 35.2761
2.6 | 1.7082 | 1 | 7.824 | 276 | 35.2761
3.2 | 2.0856 | 1 | 7.824 | 276 | 35.2761
2.9 | 1.877 | 1 | 7.824 | 276 | 35.2761
4.3 | 2.9364 | 1 | 7.824 | 276 | 35.2761
5.6 | 3.8012 | 1 | 7.824 | 276 | 35.2761
5.8 | 4.113 | 1 | 7.824 | 276 | 35.2761
6.5 | 4.6055 | 1 | 7.824 | 276 | 35.2761
7.1 | 5.0829 | 1 | 7.824 | 276 | 35.2761
7.3 | 5.3986 | 1 | 7.824 | 276 | 35.2761
7.3 | 5.5282 | 1 | 7.824 | 276 | 35.2761
7.3 | 5.7492 | 1 | 7.824 | 276 | 35.2761
7.5 | 5.805 | 1 | 7.824 | 276 | 35.2761
7.4 | 5.9343 | 1 | 7.824 | 276 | 35.2761
7 | 5.7797 | 1 | 7.824 | 276 | 35.2761
7 | 5.779 | 1 | 7.824 | 276 | 35.2761
7.2 | 5.9709 | 1 | 7.824 | 276 | 35.2761
6.9 | 5.8677 | 1 | 7.824 | 276 | 35.2761
6.4 | 5.2912 | 1 | 7.824 | 276 | 35.2761
5.8 | 5.2176 | 1 | 7.824 | 276 | 35.2761
4.9 | 3.9746 | 1 | 7.824 | 276 | 35.2761
4.5 | 3.9411 | 1 | 7.824 | 276 | 35.2761
4.4 | 3.7086 | 1 | 7.824 | 276 | 35.2761
4 | 3.101 | 1 | 7.824 | 276 | 35.2761
4.1 | 3.1979 | 1 | 7.824 | 276 | 35.2761
4.3 | 3.3918 | 1 | 7.824 | 276 | 35.2761
4.6 | 3.4678 | 1 | 7.824 | 276 | 35.2761
4.9 | 3.4201 | 1 | 7.824 | 276 | 35.2761
4.7 | 2.871 | 1 | 7.824 | 276 | 35.2761
4.5 | 1.9125 | 1 | 7.824 | 276 | 35.2761
4.3 | 1.0682 | 1 | 7.824 | 276 | 35.2761
5 | 1.7154 | 1 | 7.824 | 276 | 35.2761
5.7 | 1.9389 | 1 | 7.824 | 276 | 35.2761
4.9 | 1.592 | 1 | 7.824 | 276 | 35.2761
6.1 | 2.6248 | 1 | 7.824 | 276 | 35.2761
6.1 | 2.3758 | 1 | 7.824 | 276 | 35.2761
5.8 | 2.0717 | 1 | 7.824 | 276 | 35.2761
5 | 1.7266 | 1 | 7.824 | 276 | 35.2761
3.7 | 1.2418 | 1 | 7.824 | 276 | 35.2761
2.9 | 1.0142 | 1 | 7.824 | 276 | 35.2761
2.9 | 1.1356 | 1 | 7.824 | 276 | 35.2761
1.8 | 0.49651 | 1 | 7.824 | 276 | 35.2761
1.5 | 0.44535 | 1 | 7.824 | 276 | 35.2761
1.1 | 0.0014612 | 1 | 7.824 | 276 | 35.2761
0.9 | -0.071365 | 1 | 7.824 | 276 | 35.2761
1.3 | 0.20326 | 1 | 7.824 | 276 | 35.2761
1.3 | 0.32879 | 1 | 7.824 | 276 | 35.2761
1 | 0.15143 | 1 | 7.824 | 276 | 35.2761
0 | -0.58466 | 1 | 7.824 | 276 | 35.2761
-0.7 | -1.1103 | 1 | 7.824 | 276 | 35.2761
-1.7 | -2.0159 | 1 | 7.824 | 276 | 35.2761
-2.6 | -2.9761 | 1 | 7.824 | 276 | 35.2761
-0.4 | -1.0141 | 1 | 7.824 | 276 | 35.2761
-0.5 | -0.87369 | 1 | 7.824 | 276 | 35.2761
1.1 | -0.15196 | 1 | 7.824 | 276 | 35.2761
1.5 | 0.57362 | 1 | 7.824 | 276 | 35.2761
3.6 | 1.2657 | 1 | 7.824 | 276 | 35.2761
4.8 | 2.0237 | 1 | 7.824 | 276 | 35.2761
5.6 | 2.2128 | 1 | 7.824 | 276 | 35.2761
6.1 | 3.2528 | 1 | 7.824 | 276 | 35.2761
6.1 | 3.7597 | 1 | 7.824 | 276 | 35.2761
5.7 | 3.4675 | 1 | 7.824 | 276 | 35.2761
5.5 | 3.4745 | 1 | 7.824 | 276 | 35.2761
5.3 | 3.486 | 1 | 7.824 | 276 | 35.2761
5 | 3.5263 | 1 | 7.824 | 276 | 35.2761
5.5 | 3.8359 | 1 | 7.824 | 276 | 35.2761
5.3 | 3.9362 | 1 | 7.824 | 276 | 35.2761
4.6 | 3.4763 | 1 | 7.824 | 276 | 35.2761
4 | 2.9821 | 1 | 7.824 | 276 | 35.2761
3.1 | 2.3182 | 1 | 7.824 | 276 | 35.2761
2.3 | 1.9535 | 1 | 7.824 | 276 | 35.2761
1.8 | 1.4597 | 1 | 7.824 | 276 | 35.2761
1.7 | 1.4865 | 1 | 7.824 | 276 | 35.2761
1.9 | 1.6851 | 1 | 7.824 | 276 | 35.2761
2.2 | 2.069 | 1 | 7.824 | 276 | 35.2761
2.3 | 2.0822 | 1 | 7.824 | 276 | 35.2761
2.6 | 2.4673 | 1 | 7.824 | 276 | 35.2761
2.7 | 2.3498 | 1 | 7.824 | 276 | 35.2761
2.1 | 1.8842 | 1 | 7.824 | 276 | 35.2761
1.8 | 1.5866 | 1 | 7.824 | 276 | 35.2761
2 | 1.659 | 1 | 7.824 | 276 | 35.2761
2.6 | 2.2516 | 1 | 7.824 | 276 | 35.2761
3.3 | 2.7271 | 1 | 7.824 | 276 | 35.2761
3.8 | 3.1308 | 1 | 7.824 | 276 | 35.2761
4.2 | 3.4349 | 1 | 7.824 | 276 | 35.2761
4.1 | 3.21 | 1 | 7.824 | 276 | 35.2761
3.7 | 2.9483 | 1 | 7.824 | 276 | 35.2761
2.3 | 1.9555 | 1 | 7.824 | 276 | 35.2761
2.6 | 2.1669 | 1 | 7.824 | 276 | 35.2761
2 | 1.6591 | 1 | 7.824 | 276 | 35.2761
2.1 | 1.633 | 1 | 7.824 | 276 | 35.2761
2.2 | 1.6486 | 1 | 7.824 | 276 | 35.2761
1.9 | 1.4361 | 1 | 7.824 | 276 | 35.2761
1.7 | 1.2392 | 1 | 7.824 | 276 | 35.2761
2.2 | 1.6483 | 1 | 7.824 | 276 | 35.2761
3 | 2.3063 | 1 | 7.824 | 276 | 35.2761
4.2 | 3.5202 | 1 | 7.824 | 276 | 35.2761
4.8 | 4.3316 | 1 | 7.824 | 276 | 35.2761
5.5 | 5.0676 | 1 | 7.824 | 276 | 35.2761
6.3 | 5.6176 | 1 | 7.824 | 276 | 35.2761
6.9 | 6.2528 | 1 | 7.824 | 276 | 35.2761
7.3 | 6.6447 | 1 | 7.824 | 276 | 35.2761
7.8 | 7.0356 | 1 | 7.824 | 276 | 35.2761
8.3 | 7.5241 | 1 | 7.824 | 276 | 35.2761
8.8 | 8.013 | 1 | 7.824 | 276 | 35.2761
9.5 | 8.5939 | 1 | 7.824 | 276 | 35.2761
10.3 | 9.4263 | 1 | 7.824 | 276 | 35.2761
11 | 9.8961 | 1 | 7.824 | 276 | 35.2761
11.6 | 10.2654 | 1 | 7.824 | 276 | 35.2761
10.8 | 9.8077 | 1 | 7.824 | 276 | 35.2761
11.4 | 10.1786 | 1 | 7.824 | 276 | 35.2761
10.9 | 9.906 | 1 | 7.824 | 276 | 35.2761
11.2 | 9.9854 | 1 | 7.824 | 276 | 35.2761
11 | 10.1109 | 1 | 7.824 | 276 | 35.2761
11.8 | 10.3544 | 1 | 7.824 | 276 | 35.2761
11.5 | 10.1712 | 1 | 7.824 | 276 | 35.2761
10.8 | 9.8095 | 1 | 7.824 | 276 | 35.2761
11.1 | 9.9947 | 1 | 7.824 | 276 | 35.2761
11.2 | 9.9859 | 1 | 7.824 | 276 | 35.2761
11.4 | 10.2861 | 1 | 7.824 | 276 | 35.2761
10.6 | 9.6133 | 1 | 7.824 | 276 | 35.2761
11.3 | 9.7681 | 1 | 7.824 | 276 | 35.2761
11.4 | 8.9669 | 1 | 7.824 | 276 | 35.2761
10.8 | 8.2668 | 1 | 7.824 | 276 | 35.2761
11 | 9.0277 | 1 | 7.824 | 276 | 35.2761
10.5 | 8.5061 | 1 | 7.824 | 276 | 35.2761
10.4 | 8.4116 | 1 | 7.824 | 276 | 35.2761
11.2 | 8.9721 | 1 | 7.824 | 276 | 35.2761
12.1 | 9.5719 | 1 | 7.824 | 276 | 35.2761
12.4 | 9.7529 | 1 | 7.824 | 276 | 35.2761
12.2 | 9.6641 | 1 | 7.824 | 276 | 35.2761
12 | 9.575 | 1 | 7.824 | 276 | 35.2761
11.8 | 9.3879 | 1 | 7.824 | 276 | 35.2761
11.6 | 9.298 | 1 | 7.824 | 276 | 35.2761
11.6 | 9.0566 | 1 | 7.824 | 276 | 35.2761
11.5 | 8.8217 | 1 | 7.824 | 276 | 35.2761
11.1 | 8.4512 | 1 | 7.824 | 276 | 35.2761
11.1 | 8.2206 | 1 | 7.824 | 276 | 35.2761
11.1 | 8.2206 | 1 | 7.824 | 276 | 35.2761
10.9 | 7.7704 | 1 | 7.824 | 276 | 35.2761
10.7 | 7.5868 | 1 | 7.824 | 276 | 35.2761
10.7 | 7.6743 | 1 | 7.824 | 276 | 35.2761
10.7 | 7.4556 | 1 | 7.824 | 276 | 35.2761
10.1 | 7.9822 | 1 | 7.824 | 276 | 35.2761
9.9 | 7.6546 | 1 | 7.824 | 276 | 35.2761
9.6 | 6.797 | 1 | 7.824 | 276 | 35.2761
8.4 | 5.495 | 1 | 7.824 | 276 | 35.2761
8.1 | 5.1811 | 1 | 7.824 | 276 | 35.2761
7.8 | 5.1074 | 1 | 7.824 | 276 | 35.2761
7.8 | 5.4357 | 1 | 7.824 | 276 | 35.2761
7.9 | 5.8712 | 1 | 7.824 | 276 | 35.2761
8.2 | 5.9765 | 1 | 7.824 | 276 | 35.2761
9.1 | 6.421 | 1 | 7.824 | 276 | 35.2761
9.7 | 7.1476 | 1 | 7.824 | 276 | 35.2761
9.9 | 7.3302 | 1 | 7.824 | 276 | 35.2761
10 | 8.2157 | 1 | 7.824 | 276 | 35.2761
9.9 | 8.8725 | 1 | 7.824 | 276 | 35.2761
11 | 9.3155 | 1 | 7.824 | 276 | 35.2761
9.9 | 7.7821 | 1 | 7.824 | 276 | 35.2761
9.2 | 6.8502 | 1 | 7.824 | 276 | 35.2761
8.2 | 5.832 | 1 | 7.824 | 276 | 35.2761
7.7 | 5.4532 | 1 | 7.824 | 276 | 35.2761
7.2 | 5.5069 | 1 | 7.824 | 276 | 35.2761
6.2 | 4.6033 | 1 | 7.824 | 276 | 35.2761
5.1 | 3.7277 | 1 | 7.824 | 276 | 35.2761
4.4 | 2.9362 | 1 | 7.824 | 276 | 35.2761
3.5 | 2.1207 | 1 | 7.824 | 276 | 35.2761
3.3 | 1.9303 | 1 | 7.824 | 276 | 35.2761
3.5 | 2.3624 | 1 | 7.824 | 276 | 35.2761
3.2 | 2.1556 | 1 | 7.824 | 276 | 35.2761
2.8 | 1.7702 | 1 | 7.824 | 276 | 35.2761
2.3 | 1.4894 | 1 | 7.824 | 276 | 35.2761
2.3 | 1.3686 | 1 | 7.824 | 276 | 35.2761
1.8 | 0.86449 | 1 | 7.824 | 276 | 35.2761
1.7 | 0.89663 | 1 | 7.824 | 276 | 35.2761
2.9 | 1.7481 | 1 | 7.824 | 276 | 35.2761
4.5 | 2.4288 | 1 | 7.824 | 276 | 35.2761
4.3 | 2.3613 | 1 | 7.824 | 276 | 35.2761
4.6 | 2.6517 | 1 | 7.824 | 276 | 35.2761
4.5 | 2.4288 | 1 | 7.824 | 276 | 35.2761
3.9 | 2.3063 | 1 | 7.824 | 276 | 35.2761
3.6 | 2.1007 | 1 | 7.824 | 276 | 35.2761
2.5 | 0.68164 | 1 | 7.824 | 276 | 35.2761
1.9 | 0.33375 | 1 | 7.824 | 276 | 35.2761
0.7 | -0.43177 | 1 | 7.824 | 276 | 35.2761
-0.7 | -1.7639 | 1 | 7.824 | 276 | 35.2761
-0.2 | -1.0613 | 1 | 7.824 | 276 | 35.2761
-1 | -1.6434 | 1 | 7.824 | 276 | 35.2761
-0.6 | -1.4839 | 1 | 7.824 | 276 | 35.2761
-1.9 | -2.4805 | 1 | 7.824 | 276 | 35.2761
-1.5 | -2.0536 | 1 | 7.824 | 276 | 35.2761
-2 | -2.5775 | 1 | 7.824 | 276 | 35.2761
-2.2 | -2.7718 | 1 | 7.824 | 276 | 35.2761
-1.9 | -2.3683 | 1 | 7.824 | 276 | 35.2761
-1.5 | -2.0529 | 1 | 7.824 | 276 | 35.2761
-0.8 | -1.4476 | 1 | 7.824 | 276 | 35.2761
-1.8 | -2.2699 | 1 | 7.824 | 276 | 35.2761
-1.8 | -2.1169 | 1 | 7.824 | 276 | 35.2761
-1.3 | -1.7415 | 1 | 7.824 | 276 | 35.2761
0.1 | -0.61177 | 1 | 7.824 | 276 | 35.2761
1.5 | -0.19456 | 1 | 7.824 | 276 | 35.2761
3.7 | 1.9986 | 1 | 7.824 | 276 | 35.2761
4.3 | 1.8447 | 1 | 7.824 | 276 | 35.2761
4.5 | 2.1982 | 1 | 7.824 | 276 | 35.2761
4.1 | 2.14 | 1 | 7.824 | 276 | 35.2761
3.2 | 1.5923 | 1 | 7.824 | 276 | 35.2761
2.3 | 0.90855 | 1 | 7.824 | 276 | 35.2761
1.8 | 0.6178 | 1 | 7.824 | 276 | 35.2761
1.5 | 0.57093 | 1 | 7.824 | 276 | 35.2761
1.4 | 0.17659 | 1 | 7.824 | 276 | 35.2761
0.4 | -0.62957 | 1 | 7.824 | 276 | 35.2761
-0.4 | -1.0541 | 1 | 7.824 | 276 | 35.2761
-1.3 | -1.8151 | 1 | 7.824 | 276 | 35.2761
0 | -0.70467 | 1 | 7.824 | 276 | 35.2761
-2 | -2.3498 | 1 | 7.824 | 276 | 35.2761
-2.5 | -2.7301 | 1 | 7.824 | 276 | 35.2761
-0.7 | -1.3448 | 1 | 7.824 | 276 | 35.2761
-1.3 | -1.7384 | 1 | 7.824 | 276 | 35.2761
-0.8 | -1.3268 | 1 | 7.824 | 276 | 35.2761
-1.4 | -1.9502 | 1 | 7.824 | 276 | 35.2761
-1.1 | -1.6192 | 1 | 7.824 | 276 | 35.2761
-1.6 | -1.9173 | 1 | 7.824 | 276 | 35.2761
-1.3 | -1.7381 | 1 | 7.824 | 276 | 35.2761
0.3 | -0.41303 | 1 | 7.824 | 276 | 35.2761
2.1 | 1.1838 | 1 | 7.824 | 276 | 35.2761
4 | 2.421 | 1 | 7.824 | 276 | 35.2761
4.9 | 3.1115 | 1 | 7.824 | 276 | 35.2761
5 | 2.9716 | 1 | 7.824 | 276 | 35.2761
4.5 | 2.6955 | 1 | 7.824 | 276 | 35.2761
4.5 | 2.3275 | 1 | 7.824 | 276 | 35.2761
3.6 | 1.863 | 1 | 7.824 | 276 | 35.2761
3.5 | 2.0205 | 1 | 7.824 | 276 | 35.2761
3.9 | 2.6782 | 1 | 7.824 | 276 | 35.2761
4.5 | 3.2508 | 1 | 7.824 | 276 | 35.2761
5.5 | 4.1655 | 1 | 7.824 | 276 | 35.2761
6.4 | 5.0691 | 1 | 7.824 | 276 | 35.2761
7.2 | 6.2066 | 1 | 7.824 | 276 | 35.2761
7.5 | 6.739 | 1 | 7.824 | 276 | 35.2761
8.1 | 7.2249 | 1 | 7.824 | 276 | 35.2761
7.9 | 7.2281 | 1 | 7.824 | 276 | 35.2761
4.8 | 4.4663 | 1 | 7.824 | 276 | 35.2761
4.1 | 3.866 | 1 | 7.824 | 276 | 35.2761
3.5 | 3.2707 | 1 | 7.824 | 276 | 35.2761
4.2 | 3.1673 | 1 | 7.824 | 276 | 35.2761
3.9 | 2.5499 | 1 | 7.824 | 276 | 35.2761
3 | 1.8506 | 1 | 7.824 | 276 | 35.2761
3 | 1.6013 | 1 | 7.824 | 276 | 35.2761
4 | 2.0377 | 1 | 7.824 | 276 | 35.2761
5.1 | 2.6912 | 1 | 7.824 | 276 | 35.2761
5.9 | 3.2945 | 1 | 7.824 | 276 | 35.2761
6.3 | 3.3471 | 1 | 7.824 | 276 | 35.2761
6.9 | 3.9873 | 1 | 7.824 | 276 | 35.2761
6.5 | 3.5382 | 1 | 7.824 | 276 | 35.2761
5.3 | 3.054 | 1 | 7.824 | 276 | 35.2761
4.7 | 2.5171 | 1 | 7.824 | 276 | 35.2761
4.1 | 2.2692 | 1 | 7.824 | 276 | 35.2761
4.1 | 2.2702 | 1 | 7.824 | 276 | 35.2761
3.4 | 1.7924 | 1 | 7.824 | 276 | 35.2761
3.9 | 2.44 | 1 | 7.824 | 276 | 35.2761
4.3 | 2.6245 | 1 | 7.824 | 276 | 35.2761
3.8 | 2.465 | 1 | 7.824 | 276 | 35.2761
2.2 | 1.4037 | 1 | 7.824 | 276 | 35.2761
2.9 | 2.0026 | 1 | 7.824 | 276 | 35.2761
3.4 | 2.2839 | 1 | 7.824 | 276 | 35.2761
3.4 | 2.4058 | 1 | 7.824 | 276 | 35.2761
1.9 | 1.4353 | 1 | 7.824 | 276 | 35.2761
3.2 | 2.4184 | 1 | 7.824 | 276 | 35.2761
2.6 | 1.9164 | 1 | 7.824 | 276 | 35.2761
2.7 | 2.0144 | 1 | 7.824 | 276 | 35.2761
2.7 | 2.0147 | 1 | 7.824 | 276 | 35.2761
2.4 | 1.7221 | 1 | 7.824 | 276 | 35.2761
3.3 | 2.4343 | 1 | 7.824 | 276 | 35.2761
4.8 | 3.508 | 1 | 7.824 | 276 | 35.2761
6.5 | 4.7053 | 1 | 7.824 | 276 | 35.2761
7 | 5.0916 | 1 | 7.824 | 276 | 35.2761
7.4 | 5.51 | 1 | 7.824 | 276 | 35.2761
7.7 | 5.7049 | 1 | 7.824 | 276 | 35.2761
7.7 | 6.0551 | 1 | 7.824 | 276 | 35.2761
7.7 | 6.0551 | 1 | 7.824 | 276 | 35.2761
7.5 | 6.1816 | 1 | 7.824 | 276 | 35.2761
8.1 | 6.4349 | 1 | 7.824 | 276 | 35.2761
8.5 | 7.0466 | 1 | 7.824 | 276 | 35.2761
9.5 | 8.199 | 1 | 7.824 | 276 | 35.2761
9.3 | 8.4051 | 1 | 7.824 | 276 | 35.2761
9.4 | 8.5026 | 1 | 7.824 | 276 | 35.2761
9.3 | 8.6616 | 1 | 7.824 | 276 | 35.2761
9.4 | 8.8643 | 1 | 7.824 | 276 | 35.2761
8.5 | 8.1838 | 1 | 7.824 | 276 | 35.2761
9.3 | 8.8708 | 1 | 7.824 | 276 | 35.2761
9.5 | 9.0684 | 1 | 7.824 | 276 | 35.2761
10.1 | 9.4476 | 1 | 7.824 | 276 | 35.2761
10.3 | 9.4326 | 1 | 7.824 | 276 | 35.2761
11.1 | 9.587 | 1 | 7.824 | 276 | 35.2761
10.9 | 9.5994 | 1 | 7.824 | 276 | 35.2761
11.3 | 9.0832 | 1 | 7.824 | 276 | 35.2761
11.5 | 9.079 | 1 | 7.824 | 276 | 35.2761
11.5 | 9.3197 | 1 | 7.824 | 276 | 35.2761
11.8 | 9.0748 | 1 | 7.824 | 276 | 35.2761
11.3 | 8.6572 | 1 | 7.824 | 276 | 35.2761
12.5 | 9.5321 | 1 | 7.824 | 276 | 35.2761
12.1 | 9.1178 | 1 | 7.824 | 276 | 35.2761
11.3 | 8.8912 | 1 | 7.824 | 276 | 35.2761
10.7 | 8.5187 | 1 | 7.824 | 276 | 35.2761
9.8 | 8.0489 | 1 | 7.824 | 276 | 35.2761
9.7 | 8.0495 | 1 | 7.824 | 276 | 35.2761
9.3 | 7.9569 | 1 | 7.824 | 276 | 35.2761
9.2 | 7.8601 | 1 | 7.824 | 276 | 35.2761
9 | 7.9123 | 1 | 7.824 | 276 | 35.2761
9.2 | 8.007 | 1 | 7.824 | 276 | 35.2761
10.2 | 8.5253 | 1 | 7.824 | 276 | 35.2761
9.9 | 8.3357 | 1 | 7.824 | 276 | 35.2761
10.1 | 8.3315 | 1 | 7.824 | 276 | 35.2761
9.5 | 7.9526 | 1 | 7.824 | 276 | 35.2761
9.9 | 8.0459 | 1 | 7.824 | 276 | 35.2761
10.5 | 8.2799 | 1 | 7.824 | 276 | 35.2761
10.6 | 8.5158 | 1 | 7.824 | 276 | 35.2761
10.7 | 9.1495 | 1 | 7.824 | 276 | 35.2761
10.2 | 9.5443 | 1 | 7.824 | 276 | 35.2761
10.5 | 9.8391 | 1 | 7.824 | 276 | 35.2761
10.9 | 9.9099 | 1 | 7.824 | 276 | 35.2761
11.5 | 9.9675 | 1 | 7.824 | 276 | 35.2761
11.5 | 9.9675 | 1 | 7.824 | 276 | 35.2761
11.8 | 9.846 | 1 | 7.824 | 276 | 35.2761
12.5 | 9.7645 | 1 | 7.824 | 276 | 35.2761
12.1 | 9.4413 | 1 | 7.824 | 276 | 35.2761
10.5 | 8.6144 | 1 | 7.824 | 276 | 35.2761
9.7 | 8.0479 | 1 | 7.824 | 276 | 35.2761
9.3 | 7.8591 | 1 | 7.824 | 276 | 35.2761
7.6 | 6.0481 | 1 | 7.824 | 276 | 35.2761
7.7 | 5.6153 | 1 | 7.824 | 276 | 35.2761
5.8 | 4.2058 | 1 | 7.824 | 276 | 35.2761
6 | 4.9583 | 1 | 7.824 | 276 | 35.2761
5.1 | 4.219 | 1 | 7.824 | 276 | 35.2761
3.8 | 3.1261 | 1 | 7.824 | 276 | 35.2761
|  |  | 27957.5734 | 276 | 0.0098721

## 3 Units Operational
UP4 - 4.080MW DATAHALL DIRECT AIR SOLUTION @ 100% LOAD - 3 DAO's OPERATIONAL
Drawing Reference - BRG - 0474 - UP4 - 02 - DR - A - 010201
2017 ASHRAE Handbook - Fundamentals (SI) |  | Annual Consumption Calculation Basics
LONDON HEATHROW, United Kingdom |  | Constant full year cooling load |  | [kW] | 552 | This IT load is based on 500 W/m2 Datahall Area 1105m2
Lat: | 51.478N
Long: | 0.461W | Qty. of units |  | (pcs.) | 3 | 3 Units at full load provide 680kW of cooling capacity each Based on a total load of 552KW 3 units would be operational at. 184W each.
Elev: | 150 | Resilience |  | (pcs.) | 0
|  | Supply Temperature |  | [°C ] | 26
|  | Return Temperature |  | [°C ] | 39
|  | Air Volume per DAO |  | [m3/s] | 14.1
|  | Design pressure |  | [Pa] | 83
|  | Filter Condition |  |  | Moderate
|  | All data per single unit |  | Average = | 64.4258
Dry bulb temperature | Wet Bulb Temperature | hours / year | Absorbed Power Total | Cooling per single unit | SEER per hour (Cooling / Power input)
°C | °C | h | kW
TOTALS
4 | 3.3648 | 1 | 2.856 | 184 | 64.4258
2 | 1.4482 | 1 | 2.856 | 184 | 64.4258
0.3 | -0.046933 | 1 | 2.856 | 184 | 64.4258
0 | -0.25849 | 1 | 2.856 | 184 | 64.4258
-0.3 | -0.55507 | 1 | 2.856 | 184 | 64.4258
-1 | -1.2876 | 1 | 2.856 | 184 | 64.4258
-0.4 | -0.65368 | 1 | 2.856 | 184 | 64.4258
0.7 | 0.36673 | 1 | 2.856 | 184 | 64.4258
0.8 | 0.20246 | 1 | 2.856 | 184 | 64.4258
1.7 | 1.1151 | 1 | 2.856 | 184 | 64.4258
3.1 | 2.072 | 1 | 2.856 | 184 | 64.4258
4.4 | 2.9538 | 1 | 2.856 | 184 | 64.4258
6 | 4.3055 | 1 | 2.856 | 184 | 64.4258
6.2 | 4.4098 | 1 | 2.856 | 184 | 64.4258
6 | 4.3046 | 1 | 2.856 | 184 | 64.4258
5.7 | 4.2307 | 1 | 2.856 | 184 | 64.4258
5.1 | 3.9549 | 1 | 2.856 | 184 | 64.4258
4.9 | 3.8907 | 1 | 2.856 | 184 | 64.4258
5.1 | 4.305 | 1 | 2.856 | 184 | 64.4258
5.4 | 4.5965 | 1 | 2.856 | 184 | 64.4258
5.7 | 4.7966 | 1 | 2.856 | 184 | 64.4258
5.8 | 5.0307 | 1 | 2.856 | 184 | 64.4258
5.6 | 4.9272 | 1 | 2.856 | 184 | 64.4258
5.5 | 4.9216 | 1 | 2.856 | 184 | 64.4258
6 | 5.4594 | 1 | 2.856 | 184 | 64.4258
6.6 | 6.147 | 1 | 2.856 | 184 | 64.4258
6.5 | 6.2967 | 1 | 2.856 | 184 | 64.4258
7 | 6.6413 | 1 | 2.856 | 184 | 64.4258
8.5 | 7.8136 | 1 | 2.856 | 184 | 64.4258
8.8 | 7.8017 | 1 | 2.856 | 184 | 64.4258
8.8 | 7.7014 | 1 | 2.856 | 184 | 64.4258
8.4 | 6.9267 | 1 | 2.856 | 184 | 64.4258
7.8 | 6.354 | 1 | 2.856 | 184 | 64.4258
8.4 | 6.6017 | 1 | 2.856 | 184 | 64.4258
8.8 | 6.6609 | 1 | 2.856 | 184 | 64.4258
9.4 | 7.597 | 1 | 2.856 | 184 | 64.4258
9 | 7.2185 | 1 | 2.856 | 184 | 64.4258
9.4 | 7.5979 | 1 | 2.856 | 184 | 64.4258
8.7 | 6.4358 | 1 | 2.856 | 184 | 64.4258
8.4 | 6.514 | 1 | 2.856 | 184 | 64.4258
8.3 | 6.5115 | 1 | 2.856 | 184 | 64.4258
7.5 | 6.0254 | 1 | 2.856 | 184 | 64.4258
7.4 | 5.9306 | 1 | 2.856 | 184 | 64.4258
6.8 | 5.5841 | 1 | 2.856 | 184 | 64.4258
6.9 | 5.6809 | 1 | 2.856 | 184 | 64.4258
6.5 | 5.3872 | 1 | 2.856 | 184 | 64.4258
6.9 | 5.544 | 1 | 2.856 | 184 | 64.4258
5.7 | 5.0255 | 1 | 2.856 | 184 | 64.4258
4.9 | 4.3337 | 1 | 2.856 | 184 | 64.4258
5.2 | 4.7681 | 1 | 2.856 | 184 | 64.4258
5 | 4.6647 | 1 | 2.856 | 184 | 64.4258
4.4 | 4.0709 | 1 | 2.856 | 184 | 64.4258
5.2 | 4.8622 | 1 | 2.856 | 184 | 64.4258
5.5 | 5.0636 | 1 | 2.856 | 184 | 64.4258
6 | 5.7512 | 1 | 2.856 | 184 | 64.4258
6.6 | 6.3968 | 1 | 2.856 | 184 | 64.4258
7.8 | 7.3315 | 1 | 2.856 | 184 | 64.4258
8.5 | 7.7129 | 1 | 2.856 | 184 | 64.4258
8.3 | 7.2667 | 1 | 2.856 | 184 | 64.4258
6.8 | 6.0013 | 1 | 2.856 | 184 | 64.4258
6.1 | 5.4113 | 1 | 2.856 | 184 | 64.4258
6.2 | 5.8489 | 1 | 2.856 | 184 | 64.4258
6.8 | 6.1453 | 1 | 2.856 | 184 | 64.4258
8 | 6.3059 | 1 | 2.856 | 184 | 64.4258
7.8 | 5.2853 | 1 | 2.856 | 184 | 64.4258
6.4 | 4.7445 | 1 | 2.856 | 184 | 64.4258
5.4 | 4.0542 | 1 | 2.856 | 184 | 64.4258
5.6 | 4.1167 | 1 | 2.856 | 184 | 64.4258
5.6 | 4.2469 | 1 | 2.856 | 184 | 64.4258
5 | 3.6308 | 1 | 2.856 | 184 | 64.4258
4.7 | 3.5566 | 1 | 2.856 | 184 | 64.4258
5 | 3.9765 | 1 | 2.856 | 184 | 64.4258
5.6 | 4.7837 | 1 | 2.856 | 184 | 64.4258
4.9 | 4.1018 | 1 | 2.856 | 184 | 64.4258
4.6 | 3.8992 | 1 | 2.856 | 184 | 64.4258
5.2 | 4.394 | 1 | 2.856 | 184 | 64.4258
5.4 | 4.7269 | 1 | 2.856 | 184 | 64.4258
5.2 | 4.303 | 1 | 2.856 | 184 | 64.4258
5.5 | 4.8244 | 1 | 2.856 | 184 | 64.4258
5.7 | 4.9263 | 1 | 2.856 | 184 | 64.4258
5.7 | 4.7876 | 1 | 2.856 | 184 | 64.4258
5.9 | 5.1214 | 1 | 2.856 | 184 | 64.4258
5.5 | 4.8241 | 1 | 2.856 | 184 | 64.4258
5.7 | 4.7871 | 1 | 2.856 | 184 | 64.4258
5.5 | 4.685 | 1 | 2.856 | 184 | 64.4258
5.7 | 5.0198 | 1 | 2.856 | 184 | 64.4258
5.5 | 4.3687 | 1 | 2.856 | 184 | 64.4258
5.1 | 4.0726 | 1 | 2.856 | 184 | 64.4258
4.9 | 4.2383 | 1 | 2.856 | 184 | 64.4258
5.5 | 4.7331 | 1 | 2.856 | 184 | 64.4258
4.7 | 3.9977 | 1 | 2.856 | 184 | 64.4258
3.5 | 2.8259 | 1 | 2.856 | 184 | 64.4258
2.5 | 1.9328 | 1 | 2.856 | 184 | 64.4258
2.5 | 1.9328 | 1 | 2.856 | 184 | 64.4258
2.9 | 2.3249 | 1 | 2.856 | 184 | 64.4258
3.7 | 3.1089 | 1 | 2.856 | 184 | 64.4258
3.9 | 3.2164 | 1 | 2.856 | 184 | 64.4258
3.8 | 3.1179 | 1 | 2.856 | 184 | 64.4258
4.4 | 3.93 | 1 | 2.856 | 184 | 64.4258
5 | 4.6618 | 1 | 2.856 | 184 | 64.4258
5.9 | 5.4542 | 1 | 2.856 | 184 | 64.4258
7.6 | 7.0289 | 1 | 2.856 | 184 | 64.4258
8.2 | 7.6185 | 1 | 2.856 | 184 | 64.4258
8.6 | 7.9074 | 1 | 2.856 | 184 | 64.4258
8.9 | 8.0972 | 1 | 2.856 | 184 | 64.4258
7.2 | 6.1925 | 1 | 2.856 | 184 | 64.4258
7.6 | 6.3403 | 1 | 2.856 | 184 | 64.4258
8.2 | 6.7259 | 1 | 2.856 | 184 | 64.4258
8.1 | 6.1657 | 1 | 2.856 | 184 | 64.4258
8.4 | 6.003 | 1 | 2.856 | 184 | 64.4258
7.7 | 5.4393 | 1 | 2.856 | 184 | 64.4258
6.3 | 4.6012 | 1 | 2.856 | 184 | 64.4258
5.9 | 3.8477 | 1 | 2.856 | 184 | 64.4258
5.5 | 3.4346 | 1 | 2.856 | 184 | 64.4258
4.7 | 2.8465 | 1 | 2.856 | 184 | 64.4258
4.3 | 2.5898 | 1 | 2.856 | 184 | 64.4258
4.5 | 2.5405 | 1 | 2.856 | 184 | 64.4258
3.9 | 2.4104 | 1 | 2.856 | 184 | 64.4258
4.4 | 3.2599 | 1 | 2.856 | 184 | 64.4258
4.6 | 4.0314 | 1 | 2.856 | 184 | 64.4258
4.5 | 3.9332 | 1 | 2.856 | 184 | 64.4258
3.9 | 3.2103 | 1 | 2.856 | 184 | 64.4258
4 | 3.308 | 1 | 2.856 | 184 | 64.4258
3.1 | 2.3005 | 1 | 2.856 | 184 | 64.4258
2.9 | 2.5382 | 1 | 2.856 | 184 | 64.4258
3.5 | 3.1762 | 1 | 2.856 | 184 | 64.4258
3.4 | 3.0772 | 1 | 2.856 | 184 | 64.4258
3.8 | 3.3815 | 1 | 2.856 | 184 | 64.4258
2.6 | 2.3746 | 1 | 2.856 | 184 | 64.4258
4.3 | 3.7375 | 1 | 2.856 | 184 | 64.4258
4.4 | 3.61 | 1 | 2.856 | 184 | 64.4258
4.6 | 3.895 | 1 | 2.856 | 184 | 64.4258
4.7 | 4.1298 | 1 | 2.856 | 184 | 64.4258
4.9 | 3.9616 | 1 | 2.856 | 184 | 64.4258
4.9 | 4.0966 | 1 | 2.856 | 184 | 64.4258
4.6 | 4.0317 | 1 | 2.856 | 184 | 64.4258
4.3 | 3.8287 | 1 | 2.856 | 184 | 64.4258
3 | 2.549 | 1 | 2.856 | 184 | 64.4258
1.6 | 1.2547 | 1 | 2.856 | 184 | 64.4258
0.5 | 0.37402 | 1 | 2.856 | 184 | 64.4258
0.6 | 0.47371 | 1 | 2.856 | 184 | 64.4258
1.6 | 1.2555 | 1 | 2.856 | 184 | 64.4258
1.6 | 1.1304 | 1 | 2.856 | 184 | 64.4258
0.9 | 0.29545 | 1 | 2.856 | 184 | 64.4258
0.5 | 0.017434 | 1 | 2.856 | 184 | 64.4258
-0.2 | -0.58603 | 1 | 2.856 | 184 | 64.4258
-0.7 | -0.99551 | 1 | 2.856 | 184 | 64.4258
-0.1 | -0.3605 | 1 | 2.856 | 184 | 64.4258
0.3 | -0.17813 | 1 | 2.856 | 184 | 64.4258
0.2 | -0.27559 | 1 | 2.856 | 184 | 64.4258
0.5 | -0.065762 | 1 | 2.856 | 184 | 64.4258
0.8 | 0.10668 | 1 | 2.856 | 184 | 64.4258
1.7 | 1.1079 | 1 | 2.856 | 184 | 64.4258
2 | 1.4431 | 1 | 2.856 | 184 | 64.4258
2.6 | 1.7816 | 1 | 2.856 | 184 | 64.4258
3.2 | 2.2813 | 1 | 2.856 | 184 | 64.4258
4 | 2.9709 | 1 | 2.856 | 184 | 64.4258
4.1 | 3.1954 | 1 | 2.856 | 184 | 64.4258
4.5 | 3.3685 | 1 | 2.856 | 184 | 64.4258
3.7 | 2.8938 | 1 | 2.856 | 184 | 64.4258
3 | 2.2974 | 1 | 2.856 | 184 | 64.4258
2.5 | 1.9351 | 1 | 2.856 | 184 | 64.4258
2.6 | 2.0334 | 1 | 2.856 | 184 | 64.4258
2.7 | 2.1314 | 1 | 2.856 | 184 | 64.4258
2.4 | 1.9642 | 1 | 2.856 | 184 | 64.4258
2.6 | 2.0341 | 1 | 2.856 | 184 | 64.4258
2.4 | 2.05 | 1 | 2.856 | 184 | 64.4258
2 | 1.5291 | 1 | 2.856 | 184 | 64.4258
0.5 | 0.24792 | 1 | 2.856 | 184 | 64.4258
0.2 | -0.061261 | 1 | 2.856 | 184 | 64.4258
-0.2 | -0.45689 | 1 | 2.856 | 184 | 64.4258
-0.7 | -0.86865 | 1 | 2.856 | 184 | 64.4258
-0.9 | -1.0672 | 1 | 2.856 | 184 | 64.4258
-1.5 | -1.5819 | 1 | 2.856 | 184 | 64.4258
-1.6 | -1.6815 | 1 | 2.856 | 184 | 64.4258
-0.8 | -0.96783 | 1 | 2.856 | 184 | 64.4258
-1 | -1.1664 | 1 | 2.856 | 184 | 64.4258
1.4 | 1.0629 | 1 | 2.856 | 184 | 64.4258
1.9 | 1.3493 | 1 | 2.856 | 184 | 64.4258
2.7 | 2.133 | 1 | 2.856 | 184 | 64.4258
4.2 | 3.5143 | 1 | 2.856 | 184 | 64.4258
4.8 | 4.0111 | 1 | 2.856 | 184 | 64.4258
4.7 | 4.138 | 1 | 2.856 | 184 | 64.4258
4.2 | 3.7371 | 1 | 2.856 | 184 | 64.4258
4 | 3.6757 | 1 | 2.856 | 184 | 64.4258
4.5 | 3.9416 | 1 | 2.856 | 184 | 64.4258
5 | 4.341 | 1 | 2.856 | 184 | 64.4258
5.5 | 4.9234 | 1 | 2.856 | 184 | 64.4258
5.8 | 5.2179 | 1 | 2.856 | 184 | 64.4258
6 | 5.4616 | 1 | 2.856 | 184 | 64.4258
6 | 5.4616 | 1 | 2.856 | 184 | 64.4258
6.2 | 5.7547 | 1 | 2.856 | 184 | 64.4258
6.3 | 5.7563 | 1 | 2.856 | 184 | 64.4258
6.3 | 5.6127 | 1 | 2.856 | 184 | 64.4258
6.3 | 5.8531 | 1 | 2.856 | 184 | 64.4258
6.1 | 5.8508 | 1 | 2.856 | 184 | 64.4258
6.3 | 6.0989 | 1 | 2.856 | 184 | 64.4258
7.2 | 6.8412 | 1 | 2.856 | 184 | 64.4258
7.7 | 7.2339 | 1 | 2.856 | 184 | 64.4258
7.7 | 7.3871 | 1 | 2.856 | 184 | 64.4258
8.3 | 7.8777 | 1 | 2.856 | 184 | 64.4258
9.2 | 8.4 | 1 | 2.856 | 184 | 64.4258
9.5 | 8.385 | 1 | 2.856 | 184 | 64.4258
9.6 | 8.4814 | 1 | 2.856 | 184 | 64.4258
9 | 7.8999 | 1 | 2.856 | 184 | 64.4258
8.2 | 7.5223 | 1 | 2.856 | 184 | 64.4258
8.4 | 7.516 | 1 | 2.856 | 184 | 64.4258
8.6 | 7.3632 | 1 | 2.856 | 184 | 64.4258
8.5 | 7.364 | 1 | 2.856 | 184 | 64.4258
8.7 | 7.4584 | 1 | 2.856 | 184 | 64.4258
8.8 | 7.5543 | 1 | 2.856 | 184 | 64.4258
8.5 | 7.7125 | 1 | 2.856 | 184 | 64.4258
8.4 | 7.8192 | 1 | 2.856 | 184 | 64.4258
8.7 | 8.1662 | 1 | 2.856 | 184 | 64.4258
8.9 | 8.4688 | 1 | 2.856 | 184 | 64.4258
8.5 | 8.1788 | 1 | 2.856 | 184 | 64.4258
8 | 7.5279 | 1 | 2.856 | 184 | 64.4258
7.5 | 7.395 | 1 | 2.856 | 184 | 64.4258
7.5 | 7.0346 | 1 | 2.856 | 184 | 64.4258
7.5 | 7.1875 | 1 | 2.856 | 184 | 64.4258
7 | 6.6415 | 1 | 2.856 | 184 | 64.4258
7 | 6.6415 | 1 | 2.856 | 184 | 64.4258
7 | 6.5411 | 1 | 2.856 | 184 | 64.4258
7.5 | 6.8336 | 1 | 2.856 | 184 | 64.4258
7.2 | 6.7386 | 1 | 2.856 | 184 | 64.4258
7.3 | 6.8373 | 1 | 2.856 | 184 | 64.4258
7.9 | 7.2259 | 1 | 2.856 | 184 | 64.4258
8 | 7.4254 | 1 | 2.856 | 184 | 64.4258
8.4 | 7.7162 | 1 | 2.856 | 184 | 64.4258
8.6 | 7.8099 | 1 | 2.856 | 184 | 64.4258
9.5 | 8.3802 | 1 | 2.856 | 184 | 64.4258
9.1 | 8.0938 | 1 | 2.856 | 184 | 64.4258
9 | 7.8957 | 1 | 2.856 | 184 | 64.4258
8.3 | 7.6185 | 1 | 2.856 | 184 | 64.4258
8.5 | 7.3629 | 1 | 2.856 | 184 | 64.4258
8.5 | 7.1678 | 1 | 2.856 | 184 | 64.4258
8.4 | 7.1691 | 1 | 2.856 | 184 | 64.4258
7.6 | 6.5891 | 1 | 2.856 | 184 | 64.4258
7.2 | 6.2974 | 1 | 2.856 | 184 | 64.4258
6.7 | 5.9061 | 1 | 2.856 | 184 | 64.4258
6.6 | 5.8085 | 1 | 2.856 | 184 | 64.4258
5.7 | 5.0237 | 1 | 2.856 | 184 | 64.4258
5.8 | 5.2158 | 1 | 2.856 | 184 | 64.4258
6 | 5.4602 | 1 | 2.856 | 184 | 64.4258
5.3 | 4.9608 | 1 | 2.856 | 184 | 64.4258
5.3 | 4.9609 | 1 | 2.856 | 184 | 64.4258
6 | 5.4607 | 1 | 2.856 | 184 | 64.4258
6.1 | 5.7526 | 1 | 2.856 | 184 | 64.4258
6.8 | 6.3459 | 1 | 2.856 | 184 | 64.4258
7.6 | 6.9346 | 1 | 2.856 | 184 | 64.4258
8.8 | 7.7066 | 1 | 2.856 | 184 | 64.4258
9.1 | 7.6517 | 1 | 2.856 | 184 | 64.4258
10.4 | 8.5004 | 1 | 2.856 | 184 | 64.4258
10.1 | 7.9761 | 1 | 2.856 | 184 | 64.4258
9.6 | 7.3664 | 1 | 2.856 | 184 | 64.4258
8.5 | 7.2667 | 1 | 2.856 | 184 | 64.4258
8.1 | 7.4236 | 1 | 2.856 | 184 | 64.4258
8.6 | 7.8118 | 1 | 2.856 | 184 | 64.4258
8.4 | 7.516 | 1 | 2.856 | 184 | 64.4258
8.3 | 7.2702 | 1 | 2.856 | 184 | 64.4258
8.2 | 7.3219 | 1 | 2.856 | 184 | 64.4258
7.6 | 6.6884 | 1 | 2.856 | 184 | 64.4258
7.1 | 5.8728 | 1 | 2.856 | 184 | 64.4258
7.3 | 6.159 | 1 | 2.856 | 184 | 64.4258
7.5 | 6.4001 | 1 | 2.856 | 184 | 64.4258
7.8 | 7.0315 | 1 | 2.856 | 184 | 64.4258
8.2 | 7.4226 | 1 | 2.856 | 184 | 64.4258
8.3 | 7.6211 | 1 | 2.856 | 184 | 64.4258
9 | 8.2041 | 1 | 2.856 | 184 | 64.4258
9.4 | 8.4918 | 1 | 2.856 | 184 | 64.4258
9.5 | 8.5889 | 1 | 2.856 | 184 | 64.4258
9.3 | 8.4967 | 1 | 2.856 | 184 | 64.4258
9.4 | 8.8571 | 1 | 2.856 | 184 | 64.4258
9.6 | 9.0539 | 1 | 2.856 | 184 | 64.4258
10.4 | 9.9521 | 1 | 2.856 | 184 | 64.4258
11.9 | 11.1515 | 1 | 2.856 | 184 | 64.4258
12.6 | 11.7245 | 1 | 2.856 | 184 | 64.4258
12.5 | 11.4022 | 1 | 2.856 | 184 | 64.4258
12.4 | 11.4159 | 1 | 2.856 | 184 | 64.4258
12.3 | 11.4301 | 1 | 2.856 | 184 | 64.4258
12.1 | 11.4606 | 1 | 2.856 | 184 | 64.4258
12.5 | 11.1806 | 1 | 2.856 | 184 | 64.4258
12.3 | 10.6108 | 1 | 2.856 | 184 | 64.4258
10.6 | 10.2608 | 1 | 2.856 | 184 | 64.4258
10.1 | 9.1197 | 1 | 2.856 | 184 | 64.4258
10.1 | 8.3091 | 1 | 2.856 | 184 | 64.4258
9.8 | 7.8805 | 1 | 2.856 | 184 | 64.4258
10 | 7.3294 | 1 | 2.856 | 184 | 64.4258
9.3 | 6.7274 | 1 | 2.856 | 184 | 64.4258
8.5 | 6.2494 | 1 | 2.856 | 184 | 64.4258
8 | 5.8724 | 1 | 2.856 | 184 | 64.4258
7.9 | 5.7799 | 1 | 2.856 | 184 | 64.4258
7.7 | 5.6806 | 1 | 2.856 | 184 | 64.4258
8.3 | 6.2887 | 1 | 2.856 | 184 | 64.4258
9 | 6.8556 | 1 | 2.856 | 184 | 64.4258
9 | 6.7668 | 1 | 2.856 | 184 | 64.4258
9.3 | 7.0481 | 1 | 2.856 | 184 | 64.4258
9.9 | 7.3364 | 1 | 2.856 | 184 | 64.4258
10.6 | 7.583 | 1 | 2.856 | 184 | 64.4258
10.8 | 7.5909 | 1 | 2.856 | 184 | 64.4258
11 | 7.6428 | 1 | 2.856 | 184 | 64.4258
11.4 | 7.9607 | 1 | 2.856 | 184 | 64.4258
11.1 | 7.5187 | 1 | 2.856 | 184 | 64.4258
10.4 | 7.6192 | 1 | 2.856 | 184 | 64.4258
7.1 | 6.2046 | 1 | 2.856 | 184 | 64.4258
7.4 | 5.8437 | 1 | 2.856 | 184 | 64.4258
7.6 | 5.4633 | 1 | 2.856 | 184 | 64.4258
7.4 | 5.1507 | 1 | 2.856 | 184 | 64.4258
6.9 | 4.8937 | 1 | 2.856 | 184 | 64.4258
6.9 | 5.1072 | 1 | 2.856 | 184 | 64.4258
6.4 | 4.5934 | 1 | 2.856 | 184 | 64.4258
6.1 | 4.3946 | 1 | 2.856 | 184 | 64.4258
6.2 | 4.6166 | 1 | 2.856 | 184 | 64.4258
6.3 | 4.4992 | 1 | 2.856 | 184 | 64.4258
6.3 | 4.6268 | 1 | 2.856 | 184 | 64.4258
6.1 | 4.3955 | 1 | 2.856 | 184 | 64.4258
5.7 | 4.2276 | 1 | 2.856 | 184 | 64.4258
5.9 | 4.2066 | 1 | 2.856 | 184 | 64.4258
6.1 | 4.3118 | 1 | 2.856 | 184 | 64.4258
6 | 4.301 | 1 | 2.856 | 184 | 64.4258
6.1 | 4.3128 | 1 | 2.856 | 184 | 64.4258
6.7 | 4.6681 | 1 | 2.856 | 184 | 64.4258
7.6 | 5.1331 | 1 | 2.856 | 184 | 64.4258
8.4 | 5.6222 | 1 | 2.856 | 184 | 64.4258
8.9 | 5.6744 | 1 | 2.856 | 184 | 64.4258
8.3 | 5.3701 | 1 | 2.856 | 184 | 64.4258
8.8 | 5.9053 | 1 | 2.856 | 184 | 64.4258
8.1 | 5.4293 | 1 | 2.856 | 184 | 64.4258
7.5 | 5.0422 | 1 | 2.856 | 184 | 64.4258
7.5 | 5.2482 | 1 | 2.856 | 184 | 64.4258
6.8 | 4.7636 | 1 | 2.856 | 184 | 64.4258
6.5 | 4.6075 | 1 | 2.856 | 184 | 64.4258
6.5 | 4.6913 | 1 | 2.856 | 184 | 64.4258
5.9 | 4.3352 | 1 | 2.856 | 184 | 64.4258
4.9 | 3.7625 | 1 | 2.856 | 184 | 64.4258
4.2 | 3.4296 | 1 | 2.856 | 184 | 64.4258
3.8 | 2.9972 | 1 | 2.856 | 184 | 64.4258
2.7 | 2.1349 | 1 | 2.856 | 184 | 64.4258
3.2 | 2.6246 | 1 | 2.856 | 184 | 64.4258
3.4 | 2.9508 | 1 | 2.856 | 184 | 64.4258
2.8 | 2.4462 | 1 | 2.856 | 184 | 64.4258
3.6 | 3.3709 | 1 | 2.856 | 184 | 64.4258
4.6 | 4.3632 | 1 | 2.856 | 184 | 64.4258
5.6 | 5.164 | 1 | 2.856 | 184 | 64.4258
5.7 | 5.3581 | 1 | 2.856 | 184 | 64.4258
6.1 | 5.561 | 1 | 2.856 | 184 | 64.4258
6.6 | 6.0524 | 1 | 2.856 | 184 | 64.4258
7.2 | 6.6425 | 1 | 2.856 | 184 | 64.4258
7.5 | 6.8379 | 1 | 2.856 | 184 | 64.4258
7.4 | 6.5925 | 1 | 2.856 | 184 | 64.4258
6.8 | 6.0069 | 1 | 2.856 | 184 | 64.4258
6.4 | 5.8552 | 1 | 2.856 | 184 | 64.4258
6.2 | 5.7549 | 1 | 2.856 | 184 | 64.4258
6.2 | 5.6585 | 1 | 2.856 | 184 | 64.4258
6.3 | 5.7568 | 1 | 2.856 | 184 | 64.4258
6.2 | 5.5155 | 1 | 2.856 | 184 | 64.4258
6 | 5.1802 | 1 | 2.856 | 184 | 64.4258
5.8 | 4.8937 | 1 | 2.856 | 184 | 64.4258
5.7 | 4.9339 | 1 | 2.856 | 184 | 64.4258
5.5 | 4.8311 | 1 | 2.856 | 184 | 64.4258
5.4 | 4.596 | 1 | 2.856 | 184 | 64.4258
4.9 | 4.2439 | 1 | 2.856 | 184 | 64.4258
4.8 | 4.237 | 1 | 2.856 | 184 | 64.4258
4.5 | 3.3746 | 1 | 2.856 | 184 | 64.4258
3.5 | 2.8315 | 1 | 2.856 | 184 | 64.4258
3.4 | 2.4816 | 1 | 2.856 | 184 | 64.4258
2.8 | 2.1065 | 1 | 2.856 | 184 | 64.4258
2.4 | 1.7167 | 1 | 2.856 | 184 | 64.4258
2.6 | 1.7894 | 1 | 2.856 | 184 | 64.4258
3.5 | 2.3756 | 1 | 2.856 | 184 | 64.4258
3.9 | 2.7598 | 1 | 2.856 | 184 | 64.4258
4.4 | 2.8339 | 1 | 2.856 | 184 | 64.4258
4.9 | 2.9905 | 1 | 2.856 | 184 | 64.4258
5 | 2.9683 | 1 | 2.856 | 184 | 64.4258
5 | 2.7272 | 1 | 2.856 | 184 | 64.4258
4.5 | 2.5793 | 1 | 2.856 | 184 | 64.4258
4 | 2.3014 | 1 | 2.856 | 184 | 64.4258
3.3 | 1.8225 | 1 | 2.856 | 184 | 64.4258
2.5 | 1.3672 | 1 | 2.856 | 184 | 64.4258
1.8 | 0.74653 | 1 | 2.856 | 184 | 64.4258
1.4 | 0.17659 | 1 | 2.856 | 184 | 64.4258
0.8 | -0.28664 | 1 | 2.856 | 184 | 64.4258
0.9 | -0.19066 | 1 | 2.856 | 184 | 64.4258
1.7 | 0.51942 | 1 | 2.856 | 184 | 64.4258
1.2 | 0.10008 | 1 | 2.856 | 184 | 64.4258
1.5 | 0.035267 | 1 | 2.856 | 184 | 64.4258
1.5 | 0.036128 | 1 | 2.856 | 184 | 64.4258
2 | 0.33185 | 1 | 2.856 | 184 | 64.4258
2.3 | 0.6275 | 1 | 2.856 | 184 | 64.4258
2.6 | 1.2126 | 1 | 2.856 | 184 | 64.4258
2.6 | 1.2134 | 1 | 2.856 | 184 | 64.4258
2.5 | 1.2422 | 1 | 2.856 | 184 | 64.4258
2.7 | 1.5745 | 1 | 2.856 | 184 | 64.4258
2.8 | 1.5885 | 1 | 2.856 | 184 | 64.4258
3.1 | 1.6314 | 1 | 2.856 | 184 | 64.4258
3.5 | 1.775 | 1 | 2.856 | 184 | 64.4258
4 | 1.9364 | 1 | 2.856 | 184 | 64.4258
4.4 | 2.2436 | 1 | 2.856 | 184 | 64.4258
4 | 1.8157 | 1 | 2.856 | 184 | 64.4258
3.5 | 1.653 | 1 | 2.856 | 184 | 64.4258
2.6 | 1.094 | 1 | 2.856 | 184 | 64.4258
1.5 | 0.16455 | 1 | 2.856 | 184 | 64.4258
0.4 | -0.80853 | 1 | 2.856 | 184 | 64.4258
0.7 | -0.14088 | 1 | 2.856 | 184 | 64.4258
-0.3 | -0.67482 | 1 | 2.856 | 184 | 64.4258
-2.1 | -2.9104 | 1 | 2.856 | 184 | 64.4258
-1 | -1.9954 | 1 | 2.856 | 184 | 64.4258
-0.6 | -1.5777 | 1 | 2.856 | 184 | 64.4258
-1.3 | -2.0335 | 1 | 2.856 | 184 | 64.4258
-0.6 | -1.5783 | 1 | 2.856 | 184 | 64.4258
-0.2 | -1.1591 | 1 | 2.856 | 184 | 64.4258
0 | -0.93015 | 1 | 2.856 | 184 | 64.4258
0.8 | -0.085009 | 1 | 2.856 | 184 | 64.4258
1 | -0.35289 | 1 | 2.856 | 184 | 64.4258
1.9 | -0.1604 | 1 | 2.856 | 184 | 64.4258
2.5 | 0.71299 | 1 | 2.856 | 184 | 64.4258
3.9 | 1.719 | 1 | 2.856 | 184 | 64.4258
4.5 | 2.3407 | 1 | 2.856 | 184 | 64.4258
5.6 | 3.1558 | 1 | 2.856 | 184 | 64.4258
5.8 | 3.6854 | 1 | 2.856 | 184 | 64.4258
6.6 | 4.4674 | 1 | 2.856 | 184 | 64.4258
7.2 | 4.8611 | 1 | 2.856 | 184 | 64.4258
7.4 | 5.1679 | 1 | 2.856 | 184 | 64.4258
7.5 | 5.2596 | 1 | 2.856 | 184 | 64.4258
7.5 | 5.3851 | 1 | 2.856 | 184 | 64.4258
7.6 | 5.6061 | 1 | 2.856 | 184 | 64.4258
8 | 5.7653 | 1 | 2.856 | 184 | 64.4258
8.1 | 6.1177 | 1 | 2.856 | 184 | 64.4258
7.7 | 6.3683 | 1 | 2.856 | 184 | 64.4258
7.5 | 6.7446 | 1 | 2.856 | 184 | 64.4258
7.5 | 6.842 | 1 | 2.856 | 184 | 64.4258
7.7 | 7.0382 | 1 | 2.856 | 184 | 64.4258
7.5 | 7.1916 | 1 | 2.856 | 184 | 64.4258
7.7 | 7.1375 | 1 | 2.856 | 184 | 64.4258
7 | 6.5472 | 1 | 2.856 | 184 | 64.4258
6.9 | 6.3504 | 1 | 2.856 | 184 | 64.4258
5.9 | 5.4619 | 1 | 2.856 | 184 | 64.4258
6.4 | 5.3907 | 1 | 2.856 | 184 | 64.4258
5.9 | 4.7731 | 1 | 2.856 | 184 | 64.4258
5.4 | 4.0762 | 1 | 2.856 | 184 | 64.4258
4.5 | 3.3825 | 1 | 2.856 | 184 | 64.4258
4.5 | 3.2582 | 1 | 2.856 | 184 | 64.4258
4.6 | 3.2715 | 1 | 2.856 | 184 | 64.4258
6.3 | 4.1861 | 1 | 2.856 | 184 | 64.4258
7.2 | 4.1638 | 1 | 2.856 | 184 | 64.4258
7.5 | 4.1319 | 1 | 2.856 | 184 | 64.4258
6.9 | 3.8952 | 1 | 2.856 | 184 | 64.4258
6.2 | 3.9747 | 1 | 2.856 | 184 | 64.4258
4.5 | 3.0558 | 1 | 2.856 | 184 | 64.4258
4.2 | 2.8507 | 1 | 2.856 | 184 | 64.4258
2.8 | 2.0298 | 1 | 2.856 | 184 | 64.4258
2.2 | 1.6489 | 1 | 2.856 | 184 | 64.4258
2.1 | 1.4294 | 1 | 2.856 | 184 | 64.4258
1.3 | 0.58885 | 1 | 2.856 | 184 | 64.4258
-0.2 | -1.049 | 1 | 2.856 | 184 | 64.4258
-0.4 | -1.012 | 1 | 2.856 | 184 | 64.4258
0.3 | -0.16826 | 1 | 2.856 | 184 | 64.4258
0.6 | 0.0014137 | 1 | 2.856 | 184 | 64.4258
1.1 | 0.0046775 | 1 | 2.856 | 184 | 64.4258
1.5 | 0.70602 | 1 | 2.856 | 184 | 64.4258
1.6 | 0.94103 | 1 | 2.856 | 184 | 64.4258
2 | 1.4529 | 1 | 2.856 | 184 | 64.4258
2.6 | 1.9172 | 1 | 2.856 | 184 | 64.4258
3.5 | 2.5865 | 1 | 2.856 | 184 | 64.4258
4.5 | 3.5974 | 1 | 2.856 | 184 | 64.4258
5.2 | 4.1886 | 1 | 2.856 | 184 | 64.4258
6.4 | 5.3948 | 1 | 2.856 | 184 | 64.4258
6.8 | 5.7821 | 1 | 2.856 | 184 | 64.4258
7.7 | 6.6059 | 1 | 2.856 | 184 | 64.4258
8.9 | 7.3341 | 1 | 2.856 | 184 | 64.4258
9.4 | 7.7636 | 1 | 2.856 | 184 | 64.4258
8 | 6.8961 | 1 | 2.856 | 184 | 64.4258
7.5 | 6.5074 | 1 | 2.856 | 184 | 64.4258
8.7 | 7.3806 | 1 | 2.856 | 184 | 64.4258
7.6 | 6.8452 | 1 | 2.856 | 184 | 64.4258
7.2 | 6.6482 | 1 | 2.856 | 184 | 64.4258
7.6 | 6.9426 | 1 | 2.856 | 184 | 64.4258
7.3 | 6.7465 | 1 | 2.856 | 184 | 64.4258
6.1 | 5.7571 | 1 | 2.856 | 184 | 64.4258
6.5 | 6.3003 | 1 | 2.856 | 184 | 64.4258
5.9 | 5.6555 | 1 | 2.856 | 184 | 64.4258
7 | 6.8982 | 1 | 2.856 | 184 | 64.4258
7.1 | 6.9979 | 1 | 2.856 | 184 | 64.4258
7.3 | 6.9444 | 1 | 2.856 | 184 | 64.4258
7.5 | 7.1926 | 1 | 2.856 | 184 | 64.4258
7.7 | 7.2393 | 1 | 2.856 | 184 | 64.4258
6.5 | 5.9592 | 1 | 2.856 | 184 | 64.4258
6.1 | 5.6133 | 1 | 2.856 | 184 | 64.4258
6.7 | 5.9179 | 1 | 2.856 | 184 | 64.4258
7.1 | 6.3083 | 1 | 2.856 | 184 | 64.4258
7.8 | 6.8459 | 1 | 2.856 | 184 | 64.4258
6.7 | 5.9176 | 1 | 2.856 | 184 | 64.4258
8.4 | 6.9502 | 1 | 2.856 | 184 | 64.4258
8.7 | 7.3799 | 1 | 2.856 | 184 | 64.4258
9.5 | 7.8581 | 1 | 2.856 | 184 | 64.4258
9.5 | 7.8581 | 1 | 2.856 | 184 | 64.4258
9.2 | 7.8601 | 1 | 2.856 | 184 | 64.4258
9 | 7.7655 | 1 | 2.856 | 184 | 64.4258
9.3 | 8.1042 | 1 | 2.856 | 184 | 64.4258
9.4 | 8.2008 | 1 | 2.856 | 184 | 64.4258
9.3 | 8.3037 | 1 | 2.856 | 184 | 64.4258
9 | 8.3153 | 1 | 2.856 | 184 | 64.4258
9.1 | 8.3111 | 1 | 2.856 | 184 | 64.4258
9.2 | 8.4089 | 1 | 2.856 | 184 | 64.4258
8.9 | 8.4753 | 1 | 2.856 | 184 | 64.4258
9.1 | 8.5684 | 1 | 2.856 | 184 | 64.4258
9.5 | 8.8578 | 1 | 2.856 | 184 | 64.4258
9.6 | 8.956 | 1 | 2.856 | 184 | 64.4258
9.6 | 8.8518 | 1 | 2.856 | 184 | 64.4258
9.6 | 8.9557 | 1 | 2.856 | 184 | 64.4258
9.8 | 8.9439 | 1 | 2.856 | 184 | 64.4258
9.9 | 9.0415 | 1 | 2.856 | 184 | 64.4258
10.1 | 9.4476 | 1 | 2.856 | 184 | 64.4258
10.6 | 9.7256 | 1 | 2.856 | 184 | 64.4258
11 | 9.9044 | 1 | 2.856 | 184 | 64.4258
10.5 | 9.7338 | 1 | 2.856 | 184 | 64.4258
10.6 | 9.9388 | 1 | 2.856 | 184 | 64.4258
10.3 | 9.0711 | 1 | 2.856 | 184 | 64.4258
10.9 | 9.3439 | 1 | 2.856 | 184 | 64.4258
10.1 | 8.0967 | 1 | 2.856 | 184 | 64.4258
7.8 | 6.3767 | 1 | 2.856 | 184 | 64.4258
7.5 | 6.181 | 1 | 2.856 | 184 | 64.4258
7.9 | 6.2458 | 1 | 2.856 | 184 | 64.4258
7.1 | 5.5294 | 1 | 2.856 | 184 | 64.4258
7 | 5.5661 | 1 | 2.856 | 184 | 64.4258
7.1 | 5.6616 | 1 | 2.856 | 184 | 64.4258
7.1 | 5.527 | 1 | 2.856 | 184 | 64.4258
7.7 | 6.4633 | 1 | 2.856 | 184 | 64.4258
9.4 | 8.5002 | 1 | 2.856 | 184 | 64.4258
10.6 | 9.6173 | 1 | 2.856 | 184 | 64.4258
10.9 | 9.9091 | 1 | 2.856 | 184 | 64.4258
11.1 | 9.9972 | 1 | 2.856 | 184 | 64.4258
11.5 | 10.1729 | 1 | 2.856 | 184 | 64.4258
11.7 | 10.1561 | 1 | 2.856 | 184 | 64.4258
11 | 10.1125 | 1 | 2.856 | 184 | 64.4258
10.6 | 9.9362 | 1 | 2.856 | 184 | 64.4258
10.4 | 9.8475 | 1 | 2.856 | 184 | 64.4258
10.6 | 9.8291 | 1 | 2.856 | 184 | 64.4258
11.1 | 9.5823 | 1 | 2.856 | 184 | 64.4258
11.1 | 9.3295 | 1 | 2.856 | 184 | 64.4258
11.1 | 9.2308 | 1 | 2.856 | 184 | 64.4258
11 | 7.665 | 1 | 2.856 | 184 | 64.4258
10.4 | 6.5217 | 1 | 2.856 | 184 | 64.4258
9.5 | 6.0751 | 1 | 2.856 | 184 | 64.4258
7.9 | 4.7963 | 1 | 2.856 | 184 | 64.4258
7.1 | 4.0786 | 1 | 2.856 | 184 | 64.4258
5.6 | 3.3454 | 1 | 2.856 | 184 | 64.4258
4.8 | 3.0234 | 1 | 2.856 | 184 | 64.4258
3.7 | 2.3355 | 1 | 2.856 | 184 | 64.4258
4.2 | 2.8522 | 1 | 2.856 | 184 | 64.4258
3.8 | 2.5504 | 1 | 2.856 | 184 | 64.4258
4.1 | 2.637 | 1 | 2.856 | 184 | 64.4258
3.9 | 2.5647 | 1 | 2.856 | 184 | 64.4258
4.1 | 2.8764 | 1 | 2.856 | 184 | 64.4258
4.5 | 3.3837 | 1 | 2.856 | 184 | 64.4258
4.3 | 3.5307 | 1 | 2.856 | 184 | 64.4258
4.1 | 3.7776 | 1 | 2.856 | 184 | 64.4258
4 | 3.7692 | 1 | 2.856 | 184 | 64.4258
4 | 3.7691 | 1 | 2.856 | 184 | 64.4258
4.4 | 4.0739 | 1 | 2.856 | 184 | 64.4258
4.4 | 4.1659 | 1 | 2.856 | 184 | 64.4258
4.6 | 4.3643 | 1 | 2.856 | 184 | 64.4258
5 | 4.6673 | 1 | 2.856 | 184 | 64.4258
5.2 | 4.9596 | 1 | 2.856 | 184 | 64.4258
5.4 | 5.1579 | 1 | 2.856 | 184 | 64.4258
5.9 | 5.6541 | 1 | 2.856 | 184 | 64.4258
6.3 | 5.9529 | 1 | 2.856 | 184 | 64.4258
6.5 | 6.2991 | 1 | 2.856 | 184 | 64.4258
7.6 | 7.1886 | 1 | 2.856 | 184 | 64.4258
7.9 | 7.6907 | 1 | 2.856 | 184 | 64.4258
8.9 | 8.5785 | 1 | 2.856 | 184 | 64.4258
9.8 | 9.3626 | 1 | 2.856 | 184 | 64.4258
9.9 | 9.4614 | 1 | 2.856 | 184 | 64.4258
10.1 | 9.6591 | 1 | 2.856 | 184 | 64.4258
10 | 9.4526 | 1 | 2.856 | 184 | 64.4258
10.1 | 9.5511 | 1 | 2.856 | 184 | 64.4258
10.1 | 9.5509 | 1 | 2.856 | 184 | 64.4258
10.1 | 9.6587 | 1 | 2.856 | 184 | 64.4258
10.5 | 9.9448 | 1 | 2.856 | 184 | 64.4258
10.5 | 9.7287 | 1 | 2.856 | 184 | 64.4258
11 | 10.003 | 1 | 2.856 | 184 | 64.4258
11.4 | 10.178 | 1 | 2.856 | 184 | 64.4258
10.9 | 10.3383 | 1 | 2.856 | 184 | 64.4258
11 | 10.1098 | 1 | 2.856 | 184 | 64.4258
11 | 10.0025 | 1 | 2.856 | 184 | 64.4258
10.7 | 9.5007 | 1 | 2.856 | 184 | 64.4258
11.4 | 9.968 | 1 | 2.856 | 184 | 64.4258
11.5 | 9.8567 | 1 | 2.856 | 184 | 64.4258
12.2 | 9.3289 | 1 | 2.856 | 184 | 64.4258
11.1 | 8.0884 | 1 | 2.856 | 184 | 64.4258
10.8 | 7.6808 | 1 | 2.856 | 184 | 64.4258
10 | 6.8668 | 1 | 2.856 | 184 | 64.4258
9.7 | 7.0203 | 1 | 2.856 | 184 | 64.4258
9.7 | 6.8028 | 1 | 2.856 | 184 | 64.4258
8.7 | 7.1282 | 1 | 2.856 | 184 | 64.4258
7.6 | 6.0781 | 1 | 2.856 | 184 | 64.4258
6.6 | 5.1245 | 1 | 2.856 | 184 | 64.4258
6.8 | 5.2267 | 1 | 2.856 | 184 | 64.4258
6.4 | 4.9345 | 1 | 2.856 | 184 | 64.4258
5.8 | 3.9835 | 1 | 2.856 | 184 | 64.4258
6.9 | 4.5193 | 1 | 2.856 | 184 | 64.4258
5.5 | 3.8234 | 1 | 2.856 | 184 | 64.4258
7.5 | 3.9785 | 1 | 2.856 | 184 | 64.4258
7.2 | 3.7848 | 1 | 2.856 | 184 | 64.4258
6.2 | 3.2525 | 1 | 2.856 | 184 | 64.4258
5.8 | 3.2013 | 1 | 2.856 | 184 | 64.4258
6 | 3.2712 | 1 | 2.856 | 184 | 64.4258
6.3 | 3.3551 | 1 | 2.856 | 184 | 64.4258
6.8 | 3.6282 | 1 | 2.856 | 184 | 64.4258
7.7 | 4.3485 | 1 | 2.856 | 184 | 64.4258
8.7 | 5.1296 | 1 | 2.856 | 184 | 64.4258
9.3 | 5.2945 | 1 | 2.856 | 184 | 64.4258
9.5 | 5.3613 | 1 | 2.856 | 184 | 64.4258
9.4 | 5.601 | 1 | 2.856 | 184 | 64.4258
9.4 | 5.8274 | 1 | 2.856 | 184 | 64.4258
9.1 | 6.193 | 1 | 2.856 | 184 | 64.4258
8.8 | 6.1258 | 1 | 2.856 | 184 | 64.4258
9.2 | 6.324 | 1 | 2.856 | 184 | 64.4258
9.2 | 6.6626 | 1 | 2.856 | 184 | 64.4258
9.2 | 6.6613 | 1 | 2.856 | 184 | 64.4258
9.3 | 6.7525 | 1 | 2.856 | 184 | 64.4258
9.3 | 6.7525 | 1 | 2.856 | 184 | 64.4258
9.1 | 6.8732 | 1 | 2.856 | 184 | 64.4258
9.2 | 6.8765 | 1 | 2.856 | 184 | 64.4258
9.2 | 6.7433 | 1 | 2.856 | 184 | 64.4258
8.7 | 6.4537 | 1 | 2.856 | 184 | 64.4258
9.1 | 6.6495 | 1 | 2.856 | 184 | 64.4258
9.4 | 7.2853 | 1 | 2.856 | 184 | 64.4258
9.8 | 7.7997 | 1 | 2.856 | 184 | 64.4258
10.3 | 8.319 | 1 | 2.856 | 184 | 64.4258
10.7 | 8.696 | 1 | 2.856 | 184 | 64.4258
10.5 | 8.8501 | 1 | 2.856 | 184 | 64.4258
10.3 | 9.0616 | 1 | 2.856 | 184 | 64.4258
10 | 9.3443 | 1 | 2.856 | 184 | 64.4258
10.9 | 9.5889 | 1 | 2.856 | 184 | 64.4258
10.3 | 9.6388 | 1 | 2.856 | 184 | 64.4258
10.8 | 8.5944 | 1 | 2.856 | 184 | 64.4258
10.7 | 8.5955 | 1 | 2.856 | 184 | 64.4258
11 | 10.2165 | 1 | 2.856 | 184 | 64.4258
10.5 | 7.3586 | 1 | 2.856 | 184 | 64.4258
10.2 | 6.9559 | 1 | 2.856 | 184 | 64.4258
10.2 | 7.1659 | 1 | 2.856 | 184 | 64.4258
8.4 | 7.1715 | 1 | 2.856 | 184 | 64.4258
5.4 | 4.2807 | 1 | 2.856 | 184 | 64.4258
5.6 | 3.7945 | 1 | 2.856 | 184 | 64.4258
4.6 | 2.7782 | 1 | 2.856 | 184 | 64.4258
5 | 3.0756 | 1 | 2.856 | 184 | 64.4258
4.5 | 1.7996 | 1 | 2.856 | 184 | 64.4258
5 | 2.4751 | 1 | 2.856 | 184 | 64.4258
5.3 | 3.2839 | 1 | 2.856 | 184 | 64.4258
5.3 | 3.1703 | 1 | 2.856 | 184 | 64.4258
5.5 | 3.1301 | 1 | 2.856 | 184 | 64.4258
5.6 | 2.47 | 1 | 2.856 | 184 | 64.4258
5 | 2.2141 | 1 | 2.856 | 184 | 64.4258
4.3 | 2.2642 | 1 | 2.856 | 184 | 64.4258
4.5 | 1.937 | 1 | 2.856 | 184 | 64.4258
4.2 | 2.0055 | 1 | 2.856 | 184 | 64.4258
5.6 | 2.8687 | 1 | 2.856 | 184 | 64.4258
7.1 | 3.5728 | 1 | 2.856 | 184 | 64.4258
7.4 | 3.5496 | 1 | 2.856 | 184 | 64.4258
7.6 | 3.2366 | 1 | 2.856 | 184 | 64.4258
7.8 | 2.9562 | 1 | 2.856 | 184 | 64.4258
7.5 | 2.4039 | 1 | 2.856 | 184 | 64.4258
7.1 | 2.4771 | 1 | 2.856 | 184 | 64.4258
6.2 | 2.2609 | 1 | 2.856 | 184 | 64.4258
5.2 | 1.565 | 1 | 2.856 | 184 | 64.4258
4.3 | 1.645 | 1 | 2.856 | 184 | 64.4258
4 | 1.5498 | 1 | 2.856 | 184 | 64.4258
3.3 | 1.1857 | 1 | 2.856 | 184 | 64.4258
2.6 | 0.85634 | 1 | 2.856 | 184 | 64.4258
2.5 | 0.71912 | 1 | 2.856 | 184 | 64.4258
1.4 | 0.18866 | 1 | 2.856 | 184 | 64.4258
2 | 0.83165 | 1 | 2.856 | 184 | 64.4258
2.4 | 0.89997 | 1 | 2.856 | 184 | 64.4258
2.6 | 1.2228 | 1 | 2.856 | 184 | 64.4258
2.7 | 1.8159 | 1 | 2.856 | 184 | 64.4258
3.3 | 2.5196 | 1 | 2.856 | 184 | 64.4258
3.6 | 2.9375 | 1 | 2.856 | 184 | 64.4258
4.1 | 3.7793 | 1 | 2.856 | 184 | 64.4258
4.9 | 4.5706 | 1 | 2.856 | 184 | 64.4258
5.9 | 5.5599 | 1 | 2.856 | 184 | 64.4258
7.5 | 7.1933 | 1 | 2.856 | 184 | 64.4258
8.8 | 8.2741 | 1 | 2.856 | 184 | 64.4258
10 | 9.0374 | 1 | 2.856 | 184 | 64.4258
10.1 | 9.238 | 1 | 2.856 | 184 | 64.4258
10.5 | 9.4193 | 1 | 2.856 | 184 | 64.4258
10.7 | 9.407 | 1 | 2.856 | 184 | 64.4258
10.4 | 8.9654 | 1 | 2.856 | 184 | 64.4258
10.1 | 8.7771 | 1 | 2.856 | 184 | 64.4258
9.9 | 8.5844 | 1 | 2.856 | 184 | 64.4258
9.5 | 8.2974 | 1 | 2.856 | 184 | 64.4258
9.1 | 7.911 | 1 | 2.856 | 184 | 64.4258
9.3 | 7.7636 | 1 | 2.856 | 184 | 64.4258
9.3 | 7.8591 | 1 | 2.856 | 184 | 64.4258
9.2 | 8.0065 | 1 | 2.856 | 184 | 64.4258
9.5 | 7.9533 | 1 | 2.856 | 184 | 64.4258
9.6 | 7.9518 | 1 | 2.856 | 184 | 64.4258
9 | 7.5695 | 1 | 2.856 | 184 | 64.4258
9.3 | 7.8571 | 1 | 2.856 | 184 | 64.4258
9.3 | 7.7607 | 1 | 2.856 | 184 | 64.4258
9.2 | 7.8576 | 1 | 2.856 | 184 | 64.4258
9.1 | 8.0071 | 1 | 2.856 | 184 | 64.4258
8.6 | 8.0233 | 1 | 2.856 | 184 | 64.4258
8.6 | 7.9217 | 1 | 2.856 | 184 | 64.4258
8 | 7.3333 | 1 | 2.856 | 184 | 64.4258
8.7 | 7.4744 | 1 | 2.856 | 184 | 64.4258
9.3 | 5.9746 | 1 | 2.856 | 184 | 64.4258
9.9 | 5.6767 | 1 | 2.856 | 184 | 64.4258
9.5 | 5.0285 | 1 | 2.856 | 184 | 64.4258
9.5 | 5.1417 | 1 | 2.856 | 184 | 64.4258
9.4 | 4.7888 | 1 | 2.856 | 184 | 64.4258
9 | 5.0033 | 1 | 2.856 | 184 | 64.4258
7.7 | 4.2416 | 1 | 2.856 | 184 | 64.4258
6.9 | 4.0087 | 1 | 2.856 | 184 | 64.4258
5.2 | 3.1664 | 1 | 2.856 | 184 | 64.4258
4.5 | 2.7053 | 1 | 2.856 | 184 | 64.4258
4.1 | 2.4062 | 1 | 2.856 | 184 | 64.4258
3.5 | 1.775 | 1 | 2.856 | 184 | 64.4258
4.2 | 2.2542 | 1 | 2.856 | 184 | 64.4258
3 | 1.617 | 1 | 2.856 | 184 | 64.4258
0.7 | -0.022844 | 1 | 2.856 | 184 | 64.4258
1.3 | 0.84669 | 1 | 2.856 | 184 | 64.4258
2.9 | 2.0061 | 1 | 2.856 | 184 | 64.4258
1.3 | 0.84669 | 1 | 2.856 | 184 | 64.4258
0.7 | 0.36924 | 1 | 2.856 | 184 | 64.4258
1.1 | 0.76999 | 1 | 2.856 | 184 | 64.4258
1.3 | 0.96754 | 1 | 2.856 | 184 | 64.4258
2.5 | 2.0682 | 1 | 2.856 | 184 | 64.4258
3.4 | 2.9544 | 1 | 2.856 | 184 | 64.4258
4.4 | 3.7167 | 1 | 2.856 | 184 | 64.4258
6 | 4.6542 | 1 | 2.856 | 184 | 64.4258
6.9 | 4.7873 | 1 | 2.856 | 184 | 64.4258
7.4 | 4.8452 | 1 | 2.856 | 184 | 64.4258
7.6 | 4.4893 | 1 | 2.856 | 184 | 64.4258
7.4 | 3.9209 | 1 | 2.856 | 184 | 64.4258
7 | 3.473 | 1 | 2.856 | 184 | 64.4258
6.7 | 3.5428 | 1 | 2.856 | 184 | 64.4258
6.6 | 3.8067 | 1 | 2.856 | 184 | 64.4258
6.5 | 4.2512 | 1 | 2.856 | 184 | 64.4258
6.4 | 4.2791 | 1 | 2.856 | 184 | 64.4258
6 | 3.9887 | 1 | 2.856 | 184 | 64.4258
5.7 | 3.951 | 1 | 2.856 | 184 | 64.4258
5.5 | 4.0937 | 1 | 2.856 | 184 | 64.4258
5.4 | 4.1262 | 1 | 2.856 | 184 | 64.4258
5.9 | 4.3515 | 1 | 2.856 | 184 | 64.4258
5.5 | 4.3536 | 1 | 2.856 | 184 | 64.4258
5.5 | 4.3548 | 1 | 2.856 | 184 | 64.4258
5.1 | 4.5863 | 1 | 2.856 | 184 | 64.4258
5.6 | 4.9859 | 1 | 2.856 | 184 | 64.4258
5.7 | 5.2228 | 1 | 2.856 | 184 | 64.4258
6.5 | 5.8212 | 1 | 2.856 | 184 | 64.4258
6.9 | 6.1653 | 1 | 2.856 | 184 | 64.4258
7.5 | 6.5613 | 1 | 2.856 | 184 | 64.4258
7.9 | 6.8073 | 1 | 2.856 | 184 | 64.4258
8.1 | 6.8592 | 1 | 2.856 | 184 | 64.4258
8.1 | 6.9061 | 1 | 2.856 | 184 | 64.4258
8.8 | 7.4848 | 1 | 2.856 | 184 | 64.4258
9.4 | 7.7271 | 1 | 2.856 | 184 | 64.4258
9.7 | 7.6396 | 1 | 2.856 | 184 | 64.4258
9.8 | 7.2851 | 1 | 2.856 | 184 | 64.4258
9.5 | 7.051 | 1 | 2.856 | 184 | 64.4258
9.3 | 7.0846 | 1 | 2.856 | 184 | 64.4258
9.1 | 7.1207 | 1 | 2.856 | 184 | 64.4258
8.8 | 7.0187 | 1 | 2.856 | 184 | 64.4258
8.7 | 7.0612 | 1 | 2.856 | 184 | 64.4258
8.5 | 6.9168 | 1 | 2.856 | 184 | 64.4258
8.3 | 6.6807 | 1 | 2.856 | 184 | 64.4258
8.1 | 6.3569 | 1 | 2.856 | 184 | 64.4258
8 | 5.9144 | 1 | 2.856 | 184 | 64.4258
7.8 | 5.6432 | 1 | 2.856 | 184 | 64.4258
7.1 | 5.4961 | 1 | 2.856 | 184 | 64.4258
7.2 | 5.3332 | 1 | 2.856 | 184 | 64.4258
7.4 | 5.2281 | 1 | 2.856 | 184 | 64.4258
7.3 | 5.0535 | 1 | 2.856 | 184 | 64.4258
6.8 | 4.5116 | 1 | 2.856 | 184 | 64.4258
6.2 | 4.5588 | 1 | 2.856 | 184 | 64.4258
6.2 | 5.0744 | 1 | 2.856 | 184 | 64.4258
7.9 | 6.3453 | 1 | 2.856 | 184 | 64.4258
7.9 | 5.9926 | 1 | 2.856 | 184 | 64.4258
9.2 | 5.9924 | 1 | 2.856 | 184 | 64.4258
8.7 | 5.7758 | 1 | 2.856 | 184 | 64.4258
8.9 | 5.9574 | 1 | 2.856 | 184 | 64.4258
9.6 | 6.5522 | 1 | 2.856 | 184 | 64.4258
8.9 | 6.1601 | 1 | 2.856 | 184 | 64.4258
8 | 5.4153 | 1 | 2.856 | 184 | 64.4258
6.9 | 4.8442 | 1 | 2.856 | 184 | 64.4258
7.2 | 5.2072 | 1 | 2.856 | 184 | 64.4258
6.5 | 5.0114 | 1 | 2.856 | 184 | 64.4258
6.7 | 5.2018 | 1 | 2.856 | 184 | 64.4258
6 | 4.9246 | 1 | 2.856 | 184 | 64.4258
6.1 | 5.0211 | 1 | 2.856 | 184 | 64.4258
4.8 | 4.2461 | 1 | 2.856 | 184 | 64.4258
5 | 4.4422 | 1 | 2.856 | 184 | 64.4258
4.3 | 3.8438 | 1 | 2.856 | 184 | 64.4258
3.6 | 3.1978 | 1 | 2.856 | 184 | 64.4258
4.6 | 4.275 | 1 | 2.856 | 184 | 64.4258
5.1 | 4.677 | 1 | 2.856 | 184 | 64.4258
5.6 | 5.1702 | 1 | 2.856 | 184 | 64.4258
6.2 | 5.5265 | 1 | 2.856 | 184 | 64.4258
4.8 | 4.2008 | 1 | 2.856 | 184 | 64.4258
7.3 | 6.5553 | 1 | 2.856 | 184 | 64.4258
8.1 | 7.2394 | 1 | 2.856 | 184 | 64.4258
8.6 | 7.5308 | 1 | 2.856 | 184 | 64.4258
8.9 | 7.6748 | 1 | 2.856 | 184 | 64.4258
10.1 | 8.4869 | 1 | 2.856 | 184 | 64.4258
10.4 | 8.7726 | 1 | 2.856 | 184 | 64.4258
10.5 | 8.7693 | 1 | 2.856 | 184 | 64.4258
10.3 | 8.7254 | 1 | 2.856 | 184 | 64.4258
9.6 | 8.1522 | 1 | 2.856 | 184 | 64.4258
8.5 | 7.3834 | 1 | 2.856 | 184 | 64.4258
9.4 | 8.1063 | 1 | 2.856 | 184 | 64.4258
9.6 | 8.3979 | 1 | 2.856 | 184 | 64.4258
9.8 | 8.5413 | 1 | 2.856 | 184 | 64.4258
8.8 | 8.0203 | 1 | 2.856 | 184 | 64.4258
9.2 | 8.3101 | 1 | 2.856 | 184 | 64.4258
9.9 | 8.6378 | 1 | 2.856 | 184 | 64.4258
9.9 | 8.5378 | 1 | 2.856 | 184 | 64.4258
9.5 | 8.4003 | 1 | 2.856 | 184 | 64.4258
9.4 | 8.2036 | 1 | 2.856 | 184 | 64.4258
9.2 | 7.8148 | 1 | 2.856 | 184 | 64.4258
9.4 | 7.8621 | 1 | 2.856 | 184 | 64.4258
9.8 | 8.1479 | 1 | 2.856 | 184 | 64.4258
9.9 | 8.1463 | 1 | 2.856 | 184 | 64.4258
10.1 | 8.2875 | 1 | 2.856 | 184 | 64.4258
10.4 | 8.524 | 1 | 2.856 | 184 | 64.4258
10.5 | 8.7157 | 1 | 2.856 | 184 | 64.4258
10.7 | 9.0043 | 1 | 2.856 | 184 | 64.4258
11.3 | 9.3762 | 1 | 2.856 | 184 | 64.4258
12.5 | 10.1095 | 1 | 2.856 | 184 | 64.4258
12.6 | 10.252 | 1 | 2.856 | 184 | 64.4258
12.7 | 10.4455 | 1 | 2.856 | 184 | 64.4258
12.2 | 10.1755 | 1 | 2.856 | 184 | 64.4258
11.4 | 9.769 | 1 | 2.856 | 184 | 64.4258
11.1 | 9.4827 | 1 | 2.856 | 184 | 64.4258
10.7 | 9.1502 | 1 | 2.856 | 184 | 64.4258
10.4 | 8.7629 | 1 | 2.856 | 184 | 64.4258
11.1 | 9.4827 | 1 | 2.856 | 184 | 64.4258
10.3 | 6.9946 | 1 | 2.856 | 184 | 64.4258
9.2 | 5.3921 | 1 | 2.856 | 184 | 64.4258
8.1 | 4.7112 | 1 | 2.856 | 184 | 64.4258
7.3 | 4.2537 | 1 | 2.856 | 184 | 64.4258
8 | 4.5496 | 1 | 2.856 | 184 | 64.4258
7.7 | 4.7251 | 1 | 2.856 | 184 | 64.4258
8.1 | 4.8579 | 1 | 2.856 | 184 | 64.4258
7.8 | 4.8523 | 1 | 2.856 | 184 | 64.4258
7.5 | 4.813 | 1 | 2.856 | 184 | 64.4258
7.4 | 4.8003 | 1 | 2.856 | 184 | 64.4258
7.7 | 4.9956 | 1 | 2.856 | 184 | 64.4258
8.3 | 5.4645 | 1 | 2.856 | 184 | 64.4258
8.7 | 5.7465 | 1 | 2.856 | 184 | 64.4258
9.5 | 6.1506 | 1 | 2.856 | 184 | 64.4258
8.9 | 6.1329 | 1 | 2.856 | 184 | 64.4258
9.6 | 6.12 | 1 | 2.856 | 184 | 64.4258
9.5 | 5.8761 | 1 | 2.856 | 184 | 64.4258
9.1 | 5.409 | 1 | 2.856 | 184 | 64.4258
8.1 | 5.0079 | 1 | 2.856 | 184 | 64.4258
8 | 5.1505 | 1 | 2.856 | 184 | 64.4258
7.7 | 4.8778 | 1 | 2.856 | 184 | 64.4258
7.4 | 5.0006 | 1 | 2.856 | 184 | 64.4258
6.8 | 5.0656 | 1 | 2.856 | 184 | 64.4258
7.2 | 4.6948 | 1 | 2.856 | 184 | 64.4258
7.6 | 4.9029 | 1 | 2.856 | 184 | 64.4258
7.3 | 5.0293 | 1 | 2.856 | 184 | 64.4258
7.2 | 5.1008 | 1 | 2.856 | 184 | 64.4258
7.4 | 5.2874 | 1 | 2.856 | 184 | 64.4258
7.4 | 5.2874 | 1 | 2.856 | 184 | 64.4258
7.3 | 5.1107 | 1 | 2.856 | 184 | 64.4258
7.1 | 5.0901 | 1 | 2.856 | 184 | 64.4258
7 | 5.2088 | 1 | 2.856 | 184 | 64.4258
6.6 | 5.2218 | 1 | 2.856 | 184 | 64.4258
6.7 | 4.8834 | 1 | 2.856 | 184 | 64.4258
6.7 | 4.8412 | 1 | 2.856 | 184 | 64.4258
6.7 | 4.7992 | 1 | 2.856 | 184 | 64.4258
7.2 | 5.0569 | 1 | 2.856 | 184 | 64.4258
7.9 | 5.2933 | 1 | 2.856 | 184 | 64.4258
8.1 | 5.2738 | 1 | 2.856 | 184 | 64.4258
7.9 | 5.5391 | 1 | 2.856 | 184 | 64.4258
8.8 | 5.6271 | 1 | 2.856 | 184 | 64.4258
8.6 | 5.4863 | 1 | 2.856 | 184 | 64.4258
8.1 | 5.5952 | 1 | 2.856 | 184 | 64.4258
7.9 | 5.2867 | 1 | 2.856 | 184 | 64.4258
7.4 | 5.4065 | 1 | 2.856 | 184 | 64.4258
6.6 | 5.6722 | 1 | 2.856 | 184 | 64.4258
6.7 | 6.2488 | 1 | 2.856 | 184 | 64.4258
6.7 | 5.4454 | 1 | 2.856 | 184 | 64.4258
6.3 | 4.84 | 1 | 2.856 | 184 | 64.4258
6.5 | 4.986 | 1 | 2.856 | 184 | 64.4258
5.9 | 3.9975 | 1 | 2.856 | 184 | 64.4258
4.9 | 3.5046 | 1 | 2.856 | 184 | 64.4258
4.5 | 3.2474 | 1 | 2.856 | 184 | 64.4258
4.1 | 2.5828 | 1 | 2.856 | 184 | 64.4258
3.3 | 1.8578 | 1 | 2.856 | 184 | 64.4258
3 | 1.4723 | 1 | 2.856 | 184 | 64.4258
3 | 1.3877 | 1 | 2.856 | 184 | 64.4258
2.6 | 0.90996 | 1 | 2.856 | 184 | 64.4258
2 | 0.7715 | 1 | 2.856 | 184 | 64.4258
2.3 | 0.15433 | 1 | 2.856 | 184 | 64.4258
2.7 | -0.43142 | 1 | 2.856 | 184 | 64.4258
3.3 | -0.42711 | 1 | 2.856 | 184 | 64.4258
3.7 | -0.74224 | 1 | 2.856 | 184 | 64.4258
4.2 | -0.50054 | 1 | 2.856 | 184 | 64.4258
4.7 | -0.05827 | 1 | 2.856 | 184 | 64.4258
4.8 | 0.22405 | 1 | 2.856 | 184 | 64.4258
4.2 | -0.41039 | 1 | 2.856 | 184 | 64.4258
3.7 | -0.62395 | 1 | 2.856 | 184 | 64.4258
2.9 | -1.1805 | 1 | 2.856 | 184 | 64.4258
2.2 | -1.1105 | 1 | 2.856 | 184 | 64.4258
1.7 | -1.1794 | 1 | 2.856 | 184 | 64.4258
1.1 | -1.1992 | 1 | 2.856 | 184 | 64.4258
0.9 | -1.3163 | 1 | 2.856 | 184 | 64.4258
0.7 | -1.402 | 1 | 2.856 | 184 | 64.4258
-1.1 | -2.4444 | 1 | 2.856 | 184 | 64.4258
0.4 | -1.7063 | 1 | 2.856 | 184 | 64.4258
0.6 | -1.2668 | 1 | 2.856 | 184 | 64.4258
-0.2 | -1.7718 | 1 | 2.856 | 184 | 64.4258
-0.1 | -1.2959 | 1 | 2.856 | 184 | 64.4258
-0.4 | -1.6163 | 1 | 2.856 | 184 | 64.4258
-0.5 | -1.4954 | 1 | 2.856 | 184 | 64.4258
0.7 | -0.57728 | 1 | 2.856 | 184 | 64.4258
0.6 | -0.55984 | 1 | 2.856 | 184 | 64.4258
1.2 | -0.29364 | 1 | 2.856 | 184 | 64.4258
1.8 | 0.48507 | 1 | 2.856 | 184 | 64.4258
2.5 | 1.1 | 1 | 2.856 | 184 | 64.4258
2.8 | 1.2709 | 1 | 2.856 | 184 | 64.4258
2.6 | 1.5834 | 1 | 2.856 | 184 | 64.4258
2.3 | 1.4528 | 1 | 2.856 | 184 | 64.4258
2.5 | 1.7687 | 1 | 2.856 | 184 | 64.4258
2.2 | 1.558 | 1 | 2.856 | 184 | 64.4258
2.2 | 1.3951 | 1 | 2.856 | 184 | 64.4258
2.4 | 1.712 | 1 | 2.856 | 184 | 64.4258
2.7 | 1.7989 | 1 | 2.856 | 184 | 64.4258
2.6 | 1.7021 | 1 | 2.856 | 184 | 64.4258
2.2 | 1.3951 | 1 | 2.856 | 184 | 64.4258
0.6 | 0.036115 | 1 | 2.856 | 184 | 64.4258
-0.3 | -0.42944 | 1 | 2.856 | 184 | 64.4258
0.1 | -0.84938 | 1 | 2.856 | 184 | 64.4258
-0.4 | -1.5134 | 1 | 2.856 | 184 | 64.4258
-1.1 | -2.1081 | 1 | 2.856 | 184 | 64.4258
-1.7 | -2.7494 | 1 | 2.856 | 184 | 64.4258
-1.6 | -2.5152 | 1 | 2.856 | 184 | 64.4258
-1 | -1.9038 | 1 | 2.856 | 184 | 64.4258
-0.7 | -1.5789 | 1 | 2.856 | 184 | 64.4258
-1.1 | -1.9991 | 1 | 2.856 | 184 | 64.4258
-1.3 | -2.3322 | 1 | 2.856 | 184 | 64.4258
-1 | -2.1163 | 1 | 2.856 | 184 | 64.4258
-0.1 | -1.2987 | 1 | 2.856 | 184 | 64.4258
1 | -0.51749 | 1 | 2.856 | 184 | 64.4258
1.9 | -0.61725 | 1 | 2.856 | 184 | 64.4258
2.5 | -0.27579 | 1 | 2.856 | 184 | 64.4258
3.2 | -0.064929 | 1 | 2.856 | 184 | 64.4258
3.1 | -0.060973 | 1 | 2.856 | 184 | 64.4258
3 | -0.63157 | 1 | 2.856 | 184 | 64.4258
2.3 | -0.8382 | 1 | 2.856 | 184 | 64.4258
1.3 | -1.118 | 1 | 2.856 | 184 | 64.4258
0.3 | -1.7681 | 1 | 2.856 | 184 | 64.4258
0.9 | -1.5357 | 1 | 2.856 | 184 | 64.4258
0.1 | -2.0412 | 1 | 2.856 | 184 | 64.4258
-0.1 | -2.0053 | 1 | 2.856 | 184 | 64.4258
-0.8 | -2.1648 | 1 | 2.856 | 184 | 64.4258
-0.8 | -2.0285 | 1 | 2.856 | 184 | 64.4258
-1.5 | -2.5196 | 1 | 2.856 | 184 | 64.4258
-1.4 | -2.3192 | 1 | 2.856 | 184 | 64.4258
-1.5 | -2.7557 | 1 | 2.856 | 184 | 64.4258
-1.1 | -2.5769 | 1 | 2.856 | 184 | 64.4258
-1.2 | -2.7966 | 1 | 2.856 | 184 | 64.4258
-0.2 | -1.8722 | 1 | 2.856 | 184 | 64.4258
-0.4 | -1.858 | 1 | 2.856 | 184 | 64.4258
-0.3 | -1.626 | 1 | 2.856 | 184 | 64.4258
0.6 | -0.44202 | 1 | 2.856 | 184 | 64.4258
1.6 | -0.68578 | 1 | 2.856 | 184 | 64.4258
2.7 | -0.30683 | 1 | 2.856 | 184 | 64.4258
3.2 | 0.54339 | 1 | 2.856 | 184 | 64.4258
3.5 | 0.82687 | 1 | 2.856 | 184 | 64.4258
4.2 | 1.1955 | 1 | 2.856 | 184 | 64.4258
4.3 | 0.94466 | 1 | 2.856 | 184 | 64.4258
4.1 | 0.76446 | 1 | 2.856 | 184 | 64.4258
3.4 | 0.69873 | 1 | 2.856 | 184 | 64.4258
2.5 | 0.28119 | 1 | 2.856 | 184 | 64.4258
2 | -0.28591 | 1 | 2.856 | 184 | 64.4258
1.9 | -0.507 | 1 | 2.856 | 184 | 64.4258
1.5 | -0.80152 | 1 | 2.856 | 184 | 64.4258
0.2 | -1.3254 | 1 | 2.856 | 184 | 64.4258
0.2 | -1.6905 | 1 | 2.856 | 184 | 64.4258
-1 | -2.1076 | 1 | 2.856 | 184 | 64.4258
-0.2 | -1.7644 | 1 | 2.856 | 184 | 64.4258
-2.3 | -3.1087 | 1 | 2.856 | 184 | 64.4258
-1.5 | -2.4101 | 1 | 2.856 | 184 | 64.4258
-1.1 | -2.0973 | 1 | 2.856 | 184 | 64.4258
-1.3 | -2.3229 | 1 | 2.856 | 184 | 64.4258
-1.5 | -2.4095 | 1 | 2.856 | 184 | 64.4258
-1.5 | -2.409 | 1 | 2.856 | 184 | 64.4258
-1.6 | -2.3988 | 1 | 2.856 | 184 | 64.4258
-1.5 | -2.4095 | 1 | 2.856 | 184 | 64.4258
0.9 | -0.70495 | 1 | 2.856 | 184 | 64.4258
3.6 | 1.229 | 1 | 2.856 | 184 | 64.4258
5.3 | 1.7713 | 1 | 2.856 | 184 | 64.4258
5 | 1.7394 | 1 | 2.856 | 184 | 64.4258
5.2 | 1.6446 | 1 | 2.856 | 184 | 64.4258
5.3 | 2.0516 | 1 | 2.856 | 184 | 64.4258
5.3 | 2.5008 | 1 | 2.856 | 184 | 64.4258
4.9 | 2.6402 | 1 | 2.856 | 184 | 64.4258
4.8 | 2.7922 | 1 | 2.856 | 184 | 64.4258
4.3 | 2.5149 | 1 | 2.856 | 184 | 64.4258
3.9 | 2.6046 | 1 | 2.856 | 184 | 64.4258
4 | 2.621 | 1 | 2.856 | 184 | 64.4258
3.4 | 2.5303 | 1 | 2.856 | 184 | 64.4258
3.2 | 2.4184 | 1 | 2.856 | 184 | 64.4258
3 | 2.4327 | 1 | 2.856 | 184 | 64.4258
3.2 | 2.5022 | 1 | 2.856 | 184 | 64.4258
3.4 | 2.4892 | 1 | 2.856 | 184 | 64.4258
3.1 | 2.363 | 1 | 2.856 | 184 | 64.4258
3.2 | 2.3775 | 1 | 2.856 | 184 | 64.4258
3 | 2.4327 | 1 | 2.856 | 184 | 64.4258
2.9 | 2.4192 | 1 | 2.856 | 184 | 64.4258
3.1 | 2.363 | 1 | 2.856 | 184 | 64.4258
3.2 | 2.296 | 1 | 2.856 | 184 | 64.4258
3.6 | 2.5201 | 1 | 2.856 | 184 | 64.4258
4.1 | 2.8784 | 1 | 2.856 | 184 | 64.4258
4.7 | 3.2888 | 1 | 2.856 | 184 | 64.4258
5.8 | 4.1685 | 1 | 2.856 | 184 | 64.4258
6.5 | 4.4979 | 1 | 2.856 | 184 | 64.4258
7.1 | 4.8531 | 1 | 2.856 | 184 | 64.4258
7.1 | 4.6527 | 1 | 2.856 | 184 | 64.4258
7.3 | 4.7574 | 1 | 2.856 | 184 | 64.4258
6.9 | 4.6688 | 1 | 2.856 | 184 | 64.4258
6.1 | 4.2059 | 1 | 2.856 | 184 | 64.4258
5.3 | 3.8614 | 1 | 2.856 | 184 | 64.4258
4.7 | 3.5377 | 1 | 2.856 | 184 | 64.4258
4.4 | 3.3747 | 1 | 2.856 | 184 | 64.4258
4 | 3.1145 | 1 | 2.856 | 184 | 64.4258
4.1 | 3.1693 | 1 | 2.856 | 184 | 64.4258
3.7 | 3.0349 | 1 | 2.856 | 184 | 64.4258
3.7 | 2.9923 | 1 | 2.856 | 184 | 64.4258
3.7 | 2.8658 | 1 | 2.856 | 184 | 64.4258
3.4 | 2.4107 | 1 | 2.856 | 184 | 64.4258
3.6 | 2.2838 | 1 | 2.856 | 184 | 64.4258
3.7 | 2.1861 | 1 | 2.856 | 184 | 64.4258
3.1 | 1.9246 | 1 | 2.856 | 184 | 64.4258
3 | 1.907 | 1 | 2.856 | 184 | 64.4258
1.9 | 1.0744 | 1 | 2.856 | 184 | 64.4258
3 | 1.4963 | 1 | 2.856 | 184 | 64.4258
4.1 | 2.1235 | 1 | 2.856 | 184 | 64.4258
5.1 | 2.5655 | 1 | 2.856 | 184 | 64.4258
5.9 | 2.4487 | 1 | 2.856 | 184 | 64.4258
6.5 | 1.3152 | 1 | 2.856 | 184 | 64.4258
6.7 | 2.143 | 1 | 2.856 | 184 | 64.4258
7 | 1.8587 | 1 | 2.856 | 184 | 64.4258
5.8 | 1.3098 | 1 | 2.856 | 184 | 64.4258
4.9 | 0.53576 | 1 | 2.856 | 184 | 64.4258
4.4 | 0.23937 | 1 | 2.856 | 184 | 64.4258
3.3 | 0.20487 | 1 | 2.856 | 184 | 64.4258
2.5 | -0.22941 | 1 | 2.856 | 184 | 64.4258
1.7 | -0.69068 | 1 | 2.856 | 184 | 64.4258
0.6 | -1.0048 | 1 | 2.856 | 184 | 64.4258
0.1 | -1.2993 | 1 | 2.856 | 184 | 64.4258
-1.2 | -2.1834 | 1 | 2.856 | 184 | 64.4258
-1.9 | -2.6811 | 1 | 2.856 | 184 | 64.4258
-1.6 | -2.3921 | 1 | 2.856 | 184 | 64.4258
-2.4 | -3.0951 | 1 | 2.856 | 184 | 64.4258
-2.4 | -3.231 | 1 | 2.856 | 184 | 64.4258
-1.5 | -2.6393 | 1 | 2.856 | 184 | 64.4258
-2.7 | -3.5196 | 1 | 2.856 | 184 | 64.4258
-1 | -2.2343 | 1 | 2.856 | 184 | 64.4258
-0.9 | -2.107 | 1 | 2.856 | 184 | 64.4258
0.4 | -0.98697 | 1 | 2.856 | 184 | 64.4258
1.5 | -0.41996 | 1 | 2.856 | 184 | 64.4258
3.8 | 1.5478 | 1 | 2.856 | 184 | 64.4258
4.4 | 2.6527 | 1 | 2.856 | 184 | 64.4258
5.4 | 3.7511 | 1 | 2.856 | 184 | 64.4258
5.7 | 4.0336 | 1 | 2.856 | 184 | 64.4258
6.1 | 4.5788 | 1 | 2.856 | 184 | 64.4258
5.9 | 4.955 | 1 | 2.856 | 184 | 64.4258
6.1 | 5.5659 | 1 | 2.856 | 184 | 64.4258
6.5 | 6.1038 | 1 | 2.856 | 184 | 64.4258
6.6 | 6.2026 | 1 | 2.856 | 184 | 64.4258
6.6 | 6.2515 | 1 | 2.856 | 184 | 64.4258
7 | 6.5978 | 1 | 2.856 | 184 | 64.4258
7 | 6.4995 | 1 | 2.856 | 184 | 64.4258
7.2 | 6.7458 | 1 | 2.856 | 184 | 64.4258
6.6 | 6.0573 | 1 | 2.856 | 184 | 64.4258
6.1 | 5.1935 | 1 | 2.856 | 184 | 64.4258
5.6 | 4.6191 | 1 | 2.856 | 184 | 64.4258
4.5 | 3.814 | 1 | 2.856 | 184 | 64.4258
3.8 | 3.3478 | 1 | 2.856 | 184 | 64.4258
3.2 | 2.757 | 1 | 2.856 | 184 | 64.4258
3.1 | 2.6156 | 1 | 2.856 | 184 | 64.4258
3.2 | 2.6711 | 1 | 2.856 | 184 | 64.4258
3 | 2.5603 | 1 | 2.856 | 184 | 64.4258
3.5 | 3.0524 | 1 | 2.856 | 184 | 64.4258
5 | 4.2579 | 1 | 2.856 | 184 | 64.4258
5.3 | 4.461 | 1 | 2.856 | 184 | 64.4258
7.3 | 5.9416 | 1 | 2.856 | 184 | 64.4258
7 | 5.5194 | 1 | 2.856 | 184 | 64.4258
8.2 | 6.2126 | 1 | 2.856 | 184 | 64.4258
8.8 | 6.2519 | 1 | 2.856 | 184 | 64.4258
8.4 | 5.9659 | 1 | 2.856 | 184 | 64.4258
8.2 | 5.8218 | 1 | 2.856 | 184 | 64.4258
7.8 | 5.3686 | 1 | 2.856 | 184 | 64.4258
7.4 | 5.5004 | 1 | 2.856 | 184 | 64.4258
7.2 | 5.4853 | 1 | 2.856 | 184 | 64.4258
6.9 | 5.3314 | 1 | 2.856 | 184 | 64.4258
6.2 | 4.7956 | 1 | 2.856 | 184 | 64.4258
6.1 | 4.7428 | 1 | 2.856 | 184 | 64.4258
6.1 | 4.6561 | 1 | 2.856 | 184 | 64.4258
6.8 | 5.191 | 1 | 2.856 | 184 | 64.4258
6.3 | 5.1102 | 1 | 2.856 | 184 | 64.4258
7.1 | 5.7425 | 1 | 2.856 | 184 | 64.4258
7.3 | 5.9799 | 1 | 2.856 | 184 | 64.4258
7.1 | 5.9251 | 1 | 2.856 | 184 | 64.4258
6.1 | 4.6979 | 1 | 2.856 | 184 | 64.4258
5.9 | 4.6373 | 1 | 2.856 | 184 | 64.4258
5.8 | 4.3266 | 1 | 2.856 | 184 | 64.4258
6.8 | 3.6668 | 1 | 2.856 | 184 | 64.4258
7.7 | 4.345 | 1 | 2.856 | 184 | 64.4258
8.4 | 4.597 | 1 | 2.856 | 184 | 64.4258
8.1 | 3.6168 | 1 | 2.856 | 184 | 64.4258
8.7 | 3.6371 | 1 | 2.856 | 184 | 64.4258
8.6 | 3.4234 | 1 | 2.856 | 184 | 64.4258
8.6 | 3.3301 | 1 | 2.856 | 184 | 64.4258
8.4 | 3.605 | 1 | 2.856 | 184 | 64.4258
8 | 3.4229 | 1 | 2.856 | 184 | 64.4258
6.8 | 3.0156 | 1 | 2.856 | 184 | 64.4258
6.6 | 2.9772 | 1 | 2.856 | 184 | 64.4258
6 | 3.0315 | 1 | 2.856 | 184 | 64.4258
5.8 | 3.0426 | 1 | 2.856 | 184 | 64.4258
5.9 | 3.2613 | 1 | 2.856 | 184 | 64.4258
5.5 | 3.3161 | 1 | 2.856 | 184 | 64.4258
4.9 | 3.1066 | 1 | 2.856 | 184 | 64.4258
5.3 | 3.4026 | 1 | 2.856 | 184 | 64.4258
5.7 | 3.54 | 1 | 2.856 | 184 | 64.4258
5.7 | 3.6181 | 1 | 2.856 | 184 | 64.4258
6 | 3.474 | 1 | 2.856 | 184 | 64.4258
4.4 | 2.9941 | 1 | 2.856 | 184 | 64.4258
5.1 | 2.8254 | 1 | 2.856 | 184 | 64.4258
4.8 | 2.9368 | 1 | 2.856 | 184 | 64.4258
4.4 | 2.9957 | 1 | 2.856 | 184 | 64.4258
4.8 | 3.0549 | 1 | 2.856 | 184 | 64.4258
5.1 | 2.9124 | 1 | 2.856 | 184 | 64.4258
6 | 3.6675 | 1 | 2.856 | 184 | 64.4258
7.1 | 4.5621 | 1 | 2.856 | 184 | 64.4258
8.2 | 4.5728 | 1 | 2.856 | 184 | 64.4258
9 | 4.9889 | 1 | 2.856 | 184 | 64.4258
9 | 5.0604 | 1 | 2.856 | 184 | 64.4258
8.8 | 5.3232 | 1 | 2.856 | 184 | 64.4258
8.3 | 5.4975 | 1 | 2.856 | 184 | 64.4258
7.9 | 5.6243 | 1 | 2.856 | 184 | 64.4258
7.5 | 5.9451 | 1 | 2.856 | 184 | 64.4258
7.3 | 6.3075 | 1 | 2.856 | 184 | 64.4258
8 | 7.0347 | 1 | 2.856 | 184 | 64.4258
8 | 7.3806 | 1 | 2.856 | 184 | 64.4258
8.3 | 7.7771 | 1 | 2.856 | 184 | 64.4258
9.6 | 8.4371 | 1 | 2.856 | 184 | 64.4258
9.8 | 8.3799 | 1 | 2.856 | 184 | 64.4258
9.9 | 8.23 | 1 | 2.856 | 184 | 64.4258
9.9 | 8.134 | 1 | 2.856 | 184 | 64.4258
9.6 | 7.8013 | 1 | 2.856 | 184 | 64.4258
9.7 | 7.897 | 1 | 2.856 | 184 | 64.4258
9.6 | 7.7548 | 1 | 2.856 | 184 | 64.4258
9.8 | 7.7567 | 1 | 2.856 | 184 | 64.4258
9.3 | 7.4724 | 1 | 2.856 | 184 | 64.4258
9.7 | 7.7579 | 1 | 2.856 | 184 | 64.4258
9.8 | 7.8995 | 1 | 2.856 | 184 | 64.4258
10.1 | 8.1365 | 1 | 2.856 | 184 | 64.4258
11.2 | 8.3273 | 1 | 2.856 | 184 | 64.4258
11.3 | 8.2394 | 1 | 2.856 | 184 | 64.4258
11 | 8.3237 | 1 | 2.856 | 184 | 64.4258
11 | 8.4157 | 1 | 2.856 | 184 | 64.4258
10.9 | 8.3691 | 1 | 2.856 | 184 | 64.4258
10.7 | 8.3223 | 1 | 2.856 | 184 | 64.4258
9.9 | 7.9467 | 1 | 2.856 | 184 | 64.4258
9.5 | 7.7572 | 1 | 2.856 | 184 | 64.4258
9.4 | 7.8045 | 1 | 2.856 | 184 | 64.4258
9.5 | 8.193 | 1 | 2.856 | 184 | 64.4258
9.2 | 8.3035 | 1 | 2.856 | 184 | 64.4258
9.6 | 8.3885 | 1 | 2.856 | 184 | 64.4258
9.2 | 8.4566 | 1 | 2.856 | 184 | 64.4258
9.2 | 8.4563 | 1 | 2.856 | 184 | 64.4258
9.3 | 8.6057 | 1 | 2.856 | 184 | 64.4258
9.8 | 8.9388 | 1 | 2.856 | 184 | 64.4258
10 | 9.0819 | 1 | 2.856 | 184 | 64.4258
9.9 | 9.3001 | 1 | 2.856 | 184 | 64.4258
10.3 | 9.3741 | 1 | 2.856 | 184 | 64.4258
10.8 | 9.7561 | 1 | 2.856 | 184 | 64.4258
10.9 | 10.0132 | 1 | 2.856 | 184 | 64.4258
11.1 | 10.2627 | 1 | 2.856 | 184 | 64.4258
12 | 10.8148 | 1 | 2.856 | 184 | 64.4258
12.1 | 10.9118 | 1 | 2.856 | 184 | 64.4258
12.7 | 11.2206 | 1 | 2.856 | 184 | 64.4258
13 | 11.4559 | 1 | 2.856 | 184 | 64.4258
13 | 11.619 | 1 | 2.856 | 184 | 64.4258
12.8 | 11.2097 | 1 | 2.856 | 184 | 64.4258
12.9 | 11.1444 | 1 | 2.856 | 184 | 64.4258
12.4 | 10.8255 | 1 | 2.856 | 184 | 64.4258
12.1 | 10.6433 | 1 | 2.856 | 184 | 64.4258
12 | 10.5476 | 1 | 2.856 | 184 | 64.4258
11.4 | 10.3402 | 1 | 2.856 | 184 | 64.4258
9.8 | 9.044 | 1 | 2.856 | 184 | 64.4258
9 | 7.9569 | 1 | 2.856 | 184 | 64.4258
8.8 | 6.9054 | 1 | 2.856 | 184 | 64.4258
8.6 | 7.1338 | 1 | 2.856 | 184 | 64.4258
8.2 | 6.384 | 1 | 2.856 | 184 | 64.4258
7.8 | 6.6491 | 1 | 2.856 | 184 | 64.4258
7.9 | 6.938 | 1 | 2.856 | 184 | 64.4258
5.9 | 5.4612 | 1 | 2.856 | 184 | 64.4258
7.2 | 6.0698 | 1 | 2.856 | 184 | 64.4258
6.4 | 5.298 | 1 | 2.856 | 184 | 64.4258
6.3 | 5.2923 | 1 | 2.856 | 184 | 64.4258
4.6 | 3.8209 | 1 | 2.856 | 184 | 64.4258
6.9 | 4.903 | 1 | 2.856 | 184 | 64.4258
7.5 | 4.929 | 1 | 2.856 | 184 | 64.4258
8.4 | 4.8238 | 1 | 2.856 | 184 | 64.4258
8.8 | 5.1019 | 1 | 2.856 | 184 | 64.4258
9.5 | 5.5701 | 1 | 2.856 | 184 | 64.4258
9.8 | 5.6494 | 1 | 2.856 | 184 | 64.4258
9.1 | 5.2927 | 1 | 2.856 | 184 | 64.4258
8.6 | 4.9987 | 1 | 2.856 | 184 | 64.4258
8.2 | 4.6815 | 1 | 2.856 | 184 | 64.4258
7.7 | 4.6809 | 1 | 2.856 | 184 | 64.4258
7.5 | 4.3495 | 1 | 2.856 | 184 | 64.4258
7.1 | 4.1012 | 1 | 2.856 | 184 | 64.4258
6.8 | 4.1287 | 1 | 2.856 | 184 | 64.4258
6.4 | 4.3106 | 1 | 2.856 | 184 | 64.4258
6.4 | 4.6411 | 1 | 2.856 | 184 | 64.4258
6.7 | 4.8383 | 1 | 2.856 | 184 | 64.4258
6.6 | 4.8714 | 1 | 2.856 | 184 | 64.4258
6.8 | 5.1025 | 1 | 2.856 | 184 | 64.4258
6.7 | 5.2251 | 1 | 2.856 | 184 | 64.4258
6.8 | 5.3642 | 1 | 2.856 | 184 | 64.4258
7.1 | 5.5159 | 1 | 2.856 | 184 | 64.4258
7.2 | 6.0658 | 1 | 2.856 | 184 | 64.4258
8 | 7.0799 | 1 | 2.856 | 184 | 64.4258
8.3 | 7.5215 | 1 | 2.856 | 184 | 64.4258
8.9 | 6.8534 | 1 | 2.856 | 184 | 64.4258
9.7 | 7.2844 | 1 | 2.856 | 184 | 64.4258
9.5 | 6.9197 | 1 | 2.856 | 184 | 64.4258
10.4 | 7.8411 | 1 | 2.856 | 184 | 64.4258
10.7 | 8.0262 | 1 | 2.856 | 184 | 64.4258
11.2 | 7.8588 | 1 | 2.856 | 184 | 64.4258
9.4 | 7.5058 | 1 | 2.856 | 184 | 64.4258
9.4 | 6.8248 | 1 | 2.856 | 184 | 64.4258
9.2 | 5.73 | 1 | 2.856 | 184 | 64.4258
8.7 | 4.7205 | 1 | 2.856 | 184 | 64.4258
7.9 | 4.7591 | 1 | 2.856 | 184 | 64.4258
7.6 | 4.3397 | 1 | 2.856 | 184 | 64.4258
5.9 | 3.9111 | 1 | 2.856 | 184 | 64.4258
4.2 | 3.1244 | 1 | 2.856 | 184 | 64.4258
5 | 3.1887 | 1 | 2.856 | 184 | 64.4258
4.8 | 2.9606 | 1 | 2.856 | 184 | 64.4258
4.2 | 1.8543 | 1 | 2.856 | 184 | 64.4258
3.5 | 1.5821 | 1 | 2.856 | 184 | 64.4258
3.4 | 1.1635 | 1 | 2.856 | 184 | 64.4258
3.6 | 1.2003 | 1 | 2.856 | 184 | 64.4258
3.2 | 1.4131 | 1 | 2.856 | 184 | 64.4258
3.8 | 1.5105 | 1 | 2.856 | 184 | 64.4258
3.7 | 1.4935 | 1 | 2.856 | 184 | 64.4258
3.4 | 1.6952 | 1 | 2.856 | 184 | 64.4258
4.5 | 2.229 | 1 | 2.856 | 184 | 64.4258
5.5 | 2.5832 | 1 | 2.856 | 184 | 64.4258
6.1 | 2.6856 | 1 | 2.856 | 184 | 64.4258
6.7 | 2.7962 | 1 | 2.856 | 184 | 64.4258
7.5 | 3.4492 | 1 | 2.856 | 184 | 64.4258
7.9 | 3.3151 | 1 | 2.856 | 184 | 64.4258
7 | 3.22 | 1 | 2.856 | 184 | 64.4258
7.7 | 3.0749 | 1 | 2.856 | 184 | 64.4258
6.7 | 2.5622 | 1 | 2.856 | 184 | 64.4258
5.8 | 2.0957 | 1 | 2.856 | 184 | 64.4258
5.1 | 1.5657 | 1 | 2.856 | 184 | 64.4258
4.2 | 2.3658 | 1 | 2.856 | 184 | 64.4258
3.7 | 1.7899 | 1 | 2.856 | 184 | 64.4258
3.7 | 1.7899 | 1 | 2.856 | 184 | 64.4258
3.5 | 1.472 | 1 | 2.856 | 184 | 64.4258
3.5 | 1.2751 | 1 | 2.856 | 184 | 64.4258
3.5 | 1.0084 | 1 | 2.856 | 184 | 64.4258
3.1 | 0.9684 | 1 | 2.856 | 184 | 64.4258
2.9 | 0.8139 | 1 | 2.856 | 184 | 64.4258
2.7 | 0.73641 | 1 | 2.856 | 184 | 64.4258
2.8 | 0.60461 | 1 | 2.856 | 184 | 64.4258
2.7 | 0.66023 | 1 | 2.856 | 184 | 64.4258
2.5 | 0.46806 | 1 | 2.856 | 184 | 64.4258
2.7 | 0.58516 | 1 | 2.856 | 184 | 64.4258
3.9 | 1.4706 | 1 | 2.856 | 184 | 64.4258
5.2 | 2.4359 | 1 | 2.856 | 184 | 64.4258
6.1 | 2.6325 | 1 | 2.856 | 184 | 64.4258
6.8 | 2.8396 | 1 | 2.856 | 184 | 64.4258
7.3 | 2.9426 | 1 | 2.856 | 184 | 64.4258
7.5 | 2.9501 | 1 | 2.856 | 184 | 64.4258
7.1 | 2.9327 | 1 | 2.856 | 184 | 64.4258
6.7 | 2.9609 | 1 | 2.856 | 184 | 64.4258
6.5 | 2.5653 | 1 | 2.856 | 184 | 64.4258
5.2 | 2.2782 | 1 | 2.856 | 184 | 64.4258
5.5 | 2.3307 | 1 | 2.856 | 184 | 64.4258
5.5 | 2.404 | 1 | 2.856 | 184 | 64.4258
4.3 | 2.7772 | 1 | 2.856 | 184 | 64.4258
3.1 | 2.316 | 1 | 2.856 | 184 | 64.4258
2.8 | 2.1482 | 1 | 2.856 | 184 | 64.4258
2.6 | 2.1203 | 1 | 2.856 | 184 | 64.4258
2.6 | 2.1626 | 1 | 2.856 | 184 | 64.4258
2.8 | 2.3593 | 1 | 2.856 | 184 | 64.4258
2.9 | 2.6317 | 1 | 2.856 | 184 | 64.4258
3.3 | 3.0726 | 1 | 2.856 | 184 | 64.4258
3.8 | 3.4779 | 1 | 2.856 | 184 | 64.4258
4 | 3.7214 | 1 | 2.856 | 184 | 64.4258
4.4 | 4.0254 | 1 | 2.856 | 184 | 64.4258
4.8 | 4.3281 | 1 | 2.856 | 184 | 64.4258
5.2 | 4.6294 | 1 | 2.856 | 184 | 64.4258
5.5 | 4.7854 | 1 | 2.856 | 184 | 64.4258
5.5 | 4.7399 | 1 | 2.856 | 184 | 64.4258
5.7 | 4.7528 | 1 | 2.856 | 184 | 64.4258
5.7 | 4.3993 | 1 | 2.856 | 184 | 64.4258
5.8 | 4.0716 | 1 | 2.856 | 184 | 64.4258
6.3 | 4.2153 | 1 | 2.856 | 184 | 64.4258
6.1 | 3.9492 | 1 | 2.856 | 184 | 64.4258
6.1 | 3.8323 | 1 | 2.856 | 184 | 64.4258
6.2 | 3.8094 | 1 | 2.856 | 184 | 64.4258
4.5 | 2.6179 | 1 | 2.856 | 184 | 64.4258
2.5 | 0.58429 | 1 | 2.856 | 184 | 64.4258
1.3 | -0.40823 | 1 | 2.856 | 184 | 64.4258
2.3 | 0.62653 | 1 | 2.856 | 184 | 64.4258
2.1 | 0.54951 | 1 | 2.856 | 184 | 64.4258
1.1 | -0.037564 | 1 | 2.856 | 184 | 64.4258
0.5 | -0.456 | 1 | 2.856 | 184 | 64.4258
-0.6 | -1.2087 | 1 | 2.856 | 184 | 64.4258
-0.3 | -0.67695 | 1 | 2.856 | 184 | 64.4258
-0.8 | -1.3265 | 1 | 2.856 | 184 | 64.4258
-0.2 | -0.93697 | 1 | 2.856 | 184 | 64.4258
-0.2 | -0.70045 | 1 | 2.856 | 184 | 64.4258
0.9 | -0.49075 | 1 | 2.856 | 184 | 64.4258
2.2 | 1.1096 | 1 | 2.856 | 184 | 64.4258
3.3 | 1.7829 | 1 | 2.856 | 184 | 64.4258
4.6 | 2.639 | 1 | 2.856 | 184 | 64.4258
5.7 | 3.7035 | 1 | 2.856 | 184 | 64.4258
6.9 | 4.7818 | 1 | 2.856 | 184 | 64.4258
7.7 | 5.4839 | 1 | 2.856 | 184 | 64.4258
7.9 | 5.8401 | 1 | 2.856 | 184 | 64.4258
8.3 | 6.2585 | 1 | 2.856 | 184 | 64.4258
8.7 | 6.5881 | 1 | 2.856 | 184 | 64.4258
8.5 | 6.6694 | 1 | 2.856 | 184 | 64.4258
8.8 | 6.8164 | 1 | 2.856 | 184 | 64.4258
8.3 | 6.4803 | 1 | 2.856 | 184 | 64.4258
7.8 | 6.3697 | 1 | 2.856 | 184 | 64.4258
8 | 6.6536 | 1 | 2.856 | 184 | 64.4258
8.5 | 7.0388 | 1 | 2.856 | 184 | 64.4258
8.3 | 6.9416 | 1 | 2.856 | 184 | 64.4258
8.2 | 6.8923 | 1 | 2.856 | 184 | 64.4258
7.9 | 6.6982 | 1 | 2.856 | 184 | 64.4258
7.7 | 6.4116 | 1 | 2.856 | 184 | 64.4258
7.9 | 6.6032 | 1 | 2.856 | 184 | 64.4258
8.3 | 6.9403 | 1 | 2.856 | 184 | 64.4258
8.6 | 7.2276 | 1 | 2.856 | 184 | 64.4258
9.1 | 7.7563 | 1 | 2.856 | 184 | 64.4258
9.3 | 8.1467 | 1 | 2.856 | 184 | 64.4258
9.6 | 8.3373 | 1 | 2.856 | 184 | 64.4258
9.9 | 8.6267 | 1 | 2.856 | 184 | 64.4258
10 | 8.8242 | 1 | 2.856 | 184 | 64.4258
10 | 8.9781 | 1 | 2.856 | 184 | 64.4258
10.1 | 9.0749 | 1 | 2.856 | 184 | 64.4258
9.9 | 8.88 | 1 | 2.856 | 184 | 64.4258
9.7 | 8.7369 | 1 | 2.856 | 184 | 64.4258
9.6 | 8.3349 | 1 | 2.856 | 184 | 64.4258
9.1 | 8.1523 | 1 | 2.856 | 184 | 64.4258
8.7 | 7.9645 | 1 | 2.856 | 184 | 64.4258
8.4 | 7.7211 | 1 | 2.856 | 184 | 64.4258
8.3 | 7.623 | 1 | 2.856 | 184 | 64.4258
8.2 | 7.6263 | 1 | 2.856 | 184 | 64.4258
8.3 | 7.827 | 1 | 2.856 | 184 | 64.4258
8.4 | 7.8228 | 1 | 2.856 | 184 | 64.4258
8.4 | 7.8225 | 1 | 2.856 | 184 | 64.4258
8.4 | 7.8739 | 1 | 2.856 | 184 | 64.4258
8.3 | 7.9304 | 1 | 2.856 | 184 | 64.4258
8.4 | 7.8739 | 1 | 2.856 | 184 | 64.4258
8.1 | 7.7843 | 1 | 2.856 | 184 | 64.4258
8 | 7.7371 | 1 | 2.856 | 184 | 64.4258
7.9 | 7.5861 | 1 | 2.856 | 184 | 64.4258
7.6 | 7.2377 | 1 | 2.856 | 184 | 64.4258
7.3 | 6.691 | 1 | 2.856 | 184 | 64.4258
7.3 | 6.6913 | 1 | 2.856 | 184 | 64.4258
7.8 | 6.7891 | 1 | 2.856 | 184 | 64.4258
8.1 | 6.6973 | 1 | 2.856 | 184 | 64.4258
8.4 | 6.7512 | 1 | 2.856 | 184 | 64.4258
8.6 | 5.9681 | 1 | 2.856 | 184 | 64.4258
10 | 6.8263 | 1 | 2.856 | 184 | 64.4258
10.1 | 5.2258 | 1 | 2.856 | 184 | 64.4258
10 | 5.2504 | 1 | 2.856 | 184 | 64.4258
10.3 | 5.8842 | 1 | 2.856 | 184 | 64.4258
8.9 | 5.2137 | 1 | 2.856 | 184 | 64.4258
8.6 | 5.4815 | 1 | 2.856 | 184 | 64.4258
7.4 | 4.7882 | 1 | 2.856 | 184 | 64.4258
6.6 | 4.4936 | 1 | 2.856 | 184 | 64.4258
6.5 | 4.4005 | 1 | 2.856 | 184 | 64.4258
5.9 | 4.0852 | 1 | 2.856 | 184 | 64.4258
5.8 | 3.9504 | 1 | 2.856 | 184 | 64.4258
5.2 | 3.6718 | 1 | 2.856 | 184 | 64.4258
5 | 3.5652 | 1 | 2.856 | 184 | 64.4258
4.7 | 3.3619 | 1 | 2.856 | 184 | 64.4258
4.4 | 3.3675 | 1 | 2.856 | 184 | 64.4258
4.2 | 3.3017 | 1 | 2.856 | 184 | 64.4258
4.3 | 3.3991 | 1 | 2.856 | 184 | 64.4258
4.8 | 3.6687 | 1 | 2.856 | 184 | 64.4258
5.1 | 4.001 | 1 | 2.856 | 184 | 64.4258
5.2 | 4.0974 | 1 | 2.856 | 184 | 64.4258
7.1 | 5.3473 | 1 | 2.856 | 184 | 64.4258
8.6 | 6.277 | 1 | 2.856 | 184 | 64.4258
10.3 | 6.985 | 1 | 2.856 | 184 | 64.4258
11.8 | 7.1583 | 1 | 2.856 | 184 | 64.4258
12.1 | 7.0058 | 1 | 2.856 | 184 | 64.4258
11.8 | 7.7434 | 1 | 2.856 | 184 | 64.4258
10.9 | 7.3531 | 1 | 2.856 | 184 | 64.4258
11 | 7.6097 | 1 | 2.856 | 184 | 64.4258
10 | 7.6637 | 1 | 2.856 | 184 | 64.4258
9.5 | 8.0911 | 1 | 2.856 | 184 | 64.4258
9.7 | 8.3328 | 1 | 2.856 | 184 | 64.4258
8.7 | 7.6159 | 1 | 2.856 | 184 | 64.4258
7.8 | 6.6497 | 1 | 2.856 | 184 | 64.4258
6.5 | 5.7664 | 1 | 2.856 | 184 | 64.4258
5.5 | 4.7898 | 1 | 2.856 | 184 | 64.4258
4.3 | 3.5742 | 1 | 2.856 | 184 | 64.4258
2.8 | 2.2367 | 1 | 2.856 | 184 | 64.4258
1.4 | 0.78061 | 1 | 2.856 | 184 | 64.4258
-0.3 | -0.83509 | 1 | 2.856 | 184 | 64.4258
-1.5 | -2.1541 | 1 | 2.856 | 184 | 64.4258
-1.8 | -2.3725 | 1 | 2.856 | 184 | 64.4258
-1.7 | -2.3836 | 1 | 2.856 | 184 | 64.4258
-1.4 | -2.1648 | 1 | 2.856 | 184 | 64.4258
-1 | -1.7419 | 1 | 2.856 | 184 | 64.4258
0.8 | -0.35149 | 1 | 2.856 | 184 | 64.4258
2.9 | 1.1526 | 1 | 2.856 | 184 | 64.4258
5.1 | 1.9974 | 1 | 2.856 | 184 | 64.4258
5.5 | 1.6482 | 1 | 2.856 | 184 | 64.4258
5.9 | 1.8451 | 1 | 2.856 | 184 | 64.4258
5.7 | 1.7309 | 1 | 2.856 | 184 | 64.4258
6.2 | 1.892 | 1 | 2.856 | 184 | 64.4258
5.5 | 1.2803 | 1 | 2.856 | 184 | 64.4258
5.2 | 1.3514 | 1 | 2.856 | 184 | 64.4258
4 | 0.81302 | 1 | 2.856 | 184 | 64.4258
3.6 | 0.64446 | 1 | 2.856 | 184 | 64.4258
3.2 | 0.61503 | 1 | 2.856 | 184 | 64.4258
2.1 | 0.18046 | 1 | 2.856 | 184 | 64.4258
0.8 | -0.92171 | 1 | 2.856 | 184 | 64.4258
-0.2 | -1.3714 | 1 | 2.856 | 184 | 64.4258
-1.1 | -2.2242 | 1 | 2.856 | 184 | 64.4258
-1.8 | -2.7218 | 1 | 2.856 | 184 | 64.4258
-2.8 | -3.6136 | 1 | 2.856 | 184 | 64.4258
-3.2 | -3.9333 | 1 | 2.856 | 184 | 64.4258
-3.2 | -4.0297 | 1 | 2.856 | 184 | 64.4258
-3.2 | -3.8019 | 1 | 2.856 | 184 | 64.4258
-2.6 | -3.3219 | 1 | 2.856 | 184 | 64.4258
-2.6 | -3.422 | 1 | 2.856 | 184 | 64.4258
-1.4 | -2.4085 | 1 | 2.856 | 184 | 64.4258
0.6 | -1.0057 | 1 | 2.856 | 184 | 64.4258
2.7 | -0.053105 | 1 | 2.856 | 184 | 64.4258
5 | 1.7648 | 1 | 2.856 | 184 | 64.4258
5.9 | 1.9407 | 1 | 2.856 | 184 | 64.4258
7.4 | 3.4212 | 1 | 2.856 | 184 | 64.4258
7.5 | 3.655 | 1 | 2.856 | 184 | 64.4258
8.5 | 4.0826 | 1 | 2.856 | 184 | 64.4258
8.3 | 3.867 | 1 | 2.856 | 184 | 64.4258
7.2 | 3.5627 | 1 | 2.856 | 184 | 64.4258
5.7 | 2.7389 | 1 | 2.856 | 184 | 64.4258
5.7 | 2.7389 | 1 | 2.856 | 184 | 64.4258
4.2 | 2.2606 | 1 | 2.856 | 184 | 64.4258
3.4 | 1.8076 | 1 | 2.856 | 184 | 64.4258
2.3 | 1.048 | 1 | 2.856 | 184 | 64.4258
1.4 | 0.43565 | 1 | 2.856 | 184 | 64.4258
1.7 | 0.7826 | 1 | 2.856 | 184 | 64.4258
0.9 | 0.31155 | 1 | 2.856 | 184 | 64.4258
0.5 | 0.030096 | 1 | 2.856 | 184 | 64.4258
0.8 | 0.20836 | 1 | 2.856 | 184 | 64.4258
-1.1 | -1.8035 | 1 | 2.856 | 184 | 64.4258
-0.4 | -0.93275 | 1 | 2.856 | 184 | 64.4258
-0.9 | -1.4594 | 1 | 2.856 | 184 | 64.4258
0.7 | -0.022042 | 1 | 2.856 | 184 | 64.4258
1.5 | 0.79509 | 1 | 2.856 | 184 | 64.4258
3.4 | 2.1699 | 1 | 2.856 | 184 | 64.4258
5.4 | 3.3943 | 1 | 2.856 | 184 | 64.4258
8.1 | 4.7584 | 1 | 2.856 | 184 | 64.4258
9.5 | 5.5191 | 1 | 2.856 | 184 | 64.4258
10.2 | 5.0321 | 1 | 2.856 | 184 | 64.4258
10.8 | 5.7782 | 1 | 2.856 | 184 | 64.4258
9.2 | 5.0693 | 1 | 2.856 | 184 | 64.4258
8.5 | 4.7069 | 1 | 2.856 | 184 | 64.4258
7.9 | 4.4299 | 1 | 2.856 | 184 | 64.4258
7.1 | 4.1894 | 1 | 2.856 | 184 | 64.4258
6.9 | 4.2338 | 1 | 2.856 | 184 | 64.4258
7 | 4.4393 | 1 | 2.856 | 184 | 64.4258
7.2 | 4.8611 | 1 | 2.856 | 184 | 64.4258
6.7 | 5.2341 | 1 | 2.856 | 184 | 64.4258
6.4 | 5.624 | 1 | 2.856 | 184 | 64.4258
6 | 5.5617 | 1 | 2.856 | 184 | 64.4258
6.3 | 5.8576 | 1 | 2.856 | 184 | 64.4258
6.5 | 6.0546 | 1 | 2.856 | 184 | 64.4258
6.5 | 6.2997 | 1 | 2.856 | 184 | 64.4258
6.6 | 6.3991 | 1 | 2.856 | 184 | 64.4258
6.6 | 6.3991 | 1 | 2.856 | 184 | 64.4258
6.5 | 6.3994 | 1 | 2.856 | 184 | 64.4258
6.6 | 6.4991 | 1 | 2.856 | 184 | 64.4258
7 | 6.6466 | 1 | 2.856 | 184 | 64.4258
7.6 | 7.2908 | 1 | 2.856 | 184 | 64.4258
8 | 7.4328 | 1 | 2.856 | 184 | 64.4258
8.6 | 7.6205 | 1 | 2.856 | 184 | 64.4258
9.1 | 7.7608 | 1 | 2.856 | 184 | 64.4258
9.9 | 8.1381 | 1 | 2.856 | 184 | 64.4258
9.9 | 8.0425 | 1 | 2.856 | 184 | 64.4258
9.9 | 8.1381 | 1 | 2.856 | 184 | 64.4258
9.9 | 8.0416 | 1 | 2.856 | 184 | 64.4258
10 | 8.1363 | 1 | 2.856 | 184 | 64.4258
9.8 | 7.8053 | 1 | 2.856 | 184 | 64.4258
8.7 | 7.2792 | 1 | 2.856 | 184 | 64.4258
8.6 | 7.2794 | 1 | 2.856 | 184 | 64.4258
8.3 | 7.1825 | 1 | 2.856 | 184 | 64.4258
8 | 7.1345 | 1 | 2.856 | 184 | 64.4258
7.8 | 6.891 | 1 | 2.856 | 184 | 64.4258
7.7 | 6.7937 | 1 | 2.856 | 184 | 64.4258
7.2 | 6.4028 | 1 | 2.856 | 184 | 64.4258
6.3 | 5.6183 | 1 | 2.856 | 184 | 64.4258
6 | 5.6566 | 1 | 2.856 | 184 | 64.4258
5.6 | 5.2609 | 1 | 2.856 | 184 | 64.4258
5.6 | 5.2609 | 1 | 2.856 | 184 | 64.4258
5.4 | 5.063 | 1 | 2.856 | 184 | 64.4258
5.1 | 4.7662 | 1 | 2.856 | 184 | 64.4258
5.7 | 5.36 | 1 | 2.856 | 184 | 64.4258
6.4 | 5.9553 | 1 | 2.856 | 184 | 64.4258
7.2 | 6.4028 | 1 | 2.856 | 184 | 64.4258
8.6 | 7.1367 | 1 | 2.856 | 184 | 64.4258
9.4 | 7.3821 | 1 | 2.856 | 184 | 64.4258
9.7 | 7.3894 | 1 | 2.856 | 184 | 64.4258
9.2 | 6.7469 | 1 | 2.856 | 184 | 64.4258
9.6 | 7.0296 | 1 | 2.856 | 184 | 64.4258
9.3 | 6.8384 | 1 | 2.856 | 184 | 64.4258
9 | 6.5604 | 1 | 2.856 | 184 | 64.4258
8.3 | 6.3026 | 1 | 2.856 | 184 | 64.4258
7.4 | 5.5004 | 1 | 2.856 | 184 | 64.4258
7 | 5.2097 | 1 | 2.856 | 184 | 64.4258
5.4 | 4.3783 | 1 | 2.856 | 184 | 64.4258
6.1 | 4.8765 | 1 | 2.856 | 184 | 64.4258
5.4 | 4.5113 | 1 | 2.856 | 184 | 64.4258
4.9 | 4.114 | 1 | 2.856 | 184 | 64.4258
4.2 | 3.4325 | 1 | 2.856 | 184 | 64.4258
4.7 | 3.9195 | 1 | 2.856 | 184 | 64.4258
4.4 | 3.7149 | 1 | 2.856 | 184 | 64.4258
4.8 | 4.017 | 1 | 2.856 | 184 | 64.4258
4.9 | 4.1144 | 1 | 2.856 | 184 | 64.4258
4.7 | 4.0084 | 1 | 2.856 | 184 | 64.4258
4.8 | 4.0174 | 1 | 2.856 | 184 | 64.4258
5 | 4.4375 | 1 | 2.856 | 184 | 64.4258
6 | 5.0049 | 1 | 2.856 | 184 | 64.4258
6.7 | 5.591 | 1 | 2.856 | 184 | 64.4258
6.8 | 5.9193 | 1 | 2.856 | 184 | 64.4258
7.1 | 6.1169 | 1 | 2.856 | 184 | 64.4258
7.6 | 6.1363 | 1 | 2.856 | 184 | 64.4258
8.9 | 7.0062 | 1 | 2.856 | 184 | 64.4258
9.5 | 6.7271 | 1 | 2.856 | 184 | 64.4258
7.1 | 5.2221 | 1 | 2.856 | 184 | 64.4258
8.1 | 5.7747 | 1 | 2.856 | 184 | 64.4258
6.4 | 5.1667 | 1 | 2.856 | 184 | 64.4258
6.3 | 4.9822 | 1 | 2.856 | 184 | 64.4258
5.5 | 4.3894 | 1 | 2.856 | 184 | 64.4258
6 | 4.3126 | 1 | 2.856 | 184 | 64.4258
5.5 | 4.0472 | 1 | 2.856 | 184 | 64.4258
5.5 | 4.0472 | 1 | 2.856 | 184 | 64.4258
5.3 | 3.9405 | 1 | 2.856 | 184 | 64.4258
4.1 | 3.4228 | 1 | 2.856 | 184 | 64.4258
4.9 | 3.9838 | 1 | 2.856 | 184 | 64.4258
4.5 | 3.8133 | 1 | 2.856 | 184 | 64.4258
4.4 | 3.8485 | 1 | 2.856 | 184 | 64.4258
4.7 | 4.0091 | 1 | 2.856 | 184 | 64.4258
4.8 | 4.1065 | 1 | 2.856 | 184 | 64.4258
4.5 | 3.9469 | 1 | 2.856 | 184 | 64.4258
5.3 | 4.5053 | 1 | 2.856 | 184 | 64.4258
6 | 5.0054 | 1 | 2.856 | 184 | 64.4258
6.5 | 4.9559 | 1 | 2.856 | 184 | 64.4258
7 | 5.0877 | 1 | 2.856 | 184 | 64.4258
7 | 5.0037 | 1 | 2.856 | 184 | 64.4258
4.7 | 3.9216 | 1 | 2.856 | 184 | 64.4258
5.6 | 4.4869 | 1 | 2.856 | 184 | 64.4258
6 | 4.5674 | 1 | 2.856 | 184 | 64.4258
7.5 | 5.0585 | 1 | 2.856 | 184 | 64.4258
5.3 | 3.8591 | 1 | 2.856 | 184 | 64.4258
5 | 3.6569 | 1 | 2.856 | 184 | 64.4258
4.8 | 3.4667 | 1 | 2.856 | 184 | 64.4258
4.4 | 3.1664 | 1 | 2.856 | 184 | 64.4258
3.7 | 2.8231 | 1 | 2.856 | 184 | 64.4258
3.1 | 2.4482 | 1 | 2.856 | 184 | 64.4258
2.9 | 2.2114 | 1 | 2.856 | 184 | 64.4258
2.3 | 1.8309 | 1 | 2.856 | 184 | 64.4258
3.1 | 2.5326 | 1 | 2.856 | 184 | 64.4258
3.3 | 2.7289 | 1 | 2.856 | 184 | 64.4258
3.5 | 3.0544 | 1 | 2.856 | 184 | 64.4258
3.8 | 3.2627 | 1 | 2.856 | 184 | 64.4258
3.8 | 2.6755 | 1 | 2.856 | 184 | 64.4258
3.6 | 2.484 | 1 | 2.856 | 184 | 64.4258
3.8 | 2.6761 | 1 | 2.856 | 184 | 64.4258
4.1 | 2.883 | 1 | 2.856 | 184 | 64.4258
5.1 | 3.7581 | 1 | 2.856 | 184 | 64.4258
6.3 | 4.3193 | 1 | 2.856 | 184 | 64.4258
6.7 | 4.0278 | 1 | 2.856 | 184 | 64.4258
7.3 | 4.4225 | 1 | 2.856 | 184 | 64.4258
7.7 | 4.2614 | 1 | 2.856 | 184 | 64.4258
8.1 | 4.7704 | 1 | 2.856 | 184 | 64.4258
8.4 | 4.964 | 1 | 2.856 | 184 | 64.4258
8.5 | 5.277 | 1 | 2.856 | 184 | 64.4258
8.6 | 5.2908 | 1 | 2.856 | 184 | 64.4258
7.5 | 4.4927 | 1 | 2.856 | 184 | 64.4258
6.7 | 4.4925 | 1 | 2.856 | 184 | 64.4258
5.8 | 3.5812 | 1 | 2.856 | 184 | 64.4258
6.1 | 3.2801 | 1 | 2.856 | 184 | 64.4258
5.7 | 2.9785 | 1 | 2.856 | 184 | 64.4258
5.7 | 2.9785 | 1 | 2.856 | 184 | 64.4258
5.3 | 2.6771 | 1 | 2.856 | 184 | 64.4258
5 | 2.753 | 1 | 2.856 | 184 | 64.4258
4.8 | 2.8052 | 1 | 2.856 | 184 | 64.4258
4.8 | 2.3961 | 1 | 2.856 | 184 | 64.4258
4.8 | 2.3961 | 1 | 2.856 | 184 | 64.4258
4.6 | 2.3239 | 1 | 2.856 | 184 | 64.4258
3.7 | 2.2654 | 1 | 2.856 | 184 | 64.4258
2.8 | 1.6772 | 1 | 2.856 | 184 | 64.4258
3.4 | 1.9371 | 1 | 2.856 | 184 | 64.4258
5.1 | 2.9702 | 1 | 2.856 | 184 | 64.4258
5.8 | 2.9925 | 1 | 2.856 | 184 | 64.4258
5.5 | 2.9066 | 1 | 2.856 | 184 | 64.4258
7.3 | 3.6962 | 1 | 2.856 | 184 | 64.4258
6.5 | 2.7095 | 1 | 2.856 | 184 | 64.4258
6.6 | 2.2038 | 1 | 2.856 | 184 | 64.4258
6.6 | 2.94 | 1 | 2.856 | 184 | 64.4258
6 | 2.2896 | 1 | 2.856 | 184 | 64.4258
5.8 | 2.1088 | 1 | 2.856 | 184 | 64.4258
5 | 1.6195 | 1 | 2.856 | 184 | 64.4258
4.5 | 1.2301 | 1 | 2.856 | 184 | 64.4258
4.1 | 0.79692 | 1 | 2.856 | 184 | 64.4258
3.9 | 1.0874 | 1 | 2.856 | 184 | 64.4258
3.4 | 1.1645 | 1 | 2.856 | 184 | 64.4258
2.9 | 1.0292 | 1 | 2.856 | 184 | 64.4258
2.1 | 0.68198 | 1 | 2.856 | 184 | 64.4258
2 | 0.83031 | 1 | 2.856 | 184 | 64.4258
1.4 | 0.43509 | 1 | 2.856 | 184 | 64.4258
1.4 | 0.563 | 1 | 2.856 | 184 | 64.4258
1.3 | 0.46066 | 1 | 2.856 | 184 | 64.4258
1.7 | 0.78155 | 1 | 2.856 | 184 | 64.4258
1.9 | 0.72846 | 1 | 2.856 | 184 | 64.4258
1.8 | 0.75438 | 1 | 2.856 | 184 | 64.4258
2.1 | 1.0578 | 1 | 2.856 | 184 | 64.4258
3 | 1.4921 | 1 | 2.856 | 184 | 64.4258
3.8 | 1.8659 | 1 | 2.856 | 184 | 64.4258
4.4 | 1.7351 | 1 | 2.856 | 184 | 64.4258
4.1 | 1.5261 | 1 | 2.856 | 184 | 64.4258
5 | 2 | 1 | 2.856 | 184 | 64.4258
4.2 | 1.771 | 1 | 2.856 | 184 | 64.4258
4.5 | 1.9413 | 1 | 2.856 | 184 | 64.4258
3.8 | 1.8627 | 1 | 2.856 | 184 | 64.4258
3.2 | 1.9773 | 1 | 2.856 | 184 | 64.4258
2.9 | 1.6463 | 1 | 2.856 | 184 | 64.4258
3.2 | 1.8605 | 1 | 2.856 | 184 | 64.4258
3.1 | 1.504 | 1 | 2.856 | 184 | 64.4258
2.9 | 1.5162 | 1 | 2.856 | 184 | 64.4258
2.7 | 1.5751 | 1 | 2.856 | 184 | 64.4258
2.7 | 1.4438 | 1 | 2.856 | 184 | 64.4258
2.5 | 1.3724 | 1 | 2.856 | 184 | 64.4258
2.3 | 1.2567 | 1 | 2.856 | 184 | 64.4258
2.2 | 1.2867 | 1 | 2.856 | 184 | 64.4258
2.1 | 1.1848 | 1 | 2.856 | 184 | 64.4258
2.1 | 1.1843 | 1 | 2.856 | 184 | 64.4258
2.2 | 1.2856 | 1 | 2.856 | 184 | 64.4258
2 | 1.2104 | 1 | 2.856 | 184 | 64.4258
2 | 1.3295 | 1 | 2.856 | 184 | 64.4258
2.3 | 1.6222 | 1 | 2.856 | 184 | 64.4258
3.5 | 2.3793 | 1 | 2.856 | 184 | 64.4258
4.7 | 2.7696 | 1 | 2.856 | 184 | 64.4258
6 | 2.9186 | 1 | 2.856 | 184 | 64.4258
5.3 | 2.301 | 1 | 2.856 | 184 | 64.4258
4.6 | 1.9064 | 1 | 2.856 | 184 | 64.4258
5 | 2.092 | 1 | 2.856 | 184 | 64.4258
4.5 | 1.5482 | 1 | 2.856 | 184 | 64.4258
4.1 | 1.5042 | 1 | 2.856 | 184 | 64.4258
3.6 | 1.1048 | 1 | 2.856 | 184 | 64.4258
3.3 | 1.1615 | 1 | 2.856 | 184 | 64.4258
2.9 | 0.73603 | 1 | 2.856 | 184 | 64.4258
3.2 | 0.94812 | 1 | 2.856 | 184 | 64.4258
3.3 | 1.0428 | 1 | 2.856 | 184 | 64.4258
2.3 | 1.1621 | 1 | 2.856 | 184 | 64.4258
1.4 | 0.8196 | 1 | 2.856 | 184 | 64.4258
1.1 | 0.76693 | 1 | 2.856 | 184 | 64.4258
0.9 | 0.69161 | 1 | 2.856 | 184 | 64.4258
0.5 | 0.24836 | 1 | 2.856 | 184 | 64.4258
0.3 | 0.1764 | 1 | 2.856 | 184 | 64.4258
0.5 | 0.37594 | 1 | 2.856 | 184 | 64.4258
0.9 | 0.56861 | 1 | 2.856 | 184 | 64.4258
0.6 | 0.35223 | 1 | 2.856 | 184 | 64.4258
1.2 | 0.86454 | 1 | 2.856 | 184 | 64.4258
1.9 | 1.348 | 1 | 2.856 | 184 | 64.4258
2.4 | 1.9647 | 1 | 2.856 | 184 | 64.4258
3 | 2.5552 | 1 | 2.856 | 184 | 64.4258
4.5 | 3.8067 | 1 | 2.856 | 184 | 64.4258
5.4 | 4.3702 | 1 | 2.856 | 184 | 64.4258
5.7 | 4.5704 | 1 | 2.856 | 184 | 64.4258
6.1 | 4.9559 | 1 | 2.856 | 184 | 64.4258
6.4 | 5.1546 | 1 | 2.856 | 184 | 64.4258
5.7 | 4.7952 | 1 | 2.856 | 184 | 64.4258
5.3 | 4.8668 | 1 | 2.856 | 184 | 64.4258
5.2 | 4.8625 | 1 | 2.856 | 184 | 64.4258
5.3 | 5.0571 | 1 | 2.856 | 184 | 64.4258
5.4 | 5.1563 | 1 | 2.856 | 184 | 64.4258
5.6 | 5.2583 | 1 | 2.856 | 184 | 64.4258
5.8 | 5.4561 | 1 | 2.856 | 184 | 64.4258
5.8 | 5.4561 | 1 | 2.856 | 184 | 64.4258
5.9 | 5.6524 | 1 | 2.856 | 184 | 64.4258
6.1 | 5.8508 | 1 | 2.856 | 184 | 64.4258
6.4 | 6.1984 | 1 | 2.856 | 184 | 64.4258
6.5 | 6.2978 | 1 | 2.856 | 184 | 64.4258
6.6 | 6.2477 | 1 | 2.856 | 184 | 64.4258
5 | 4.665 | 1 | 2.856 | 184 | 64.4258
4.4 | 3.8441 | 1 | 2.856 | 184 | 64.4258
4.4 | 3.8444 | 1 | 2.856 | 184 | 64.4258
5.4 | 4.7339 | 1 | 2.856 | 184 | 64.4258
6.8 | 5.7734 | 1 | 2.856 | 184 | 64.4258
8.2 | 6.5167 | 1 | 2.856 | 184 | 64.4258
9.7 | 6.8955 | 1 | 2.856 | 184 | 64.4258
10.9 | 7.348 | 1 | 2.856 | 184 | 64.4258
11.6 | 7.1631 | 1 | 2.856 | 184 | 64.4258
11.6 | 7.1631 | 1 | 2.856 | 184 | 64.4258
11.2 | 7.089 | 1 | 2.856 | 184 | 64.4258
11 | 7.1117 | 1 | 2.856 | 184 | 64.4258
10 | 6.6263 | 1 | 2.856 | 184 | 64.4258
9 | 6.5556 | 1 | 2.856 | 184 | 64.4258
9 | 6.5556 | 1 | 2.856 | 184 | 64.4258
7.9 | 6.2344 | 1 | 2.856 | 184 | 64.4258
7.6 | 6.0396 | 1 | 2.856 | 184 | 64.4258
7.9 | 6.0996 | 1 | 2.856 | 184 | 64.4258
8.5 | 6.7123 | 1 | 2.856 | 184 | 64.4258
8.2 | 6.7503 | 1 | 2.856 | 184 | 64.4258
8 | 6.9861 | 1 | 2.856 | 184 | 64.4258
7.6 | 7.0375 | 1 | 2.856 | 184 | 64.4258
7.9 | 7.3326 | 1 | 2.856 | 184 | 64.4258
8.3 | 7.6246 | 1 | 2.856 | 184 | 64.4258
8.3 | 7.8801 | 1 | 2.856 | 184 | 64.4258
9.1 | 8.2047 | 1 | 2.856 | 184 | 64.4258
9.3 | 8.3997 | 1 | 2.856 | 184 | 64.4258
9.8 | 8.5806 | 1 | 2.856 | 184 | 64.4258
9.6 | 8.4886 | 1 | 2.856 | 184 | 64.4258
9.7 | 8.4845 | 1 | 2.856 | 184 | 64.4258
10.1 | 8.6694 | 1 | 2.856 | 184 | 64.4258
10 | 8.8758 | 1 | 2.856 | 184 | 64.4258
9.9 | 9.1416 | 1 | 2.856 | 184 | 64.4258
9.8 | 9.1487 | 1 | 2.856 | 184 | 64.4258
10.2 | 9.542 | 1 | 2.856 | 184 | 64.4258
10.5 | 9.7294 | 1 | 2.856 | 184 | 64.4258
10.8 | 9.8095 | 1 | 2.856 | 184 | 64.4258
10.7 | 9.6068 | 1 | 2.856 | 184 | 64.4258
11 | 9.689 | 1 | 2.856 | 184 | 64.4258
10.9 | 9.593 | 1 | 2.856 | 184 | 64.4258
10.9 | 9.6976 | 1 | 2.856 | 184 | 64.4258
10.9 | 9.6976 | 1 | 2.856 | 184 | 64.4258
10.9 | 9.4912 | 1 | 2.856 | 184 | 64.4258
10 | 8.9295 | 1 | 2.856 | 184 | 64.4258
9.6 | 8.4912 | 1 | 2.856 | 184 | 64.4258
9.3 | 8.4027 | 1 | 2.856 | 184 | 64.4258
9.1 | 8.2077 | 1 | 2.856 | 184 | 64.4258
9.3 | 8.2014 | 1 | 2.856 | 184 | 64.4258
9.9 | 8.5813 | 1 | 2.856 | 184 | 64.4258
9.7 | 8.4884 | 1 | 2.856 | 184 | 64.4258
8.9 | 8.0135 | 1 | 2.856 | 184 | 64.4258
9.6 | 8.5944 | 1 | 2.856 | 184 | 64.4258
10.8 | 9.3478 | 1 | 2.856 | 184 | 64.4258
11 | 9.4383 | 1 | 2.856 | 184 | 64.4258
11.3 | 9.6755 | 1 | 2.856 | 184 | 64.4258
12.3 | 10.2205 | 1 | 2.856 | 184 | 64.4258
12 | 10.1389 | 1 | 2.856 | 184 | 64.4258
12.4 | 10.4169 | 1 | 2.856 | 184 | 64.4258
13.2 | 10.9175 | 1 | 2.856 | 184 | 64.4258
12.5 | 11.089 | 1 | 2.856 | 184 | 64.4258
12.4 | 11.2085 | 1 | 2.856 | 184 | 64.4258
12.3 | 11.1114 | 1 | 2.856 | 184 | 64.4258
12.1 | 11.0258 | 1 | 2.856 | 184 | 64.4258
11.9 | 10.9403 | 1 | 2.856 | 184 | 64.4258
12 | 11.0379 | 1 | 2.856 | 184 | 64.4258
11.7 | 10.9093 | 1 | 2.856 | 184 | 64.4258
11.3 | 10.7365 | 1 | 2.856 | 184 | 64.4258
11.1 | 10.6497 | 1 | 2.856 | 184 | 64.4258
11.4 | 10.7248 | 1 | 2.856 | 184 | 64.4258
11.4 | 10.6153 | 1 | 2.856 | 184 | 64.4258
11.3 | 10.6265 | 1 | 2.856 | 184 | 64.4258
11.3 | 10.6265 | 1 | 2.856 | 184 | 64.4258
11.1 | 10.5394 | 1 | 2.856 | 184 | 64.4258
11.3 | 10.6265 | 1 | 2.856 | 184 | 64.4258
11.7 | 10.9097 | 1 | 2.856 | 184 | 64.4258
12.2 | 11.1245 | 1 | 2.856 | 184 | 64.4258
12.5 | 11.307 | 1 | 2.856 | 184 | 64.4258
13.7 | 12.0838 | 1 | 2.856 | 184 | 64.4258
14.7 | 11.3124 | 1 | 2.856 | 184 | 64.4258
15.7 | 11.2161 | 1 | 2.856 | 184 | 64.4258
16.2 | 11.6131 | 1 | 2.856 | 184 | 64.4258
16.5 | 11.4629 | 1 | 2.856 | 184 | 64.4258
16.9 | 12.2318 | 1 | 2.856 | 184 | 64.4258
16.4 | 11.5093 | 1 | 2.856 | 184 | 64.4258
16.1 | 11.4283 | 1 | 2.856 | 184 | 64.4258
15 | 11.1953 | 1 | 2.856 | 184 | 64.4258
13.7 | 11.0822 | 1 | 2.856 | 184 | 64.4258
13.3 | 10.9105 | 1 | 2.856 | 184 | 64.4258
12.7 | 10.5998 | 1 | 2.856 | 184 | 64.4258
12.2 | 10.2271 | 1 | 2.856 | 184 | 64.4258
11.4 | 9.7705 | 1 | 2.856 | 184 | 64.4258
10.8 | 9.2467 | 1 | 2.856 | 184 | 64.4258
10.6 | 9.155 | 1 | 2.856 | 184 | 64.4258
8.6 | 7.8215 | 1 | 2.856 | 184 | 64.4258
9.2 | 8.105 | 1 | 2.856 | 184 | 64.4258
8.5 | 7.6236 | 1 | 2.856 | 184 | 64.4258
7.8 | 7.0393 | 1 | 2.856 | 184 | 64.4258
7.7 | 7.0397 | 1 | 2.856 | 184 | 64.4258
8.5 | 7.724 | 1 | 2.856 | 184 | 64.4258
8.3 | 7.8822 | 1 | 2.856 | 184 | 64.4258
9.8 | 9.1522 | 1 | 2.856 | 184 | 64.4258
11.3 | 10.1953 | 1 | 2.856 | 184 | 64.4258
12.6 | 10.8679 | 1 | 2.856 | 184 | 64.4258
12.9 | 11.0495 | 1 | 2.856 | 184 | 64.4258
13.1 | 10.9276 | 1 | 2.856 | 184 | 64.4258
14.3 | 11.3393 | 1 | 2.856 | 184 | 64.4258
14.3 | 11.1404 | 1 | 2.856 | 184 | 64.4258
13.7 | 10.6369 | 1 | 2.856 | 184 | 64.4258
13.7 | 9.7955 | 1 | 2.856 | 184 | 64.4258
12.7 | 9.2997 | 1 | 2.856 | 184 | 64.4258
12 | 8.9358 | 1 | 2.856 | 184 | 64.4258
11.5 | 8.6592 | 1 | 2.856 | 184 | 64.4258
10.5 | 8.0537 | 1 | 2.856 | 184 | 64.4258
10.3 | 8.0049 | 1 | 2.856 | 184 | 64.4258
9.2 | 8.3076 | 1 | 2.856 | 184 | 64.4258
8.1 | 7.9948 | 1 | 2.856 | 184 | 64.4258
7.9 | 7.7954 | 1 | 2.856 | 184 | 64.4258
7.9 | 7.7954 | 1 | 2.856 | 184 | 64.4258
7.7 | 7.7 | 1 | 2.856 | 184 | 64.4258
8 | 7.895 | 1 | 2.856 | 184 | 64.4258
7.7 | 7.7 | 1 | 2.856 | 184 | 64.4258
7.9 | 7.7952 | 1 | 2.856 | 184 | 64.4258
8.6 | 8.3872 | 1 | 2.856 | 184 | 64.4258
8.9 | 8.4743 | 1 | 2.856 | 184 | 64.4258
9.4 | 8.7581 | 1 | 2.856 | 184 | 64.4258
10.4 | 9.4225 | 1 | 2.856 | 184 | 64.4258
11.3 | 9.981 | 1 | 2.856 | 184 | 64.4258
12.7 | 10.4913 | 1 | 2.856 | 184 | 64.4258
12.4 | 10.2074 | 1 | 2.856 | 184 | 64.4258
11.8 | 10.0451 | 1 | 2.856 | 184 | 64.4258
13.8 | 9.1703 | 1 | 2.856 | 184 | 64.4258
12.7 | 7.9321 | 1 | 2.856 | 184 | 64.4258
11.6 | 8.0694 | 1 | 2.856 | 184 | 64.4258
10.2 | 8.6663 | 1 | 2.856 | 184 | 64.4258
8.7 | 6.9042 | 1 | 2.856 | 184 | 64.4258
8.8 | 6.6828 | 1 | 2.856 | 184 | 64.4258
9 | 7.3291 | 1 | 2.856 | 184 | 64.4258
8.9 | 6.9115 | 1 | 2.856 | 184 | 64.4258
8.4 | 6.5297 | 1 | 2.856 | 184 | 64.4258
8.1 | 6.4276 | 1 | 2.856 | 184 | 64.4258
8 | 6.4228 | 1 | 2.856 | 184 | 64.4258
7.8 | 6.3697 | 1 | 2.856 | 184 | 64.4258
7.7 | 6.3657 | 1 | 2.856 | 184 | 64.4258
8 | 6.653 | 1 | 2.856 | 184 | 64.4258
8.9 | 6.9989 | 1 | 2.856 | 184 | 64.4258
9.3 | 7.2831 | 1 | 2.856 | 184 | 64.4258
9.1 | 7.7557 | 1 | 2.856 | 184 | 64.4258
9.4 | 8.1918 | 1 | 2.856 | 184 | 64.4258
9.5 | 8.5922 | 1 | 2.856 | 184 | 64.4258
10.1 | 9.229 | 1 | 2.856 | 184 | 64.4258
11.1 | 9.7797 | 1 | 2.856 | 184 | 64.4258
11.3 | 10.2926 | 1 | 2.856 | 184 | 64.4258
12.3 | 11.1566 | 1 | 2.856 | 184 | 64.4258
11.4 | 9.86 | 1 | 2.856 | 184 | 64.4258
12.2 | 8.862 | 1 | 2.856 | 184 | 64.4258
11.8 | 8.0198 | 1 | 2.856 | 184 | 64.4258
11.1 | 7.7778 | 1 | 2.856 | 184 | 64.4258
10.4 | 7.6232 | 1 | 2.856 | 184 | 64.4258
9 | 6.8619 | 1 | 2.856 | 184 | 64.4258
8.7 | 6.363 | 1 | 2.856 | 184 | 64.4258
8.2 | 6.0721 | 1 | 2.856 | 184 | 64.4258
8.4 | 6.3916 | 1 | 2.856 | 184 | 64.4258
8.2 | 6.2926 | 1 | 2.856 | 184 | 64.4258
8 | 6.1923 | 1 | 2.856 | 184 | 64.4258
8.3 | 6.2957 | 1 | 2.856 | 184 | 64.4258
8.7 | 6.8981 | 1 | 2.856 | 184 | 64.4258
8.9 | 8.1093 | 1 | 2.856 | 184 | 64.4258
9.7 | 9.2624 | 1 | 2.856 | 184 | 64.4258
10.7 | 10.2506 | 1 | 2.856 | 184 | 64.4258
11.3 | 10.7319 | 1 | 2.856 | 184 | 64.4258
11.8 | 11.1127 | 1 | 2.856 | 184 | 64.4258
12.1 | 11.0175 | 1 | 2.856 | 184 | 64.4258
12.5 | 11.0781 | 1 | 2.856 | 184 | 64.4258
12.5 | 11.0775 | 1 | 2.856 | 184 | 64.4258
12.9 | 11.4629 | 1 | 2.856 | 184 | 64.4258
13.1 | 11.5456 | 1 | 2.856 | 184 | 64.4258
13.4 | 11.724 | 1 | 2.856 | 184 | 64.4258
13.8 | 12.1625 | 1 | 2.856 | 184 | 64.4258
13.2 | 11.9727 | 1 | 2.856 | 184 | 64.4258
13 | 11.6673 | 1 | 2.856 | 184 | 64.4258
13.3 | 9.5274 | 1 | 2.856 | 184 | 64.4258
11.8 | 8.0091 | 1 | 2.856 | 184 | 64.4258
10.8 | 6.9964 | 1 | 2.856 | 184 | 64.4258
10.2 | 6.8307 | 1 | 2.856 | 184 | 64.4258
9.1 | 6.5057 | 1 | 2.856 | 184 | 64.4258
8.4 | 5.9463 | 1 | 2.856 | 184 | 64.4258
8.1 | 5.7536 | 1 | 2.856 | 184 | 64.4258
8 | 5.6185 | 1 | 2.856 | 184 | 64.4258
7.7 | 5.2164 | 1 | 2.856 | 184 | 64.4258
7.6 | 5.3318 | 1 | 2.856 | 184 | 64.4258
7.1 | 4.9494 | 1 | 2.856 | 184 | 64.4258
6.5 | 4.4738 | 1 | 2.856 | 184 | 64.4258
6.7 | 4.6596 | 1 | 2.856 | 184 | 64.4258
6.6 | 4.5661 | 1 | 2.856 | 184 | 64.4258
7.2 | 5.0426 | 1 | 2.856 | 184 | 64.4258
8.5 | 5.7848 | 1 | 2.856 | 184 | 64.4258
9.5 | 6.7012 | 1 | 2.856 | 184 | 64.4258
10.4 | 6.7235 | 1 | 2.856 | 184 | 64.4258
9.2 | 7.6519 | 1 | 2.856 | 184 | 64.4258
10.5 | 7.1443 | 1 | 2.856 | 184 | 64.4258
10.6 | 7.4898 | 1 | 2.856 | 184 | 64.4258
11.9 | 7.6453 | 1 | 2.856 | 184 | 64.4258
11.7 | 7.1169 | 1 | 2.856 | 184 | 64.4258
8.6 | 6.2608 | 1 | 2.856 | 184 | 64.4258
9.9 | 6.5624 | 1 | 2.856 | 184 | 64.4258
9.3 | 5.9428 | 1 | 2.856 | 184 | 64.4258
8.9 | 6.1121 | 1 | 2.856 | 184 | 64.4258
8.2 | 5.8475 | 1 | 2.856 | 184 | 64.4258
7.7 | 5.6827 | 1 | 2.856 | 184 | 64.4258
7.7 | 5.5533 | 1 | 2.856 | 184 | 64.4258
6.8 | 5.0973 | 1 | 2.856 | 184 | 64.4258
6.1 | 4.8689 | 1 | 2.856 | 184 | 64.4258
6.7 | 5.2221 | 1 | 2.856 | 184 | 64.4258
5.6 | 4.477 | 1 | 2.856 | 184 | 64.4258
5.2 | 4.179 | 1 | 2.856 | 184 | 64.4258
3.9 | 3.3535 | 1 | 2.856 | 184 | 64.4258
4 | 3.32 | 1 | 2.856 | 184 | 64.4258
3.4 | 2.8197 | 1 | 2.856 | 184 | 64.4258
4.3 | 3.5253 | 1 | 2.856 | 184 | 64.4258
6 | 4.643 | 1 | 2.856 | 184 | 64.4258
8.1 | 5.7619 | 1 | 2.856 | 184 | 64.4258
8.8 | 5.7835 | 1 | 2.856 | 184 | 64.4258
9.1 | 5.6196 | 1 | 2.856 | 184 | 64.4258
8.6 | 5.3658 | 1 | 2.856 | 184 | 64.4258
7.4 | 5.7136 | 1 | 2.856 | 184 | 64.4258
8.4 | 6.5251 | 1 | 2.856 | 184 | 64.4258
9.6 | 6.0278 | 1 | 2.856 | 184 | 64.4258
8 | 5.7552 | 1 | 2.856 | 184 | 64.4258
8.7 | 5.5749 | 1 | 2.856 | 184 | 64.4258
7.9 | 4.5176 | 1 | 2.856 | 184 | 64.4258
6.8 | 4.2041 | 1 | 2.856 | 184 | 64.4258
5.2 | 3.5085 | 1 | 2.856 | 184 | 64.4258
4.1 | 2.7487 | 1 | 2.856 | 184 | 64.4258
4.5 | 3.0488 | 1 | 2.856 | 184 | 64.4258
3.6 | 2.4723 | 1 | 2.856 | 184 | 64.4258
3.9 | 2.5581 | 1 | 2.856 | 184 | 64.4258
3.5 | 2.256 | 1 | 2.856 | 184 | 64.4258
3.6 | 2.4723 | 1 | 2.856 | 184 | 64.4258
3.6 | 2.4723 | 1 | 2.856 | 184 | 64.4258
3.3 | 2.3873 | 1 | 2.856 | 184 | 64.4258
3.3 | 2.5118 | 1 | 2.856 | 184 | 64.4258
3.5 | 2.8337 | 1 | 2.856 | 184 | 64.4258
4.7 | 3.5713 | 1 | 2.856 | 184 | 64.4258
5.4 | 4.159 | 1 | 2.856 | 184 | 64.4258
5.8 | 4.4559 | 1 | 2.856 | 184 | 64.4258
7.4 | 5.3699 | 1 | 2.856 | 184 | 64.4258
6.8 | 4.6843 | 1 | 2.856 | 184 | 64.4258
8.7 | 5.7004 | 1 | 2.856 | 184 | 64.4258
6.2 | 5.0605 | 1 | 2.856 | 184 | 64.4258
8.5 | 6.0535 | 1 | 2.856 | 184 | 64.4258
6.6 | 4.5809 | 1 | 2.856 | 184 | 64.4258
6.1 | 4.4017 | 1 | 2.856 | 184 | 64.4258
6.7 | 4.5922 | 1 | 2.856 | 184 | 64.4258
6.9 | 4.4166 | 1 | 2.856 | 184 | 64.4258
5.5 | 4.0434 | 1 | 2.856 | 184 | 64.4258
5.1 | 3.8732 | 1 | 2.856 | 184 | 64.4258
4.5 | 3.594 | 1 | 2.856 | 184 | 64.4258
4.4 | 3.3698 | 1 | 2.856 | 184 | 64.4258
4.3 | 3.2732 | 1 | 2.856 | 184 | 64.4258
4.2 | 3.4325 | 1 | 2.856 | 184 | 64.4258
3.8 | 3.0007 | 1 | 2.856 | 184 | 64.4258
4.4 | 3.6277 | 1 | 2.856 | 184 | 64.4258
4.6 | 3.9107 | 1 | 2.856 | 184 | 64.4258
4.5 | 3.595 | 1 | 2.856 | 184 | 64.4258
4.3 | 3.4016 | 1 | 2.856 | 184 | 64.4258
4.8 | 3.8869 | 1 | 2.856 | 184 | 64.4258
5.3 | 4.1966 | 1 | 2.856 | 184 | 64.4258
5.7 | 4.3652 | 1 | 2.856 | 184 | 64.4258
6.2 | 4.7574 | 1 | 2.856 | 184 | 64.4258
6.9 | 4.9938 | 1 | 2.856 | 184 | 64.4258
7.5 | 4.937 | 1 | 2.856 | 184 | 64.4258
8.5 | 5.7317 | 1 | 2.856 | 184 | 64.4258
8.7 | 6.6843 | 1 | 2.856 | 184 | 64.4258
6.8 | 5.112 | 1 | 2.856 | 184 | 64.4258
6.6 | 4.5883 | 1 | 2.856 | 184 | 64.4258
6.1 | 4.9682 | 1 | 2.856 | 184 | 64.4258
6.6 | 5.0525 | 1 | 2.856 | 184 | 64.4258
5.7 | 4.2391 | 1 | 2.856 | 184 | 64.4258
5.5 | 4.0487 | 1 | 2.856 | 184 | 64.4258
5 | 3.7818 | 1 | 2.856 | 184 | 64.4258
3.9 | 3.2285 | 1 | 2.856 | 184 | 64.4258
3.5 | 2.8376 | 1 | 2.856 | 184 | 64.4258
3 | 2.5606 | 1 | 2.856 | 184 | 64.4258
2.8 | 2.2367 | 1 | 2.856 | 184 | 64.4258
1.9 | 1.3546 | 1 | 2.856 | 184 | 64.4258
1.4 | 0.82393 | 1 | 2.856 | 184 | 64.4258
1.6 | 1.0202 | 1 | 2.856 | 184 | 64.4258
0.3 | -0.21042 | 1 | 2.856 | 184 | 64.4258
1 | 0.67045 | 1 | 2.856 | 184 | 64.4258
1.3 | 0.72014 | 1 | 2.856 | 184 | 64.4258
2.5 | 1.6964 | 1 | 2.856 | 184 | 64.4258
3.2 | 2.4171 | 1 | 2.856 | 184 | 64.4258
3.9 | 3.098 | 1 | 2.856 | 184 | 64.4258
4.1 | 3.5537 | 1 | 2.856 | 184 | 64.4258
4.8 | 3.8859 | 1 | 2.856 | 184 | 64.4258
6.7 | 5.0148 | 1 | 2.856 | 184 | 64.4258
8.3 | 5.6247 | 1 | 2.856 | 184 | 64.4258
8.2 | 4.8336 | 1 | 2.856 | 184 | 64.4258
7.2 | 4.6171 | 1 | 2.856 | 184 | 64.4258
7.9 | 4.6773 | 1 | 2.856 | 184 | 64.4258
7.4 | 4.3792 | 1 | 2.856 | 184 | 64.4258
6.6 | 4.2634 | 1 | 2.856 | 184 | 64.4258
6.3 | 4.0661 | 1 | 2.856 | 184 | 64.4258
5.9 | 4.0947 | 1 | 2.856 | 184 | 64.4258
5.8 | 4.1245 | 1 | 2.856 | 184 | 64.4258
5.3 | 3.6118 | 1 | 2.856 | 184 | 64.4258
4.2 | 2.9729 | 1 | 2.856 | 184 | 64.4258
3.4 | 2.6134 | 1 | 2.856 | 184 | 64.4258
3 | 2.307 | 1 | 2.856 | 184 | 64.4258
2.7 | 1.9734 | 1 | 2.856 | 184 | 64.4258
2.1 | 1.6327 | 1 | 2.856 | 184 | 64.4258
1.6 | 1.3882 | 1 | 2.856 | 184 | 64.4258
2.1 | 1.7575 | 1 | 2.856 | 184 | 64.4258
2.1 | 1.7575 | 1 | 2.856 | 184 | 64.4258
2.6 | 2.1664 | 1 | 2.856 | 184 | 64.4258
4.4 | 3.5 | 1 | 2.856 | 184 | 64.4258
5.1 | 3.6268 | 1 | 2.856 | 184 | 64.4258
6.9 | 4.5452 | 1 | 2.856 | 184 | 64.4258
6.7 | 3.9018 | 1 | 2.856 | 184 | 64.4258
8 | 4.5532 | 1 | 2.856 | 184 | 64.4258
8.2 | 4.7305 | 1 | 2.856 | 184 | 64.4258
8.3 | 5.0026 | 1 | 2.856 | 184 | 64.4258
8.3 | 4.7446 | 1 | 2.856 | 184 | 64.4258
9.2 | 5.063 | 1 | 2.856 | 184 | 64.4258
8.7 | 4.4171 | 1 | 2.856 | 184 | 64.4258
8.2 | 4.5018 | 1 | 2.856 | 184 | 64.4258
7.7 | 4.5742 | 1 | 2.856 | 184 | 64.4258
7.4 | 4.6066 | 1 | 2.856 | 184 | 64.4258
7.3 | 4.7495 | 1 | 2.856 | 184 | 64.4258
6.8 | 4.6898 | 1 | 2.856 | 184 | 64.4258
6.8 | 4.6887 | 1 | 2.856 | 184 | 64.4258
6.5 | 4.6143 | 1 | 2.856 | 184 | 64.4258
6.1 | 4.6583 | 1 | 2.856 | 184 | 64.4258
5.9 | 4.7726 | 1 | 2.856 | 184 | 64.4258
5.7 | 4.7123 | 1 | 2.856 | 184 | 64.4258
5.2 | 4.8651 | 1 | 2.856 | 184 | 64.4258
5.2 | 5.1032 | 1 | 2.856 | 184 | 64.4258
5.3 | 5.2029 | 1 | 2.856 | 184 | 64.4258
5.6 | 5.2609 | 1 | 2.856 | 184 | 64.4258
5.6 | 5.3566 | 1 | 2.856 | 184 | 64.4258
5.9 | 5.4619 | 1 | 2.856 | 184 | 64.4258
6.8 | 6.1554 | 1 | 2.856 | 184 | 64.4258
6.8 | 6.2521 | 1 | 2.856 | 184 | 64.4258
7.3 | 6.404 | 1 | 2.856 | 184 | 64.4258
7.5 | 6.7435 | 1 | 2.856 | 184 | 64.4258
7.7 | 6.6965 | 1 | 2.856 | 184 | 64.4258
8.2 | 7.1811 | 1 | 2.856 | 184 | 64.4258
8 | 6.9871 | 1 | 2.856 | 184 | 64.4258
8.1 | 6.7496 | 1 | 2.856 | 184 | 64.4258
8.1 | 6.8917 | 1 | 2.856 | 184 | 64.4258
7.8 | 6.7935 | 1 | 2.856 | 184 | 64.4258
7.7 | 6.7928 | 1 | 2.856 | 184 | 64.4258
7.5 | 6.7435 | 1 | 2.856 | 184 | 64.4258
7.5 | 6.7435 | 1 | 2.856 | 184 | 64.4258
7.3 | 6.6453 | 1 | 2.856 | 184 | 64.4258
7.1 | 6.4492 | 1 | 2.856 | 184 | 64.4258
6.9 | 6.2531 | 1 | 2.856 | 184 | 64.4258
6.8 | 6.1551 | 1 | 2.856 | 184 | 64.4258
6.7 | 6.1535 | 1 | 2.856 | 184 | 64.4258
6.6 | 6.1522 | 1 | 2.856 | 184 | 64.4258
6.8 | 6.2518 | 1 | 2.856 | 184 | 64.4258
6.7 | 6.2508 | 1 | 2.856 | 184 | 64.4258
7.1 | 6.4492 | 1 | 2.856 | 184 | 64.4258
7.4 | 6.5972 | 1 | 2.856 | 184 | 64.4258
7.6 | 7.0389 | 1 | 2.856 | 184 | 64.4258
8.3 | 7.2791 | 1 | 2.856 | 184 | 64.4258
9.1 | 7.5666 | 1 | 2.856 | 184 | 64.4258
9.5 | 7.7099 | 1 | 2.856 | 184 | 64.4258
10 | 8.1363 | 1 | 2.856 | 184 | 64.4258
9.5 | 7.8527 | 1 | 2.856 | 184 | 64.4258
9.7 | 7.9473 | 1 | 2.856 | 184 | 64.4258
9.2 | 7.4253 | 1 | 2.856 | 184 | 64.4258
9.2 | 7.4261 | 1 | 2.856 | 184 | 64.4258
9.1 | 7.3313 | 1 | 2.856 | 184 | 64.4258
8.9 | 7.2348 | 1 | 2.856 | 184 | 64.4258
8.7 | 7.1388 | 1 | 2.856 | 184 | 64.4258
8.7 | 7.1388 | 1 | 2.856 | 184 | 64.4258
8.7 | 7.1395 | 1 | 2.856 | 184 | 64.4258
8.2 | 6.7553 | 1 | 2.856 | 184 | 64.4258
7.7 | 6.462 | 1 | 2.856 | 184 | 64.4258
7.4 | 6.2663 | 1 | 2.856 | 184 | 64.4258
7.3 | 6.3104 | 1 | 2.856 | 184 | 64.4258
7.1 | 6.2108 | 1 | 2.856 | 184 | 64.4258
6.9 | 6.1108 | 1 | 2.856 | 184 | 64.4258
7.2 | 6.4036 | 1 | 2.856 | 184 | 64.4258
7.3 | 6.4058 | 1 | 2.856 | 184 | 64.4258
7.8 | 6.796 | 1 | 2.856 | 184 | 64.4258
8 | 6.99 | 1 | 2.856 | 184 | 64.4258
8.9 | 7.6673 | 1 | 2.856 | 184 | 64.4258
9.7 | 8.1438 | 1 | 2.856 | 184 | 64.4258
10.4 | 8.4236 | 1 | 2.856 | 184 | 64.4258
11.2 | 8.7945 | 1 | 2.856 | 184 | 64.4258
12.3 | 7.9941 | 1 | 2.856 | 184 | 64.4258
13.6 | 8.1791 | 1 | 2.856 | 184 | 64.4258
12.1 | 7.464 | 1 | 2.856 | 184 | 64.4258
12.3 | 7.6368 | 1 | 2.856 | 184 | 64.4258
12.1 | 7.35 | 1 | 2.856 | 184 | 64.4258
11.3 | 6.962 | 1 | 2.856 | 184 | 64.4258
9 | 5.5498 | 1 | 2.856 | 184 | 64.4258
7.8 | 4.8939 | 1 | 2.856 | 184 | 64.4258
8.4 | 5.166 | 1 | 2.856 | 184 | 64.4258
7.7 | 4.9197 | 1 | 2.856 | 184 | 64.4258
6.2 | 4.1721 | 1 | 2.856 | 184 | 64.4258
5.9 | 4.0938 | 1 | 2.856 | 184 | 64.4258
5.8 | 4.3313 | 1 | 2.856 | 184 | 64.4258
6 | 5.0039 | 1 | 2.856 | 184 | 64.4258
5.7 | 4.9394 | 1 | 2.856 | 184 | 64.4258
5.6 | 5.0257 | 1 | 2.856 | 184 | 64.4258
5.3 | 4.7312 | 1 | 2.856 | 184 | 64.4258
4.9 | 4.4298 | 1 | 2.856 | 184 | 64.4258
5.3 | 4.8703 | 1 | 2.856 | 184 | 64.4258
7.5 | 6.1751 | 1 | 2.856 | 184 | 64.4258
9.9 | 7.3511 | 1 | 2.856 | 184 | 64.4258
11.4 | 7.7642 | 1 | 2.856 | 184 | 64.4258
13.1 | 8.2399 | 1 | 2.856 | 184 | 64.4258
14.1 | 7.9986 | 1 | 2.856 | 184 | 64.4258
14.6 | 8.1954 | 1 | 2.856 | 184 | 64.4258
15 | 8.0091 | 1 | 2.856 | 184 | 64.4258
15.1 | 7.737 | 1 | 2.856 | 184 | 64.4258
14.2 | 7.1671 | 1 | 2.856 | 184 | 64.4258
12.9 | 6.2549 | 1 | 2.856 | 184 | 64.4258
12.1 | 6.7497 | 1 | 2.856 | 184 | 64.4258
10.8 | 6.4332 | 1 | 2.856 | 184 | 64.4258
9.9 | 6.454 | 1 | 2.856 | 184 | 64.4258
9.4 | 6.3701 | 1 | 2.856 | 184 | 64.4258
8.7 | 6.363 | 1 | 2.856 | 184 | 64.4258
8.2 | 6.2018 | 1 | 2.856 | 184 | 64.4258
8 | 6.1013 | 1 | 2.856 | 184 | 64.4258
7 | 5.5544 | 1 | 2.856 | 184 | 64.4258
6.4 | 5.1591 | 1 | 2.856 | 184 | 64.4258
6.3 | 5.0624 | 1 | 2.856 | 184 | 64.4258
6.1 | 4.9595 | 1 | 2.856 | 184 | 64.4258
5.8 | 4.8947 | 1 | 2.856 | 184 | 64.4258
5.9 | 4.9918 | 1 | 2.856 | 184 | 64.4258
7.3 | 5.9772 | 1 | 2.856 | 184 | 64.4258
9.2 | 7.1841 | 1 | 2.856 | 184 | 64.4258
12.1 | 8.5499 | 1 | 2.856 | 184 | 64.4258
14.2 | 9.6753 | 1 | 2.856 | 184 | 64.4258
15.9 | 10.8093 | 1 | 2.856 | 184 | 64.4258
17.7 | 11.656 | 1 | 2.856 | 184 | 64.4258
18.5 | 11.3596 | 1 | 2.856 | 184 | 64.4258
19.3 | 11.3817 | 1 | 2.856 | 184 | 64.4258
17.3 | 10.2227 | 1 | 2.856 | 184 | 64.4258
17.1 | 10.25 | 1 | 2.856 | 184 | 64.4258
16.6 | 10.0703 | 1 | 2.856 | 184 | 64.4258
15.7 | 10.2029 | 1 | 2.856 | 184 | 64.4258
15 | 9.8961 | 1 | 2.856 | 184 | 64.4258
13.2 | 9.4897 | 1 | 2.856 | 184 | 64.4258
11.5 | 8.8131 | 1 | 2.856 | 184 | 64.4258
9.8 | 7.7401 | 1 | 2.856 | 184 | 64.4258
7.8 | 6.3555 | 1 | 2.856 | 184 | 64.4258
7.1 | 5.776 | 1 | 2.856 | 184 | 64.4258
6.7 | 5.4822 | 1 | 2.856 | 184 | 64.4258
5.9 | 4.9833 | 1 | 2.856 | 184 | 64.4258
4.8 | 4.1394 | 1 | 2.856 | 184 | 64.4258
3.5 | 3.043 | 1 | 2.856 | 184 | 64.4258
2.1 | 1.8795 | 1 | 2.856 | 184 | 64.4258
2 | 1.7803 | 1 | 2.856 | 184 | 64.4258
4.6 | 4.0344 | 1 | 2.856 | 184 | 64.4258
7 | 5.8607 | 1 | 2.856 | 184 | 64.4258
8.5 | 6.5961 | 1 | 2.856 | 184 | 64.4258
9.5 | 6.4651 | 1 | 2.856 | 184 | 64.4258
10.8 | 6.9684 | 1 | 2.856 | 184 | 64.4258
10.2 | 6.3565 | 1 | 2.856 | 184 | 64.4258
10.6 | 6.5513 | 1 | 2.856 | 184 | 64.4258
11.1 | 6.1245 | 1 | 2.856 | 184 | 64.4258
11.8 | 5.734 | 1 | 2.856 | 184 | 64.4258
10.9 | 5.1414 | 1 | 2.856 | 184 | 64.4258
10.3 | 5.1611 | 1 | 2.856 | 184 | 64.4258
9.2 | 4.8697 | 1 | 2.856 | 184 | 64.4258
8.3 | 4.6792 | 1 | 2.856 | 184 | 64.4258
7.5 | 4.8887 | 1 | 2.856 | 184 | 64.4258
5.3 | 3.4563 | 1 | 2.856 | 184 | 64.4258
6.4 | 4.1179 | 1 | 2.856 | 184 | 64.4258
7.3 | 4.7053 | 1 | 2.856 | 184 | 64.4258
6.5 | 4.3326 | 1 | 2.856 | 184 | 64.4258
7 | 4.156 | 1 | 2.856 | 184 | 64.4258
6.8 | 4.2865 | 1 | 2.856 | 184 | 64.4258
5.7 | 3.5887 | 1 | 2.856 | 184 | 64.4258
4.7 | 2.973 | 1 | 2.856 | 184 | 64.4258
4.7 | 3.218 | 1 | 2.856 | 184 | 64.4258
4.8 | 3.7821 | 1 | 2.856 | 184 | 64.4258
5 | 3.844 | 1 | 2.856 | 184 | 64.4258
5.3 | 3.8312 | 1 | 2.856 | 184 | 64.4258
5.5 | 3.8953 | 1 | 2.856 | 184 | 64.4258
6.6 | 4.7646 | 1 | 2.856 | 184 | 64.4258
7.4 | 5.132 | 1 | 2.856 | 184 | 64.4258
7.9 | 5.4271 | 1 | 2.856 | 184 | 64.4258
8.1 | 5.2821 | 1 | 2.856 | 184 | 64.4258
7.9 | 5.0597 | 1 | 2.856 | 184 | 64.4258
8.3 | 5.3445 | 1 | 2.856 | 184 | 64.4258
8.6 | 5.5359 | 1 | 2.856 | 184 | 64.4258
9 | 5.0517 | 1 | 2.856 | 184 | 64.4258
7.9 | 5.4321 | 1 | 2.856 | 184 | 64.4258
7 | 5.3217 | 1 | 2.856 | 184 | 64.4258
6.6 | 5.3436 | 1 | 2.856 | 184 | 64.4258
5.9 | 4.7608 | 1 | 2.856 | 184 | 64.4258
5.6 | 4.3403 | 1 | 2.856 | 184 | 64.4258
5.5 | 4.245 | 1 | 2.856 | 184 | 64.4258
5.1 | 3.9476 | 1 | 2.856 | 184 | 64.4258
4.7 | 3.5634 | 1 | 2.856 | 184 | 64.4258
4.4 | 3.2747 | 1 | 2.856 | 184 | 64.4258
4 | 2.849 | 1 | 2.856 | 184 | 64.4258
4 | 2.9742 | 1 | 2.856 | 184 | 64.4258
4.1 | 2.8623 | 1 | 2.856 | 184 | 64.4258
3.9 | 2.6715 | 1 | 2.856 | 184 | 64.4258
4.1 | 2.8637 | 1 | 2.856 | 184 | 64.4258
4.6 | 3.1359 | 1 | 2.856 | 184 | 64.4258
5.1 | 3.6118 | 1 | 2.856 | 184 | 64.4258
5.6 | 3.7964 | 1 | 2.856 | 184 | 64.4258
6.3 | 3.9302 | 1 | 2.856 | 184 | 64.4258
7.9 | 4.7689 | 1 | 2.856 | 184 | 64.4258
8.5 | 4.166 | 1 | 2.856 | 184 | 64.4258
8.7 | 3.8783 | 1 | 2.856 | 184 | 64.4258
8.1 | 4.613 | 1 | 2.856 | 184 | 64.4258
7.7 | 4.6667 | 1 | 2.856 | 184 | 64.4258
7.9 | 4.7705 | 1 | 2.856 | 184 | 64.4258
7.1 | 4.6297 | 1 | 2.856 | 184 | 64.4258
6.5 | 3.5366 | 1 | 2.856 | 184 | 64.4258
6.1 | 3.4054 | 1 | 2.856 | 184 | 64.4258
5.4 | 2.7769 | 1 | 2.856 | 184 | 64.4258
4.4 | 2.4768 | 1 | 2.856 | 184 | 64.4258
3.5 | 2.1353 | 1 | 2.856 | 184 | 64.4258
3.2 | 1.967 | 1 | 2.856 | 184 | 64.4258
2.9 | 1.7585 | 1 | 2.856 | 184 | 64.4258
2.4 | 1.263 | 1 | 2.856 | 184 | 64.4258
1.9 | 0.97541 | 1 | 2.856 | 184 | 64.4258
1.9 | 0.97594 | 1 | 2.856 | 184 | 64.4258
2.2 | 1.2815 | 1 | 2.856 | 184 | 64.4258
2.4 | 1.2637 | 1 | 2.856 | 184 | 64.4258
2.9 | 1.6371 | 1 | 2.856 | 184 | 64.4258
3.9 | 2.3213 | 1 | 2.856 | 184 | 64.4258
5.9 | 3.6475 | 1 | 2.856 | 184 | 64.4258
7.5 | 4.1195 | 1 | 2.856 | 184 | 64.4258
7.8 | 4.0795 | 1 | 2.856 | 184 | 64.4258
9 | 4.4476 | 1 | 2.856 | 184 | 64.4258
9.1 | 4.0437 | 1 | 2.856 | 184 | 64.4258
9.4 | 4.6206 | 1 | 2.856 | 184 | 64.4258
10 | 4.756 | 1 | 2.856 | 184 | 64.4258
9.3 | 3.8887 | 1 | 2.856 | 184 | 64.4258
9.1 | 4.32 | 1 | 2.856 | 184 | 64.4258
8.9 | 4.1088 | 1 | 2.856 | 184 | 64.4258
8.4 | 4.2058 | 1 | 2.856 | 184 | 64.4258
8 | 4.1486 | 1 | 2.856 | 184 | 64.4258
7.3 | 4.2812 | 1 | 2.856 | 184 | 64.4258
6 | 3.5129 | 1 | 2.856 | 184 | 64.4258
4.7 | 2.5207 | 1 | 2.856 | 184 | 64.4258
3.8 | 1.9768 | 1 | 2.856 | 184 | 64.4258
3.4 | 1.6657 | 1 | 2.856 | 184 | 64.4258
2.6 | 0.95934 | 1 | 2.856 | 184 | 64.4258
0.5 | -0.34079 | 1 | 2.856 | 184 | 64.4258
1 | -0.096527 | 1 | 2.856 | 184 | 64.4258
1.2 | -0.022422 | 1 | 2.856 | 184 | 64.4258
1.1 | -0.0011675 | 1 | 2.856 | 184 | 64.4258
2 | 0.69329 | 1 | 2.856 | 184 | 64.4258
4 | 2.0464 | 1 | 2.856 | 184 | 64.4258
5.6 | 3.2212 | 1 | 2.856 | 184 | 64.4258
8.5 | 5.5991 | 1 | 2.856 | 184 | 64.4258
10.6 | 6.3781 | 1 | 2.856 | 184 | 64.4258
11.2 | 6.4181 | 1 | 2.856 | 184 | 64.4258
12 | 6.7761 | 1 | 2.856 | 184 | 64.4258
12.3 | 6.9551 | 1 | 2.856 | 184 | 64.4258
13 | 6.9835 | 1 | 2.856 | 184 | 64.4258
11.6 | 6.2578 | 1 | 2.856 | 184 | 64.4258
11.6 | 6.2578 | 1 | 2.856 | 184 | 64.4258
10.9 | 5.8697 | 1 | 2.856 | 184 | 64.4258
9.2 | 4.9256 | 1 | 2.856 | 184 | 64.4258
7.8 | 4.1922 | 1 | 2.856 | 184 | 64.4258
8 | 4.4181 | 1 | 2.856 | 184 | 64.4258
7.8 | 4.5372 | 1 | 2.856 | 184 | 64.4258
7.5 | 5.164 | 1 | 2.856 | 184 | 64.4258
7.4 | 5.4937 | 1 | 2.856 | 184 | 64.4258
6.5 | 5.0329 | 1 | 2.856 | 184 | 64.4258
5.2 | 3.9625 | 1 | 2.856 | 184 | 64.4258
5 | 3.9862 | 1 | 2.856 | 184 | 64.4258
4.9 | 3.7595 | 1 | 2.856 | 184 | 64.4258
5 | 3.8551 | 1 | 2.856 | 184 | 64.4258
5.5 | 4.3795 | 1 | 2.856 | 184 | 64.4258
6.5 | 4.6006 | 1 | 2.856 | 184 | 64.4258
7.3 | 5.2649 | 1 | 2.856 | 184 | 64.4258
7.6 | 6.3554 | 1 | 2.856 | 184 | 64.4258
7.5 | 6.7386 | 1 | 2.856 | 184 | 64.4258
7.8 | 6.5473 | 1 | 2.856 | 184 | 64.4258
7.9 | 6.4554 | 1 | 2.856 | 184 | 64.4258
7.8 | 6.5467 | 1 | 2.856 | 184 | 64.4258
7.5 | 6.7375 | 1 | 2.856 | 184 | 64.4258
7.6 | 6.3529 | 1 | 2.856 | 184 | 64.4258
7.5 | 6.4941 | 1 | 2.856 | 184 | 64.4258
7.7 | 6.3544 | 1 | 2.856 | 184 | 64.4258
7.6 | 6.3523 | 1 | 2.856 | 184 | 64.4258
7.4 | 6.4924 | 1 | 2.856 | 184 | 64.4258
7.4 | 6.5897 | 1 | 2.856 | 184 | 64.4258
7.8 | 7.1291 | 1 | 2.856 | 184 | 64.4258
8 | 7.2248 | 1 | 2.856 | 184 | 64.4258
7.5 | 6.9348 | 1 | 2.856 | 184 | 64.4258
7.7 | 7.2328 | 1 | 2.856 | 184 | 64.4258
7.4 | 6.7369 | 1 | 2.856 | 184 | 64.4258
6.8 | 6.1486 | 1 | 2.856 | 184 | 64.4258
6.9 | 6.1009 | 1 | 2.856 | 184 | 64.4258
5.9 | 5.5538 | 1 | 2.856 | 184 | 64.4258
5.7 | 5.356 | 1 | 2.856 | 184 | 64.4258
6.5 | 6.0488 | 1 | 2.856 | 184 | 64.4258
7.4 | 6.7366 | 1 | 2.856 | 184 | 64.4258
8.3 | 7.2682 | 1 | 2.856 | 184 | 64.4258
8.9 | 8.0017 | 1 | 2.856 | 184 | 64.4258
9.4 | 7.8372 | 1 | 2.856 | 184 | 64.4258
9.5 | 8.2805 | 1 | 2.856 | 184 | 64.4258
9.9 | 8.2159 | 1 | 2.856 | 184 | 64.4258
10.7 | 8.2496 | 1 | 2.856 | 184 | 64.4258
10.8 | 8.4374 | 1 | 2.856 | 184 | 64.4258
9.7 | 8.5751 | 1 | 2.856 | 184 | 64.4258
8 | 6.8793 | 1 | 2.856 | 184 | 64.4258
7.5 | 6.4916 | 1 | 2.856 | 184 | 64.4258
7.6 | 6.3504 | 1 | 2.856 | 184 | 64.4258
6.8 | 5.9078 | 1 | 2.856 | 184 | 64.4258
6.3 | 5.6106 | 1 | 2.856 | 184 | 64.4258
6.4 | 5.8532 | 1 | 2.856 | 184 | 64.4258
6.9 | 6.0059 | 1 | 2.856 | 184 | 64.4258
7 | 6.3453 | 1 | 2.856 | 184 | 64.4258
5.9 | 5.4577 | 1 | 2.856 | 184 | 64.4258
6 | 5.5565 | 1 | 2.856 | 184 | 64.4258
6 | 5.5567 | 1 | 2.856 | 184 | 64.4258
6.2 | 5.8517 | 1 | 2.856 | 184 | 64.4258
6.5 | 6.1487 | 1 | 2.856 | 184 | 64.4258
6.9 | 6.3463 | 1 | 2.856 | 184 | 64.4258
7.1 | 6.6427 | 1 | 2.856 | 184 | 64.4258
8.4 | 7.6193 | 1 | 2.856 | 184 | 64.4258
8.9 | 7.8066 | 1 | 2.856 | 184 | 64.4258
11 | 8.7822 | 1 | 2.856 | 184 | 64.4258
13.3 | 9.5427 | 1 | 2.856 | 184 | 64.4258
15.1 | 10.12 | 1 | 2.856 | 184 | 64.4258
16.1 | 10.3894 | 1 | 2.856 | 184 | 64.4258
15.7 | 10.5155 | 1 | 2.856 | 184 | 64.4258
16.5 | 10.5679 | 1 | 2.856 | 184 | 64.4258
17.2 | 10.8311 | 1 | 2.856 | 184 | 64.4258
17 | 10.6234 | 1 | 2.856 | 184 | 64.4258
16.7 | 10.0248 | 1 | 2.856 | 184 | 64.4258
15.2 | 9.9232 | 1 | 2.856 | 184 | 64.4258
13.6 | 8.6309 | 1 | 2.856 | 184 | 64.4258
12.5 | 7.8441 | 1 | 2.856 | 184 | 64.4258
11.5 | 7.61 | 1 | 2.856 | 184 | 64.4258
10.3 | 6.9914 | 1 | 2.856 | 184 | 64.4258
8.7 | 6.2445 | 1 | 2.856 | 184 | 64.4258
7.9 | 5.8874 | 1 | 2.856 | 184 | 64.4258
7 | 5.4304 | 1 | 2.856 | 184 | 64.4258
6.1 | 4.879 | 1 | 2.856 | 184 | 64.4258
6 | 4.783 | 1 | 2.856 | 184 | 64.4258
5.5 | 4.4771 | 1 | 2.856 | 184 | 64.4258
5.6 | 4.7078 | 1 | 2.856 | 184 | 64.4258
5 | 4.2138 | 1 | 2.856 | 184 | 64.4258
5.6 | 4.7083 | 1 | 2.856 | 184 | 64.4258
7.6 | 6.1392 | 1 | 2.856 | 184 | 64.4258
9.8 | 7.7199 | 1 | 2.856 | 184 | 64.4258
12.1 | 9.1178 | 1 | 2.856 | 184 | 64.4258
15.1 | 9.8192 | 1 | 2.856 | 184 | 64.4258
16.5 | 9.7067 | 1 | 2.856 | 184 | 64.4258
17.2 | 10.2029 | 1 | 2.856 | 184 | 64.4258
17 | 9.7469 | 1 | 2.856 | 184 | 64.4258
16.9 | 9.4232 | 1 | 2.856 | 184 | 64.4258
16.4 | 9.1619 | 1 | 2.856 | 184 | 64.4258
15.7 | 8.8756 | 1 | 2.856 | 184 | 64.4258
14 | 7.4659 | 1 | 2.856 | 184 | 64.4258
11 | 5.6191 | 1 | 2.856 | 184 | 64.4258
8.9 | 4.759 | 1 | 2.856 | 184 | 64.4258
8 | 4.4441 | 1 | 2.856 | 184 | 64.4258
8.9 | 4.9932 | 1 | 2.856 | 184 | 64.4258
7.7 | 4.4732 | 1 | 2.856 | 184 | 64.4258
6.9 | 4.1218 | 1 | 2.856 | 184 | 64.4258
6.2 | 3.6343 | 1 | 2.856 | 184 | 64.4258
5.1 | 3.1888 | 1 | 2.856 | 184 | 64.4258
4 | 2.8634 | 1 | 2.856 | 184 | 64.4258
3.6 | 2.601 | 1 | 2.856 | 184 | 64.4258
3.6 | 2.4785 | 1 | 2.856 | 184 | 64.4258
3.4 | 2.287 | 1 | 2.856 | 184 | 64.4258
4.5 | 2.8202 | 1 | 2.856 | 184 | 64.4258
7.8 | 5.2538 | 1 | 2.856 | 184 | 64.4258
10.7 | 6.3743 | 1 | 2.856 | 184 | 64.4258
13 | 8.1328 | 1 | 2.856 | 184 | 64.4258
15.7 | 9.3402 | 1 | 2.856 | 184 | 64.4258
16.1 | 9.3025 | 1 | 2.856 | 184 | 64.4258
16.2 | 9.2735 | 1 | 2.856 | 184 | 64.4258
16.5 | 9.3742 | 1 | 2.856 | 184 | 64.4258
16.8 | 9.6478 | 1 | 2.856 | 184 | 64.4258
16.6 | 9.6663 | 1 | 2.856 | 184 | 64.4258
16.3 | 9.8298 | 1 | 2.856 | 184 | 64.4258
15.9 | 9.842 | 1 | 2.856 | 184 | 64.4258
14.6 | 9.1019 | 1 | 2.856 | 184 | 64.4258
13.2 | 9.1222 | 1 | 2.856 | 184 | 64.4258
11.6 | 7.6208 | 1 | 2.856 | 184 | 64.4258
10.7 | 7.0246 | 1 | 2.856 | 184 | 64.4258
10.9 | 7.2434 | 1 | 2.856 | 184 | 64.4258
9.4 | 6.5093 | 1 | 2.856 | 184 | 64.4258
7.2 | 5.8444 | 1 | 2.856 | 184 | 64.4258
7 | 5.0847 | 1 | 2.856 | 184 | 64.4258
6.8 | 5.2395 | 1 | 2.856 | 184 | 64.4258
6.2 | 4.7544 | 1 | 2.856 | 184 | 64.4258
5.7 | 4.5804 | 1 | 2.856 | 184 | 64.4258
4.3 | 3.6172 | 1 | 2.856 | 184 | 64.4258
6.2 | 4.8413 | 1 | 2.856 | 184 | 64.4258
8.3 | 6.3046 | 1 | 2.856 | 184 | 64.4258
10.1 | 6.8922 | 1 | 2.856 | 184 | 64.4258
13.1 | 8.8166 | 1 | 2.856 | 184 | 64.4258
14.6 | 9.5379 | 1 | 2.856 | 184 | 64.4258
16.3 | 10.3731 | 1 | 2.856 | 184 | 64.4258
16.8 | 9.89 | 1 | 2.856 | 184 | 64.4258
17.4 | 9.5868 | 1 | 2.856 | 184 | 64.4258
18 | 10.5248 | 1 | 2.856 | 184 | 64.4258
17.8 | 10.2151 | 1 | 2.856 | 184 | 64.4258
17.9 | 10.3312 | 1 | 2.856 | 184 | 64.4258
15.7 | 9.8588 | 1 | 2.856 | 184 | 64.4258
14.9 | 8.9539 | 1 | 2.856 | 184 | 64.4258
12.8 | 7.8248 | 1 | 2.856 | 184 | 64.4258
12.1 | 7.5691 | 1 | 2.856 | 184 | 64.4258
11.5 | 7.852 | 1 | 2.856 | 184 | 64.4258
11.2 | 7.6658 | 1 | 2.856 | 184 | 64.4258
10.2 | 7.6702 | 1 | 2.856 | 184 | 64.4258
9 | 7.0942 | 1 | 2.856 | 184 | 64.4258
10.3 | 8.9625 | 1 | 2.856 | 184 | 64.4258
10 | 8.7739 | 1 | 2.856 | 184 | 64.4258
9.3 | 8.2476 | 1 | 2.856 | 184 | 64.4258
9.9 | 8.8814 | 1 | 2.856 | 184 | 64.4258
10.1 | 9.2322 | 1 | 2.856 | 184 | 64.4258
10.6 | 9.6147 | 1 | 2.856 | 184 | 64.4258
11.6 | 10.2677 | 1 | 2.856 | 184 | 64.4258
12.2 | 10.4253 | 1 | 2.856 | 184 | 64.4258
13.1 | 10.1166 | 1 | 2.856 | 184 | 64.4258
13.6 | 10.0985 | 1 | 2.856 | 184 | 64.4258
14 | 9.8182 | 1 | 2.856 | 184 | 64.4258
12.4 | 10.6162 | 1 | 2.856 | 184 | 64.4258
11.1 | 9.3255 | 1 | 2.856 | 184 | 64.4258
12.4 | 7.9866 | 1 | 2.856 | 184 | 64.4258
12.5 | 6.3416 | 1 | 2.856 | 184 | 64.4258
12.6 | 5.5456 | 1 | 2.856 | 184 | 64.4258
11.5 | 5.1392 | 1 | 2.856 | 184 | 64.4258
8.3 | 5.0681 | 1 | 2.856 | 184 | 64.4258
6.5 | 3.9339 | 1 | 2.856 | 184 | 64.4258
5.9 | 3.8869 | 1 | 2.856 | 184 | 64.4258
6 | 4.2242 | 1 | 2.856 | 184 | 64.4258
5.2 | 3.5121 | 1 | 2.856 | 184 | 64.4258
5.1 | 3.6205 | 1 | 2.856 | 184 | 64.4258
5.2 | 3.7571 | 1 | 2.856 | 184 | 64.4258
5 | 3.649 | 1 | 2.856 | 184 | 64.4258
5.8 | 4.242 | 1 | 2.856 | 184 | 64.4258
6.2 | 4.5366 | 1 | 2.856 | 184 | 64.4258
6.4 | 4.5971 | 1 | 2.856 | 184 | 64.4258
6.4 | 4.8097 | 1 | 2.856 | 184 | 64.4258
7 | 4.9924 | 1 | 2.856 | 184 | 64.4258
8.5 | 5.9219 | 1 | 2.856 | 184 | 64.4258
9.1 | 6.0977 | 1 | 2.856 | 184 | 64.4258
10 | 6.6263 | 1 | 2.856 | 184 | 64.4258
10.3 | 7.3177 | 1 | 2.856 | 184 | 64.4258
11.7 | 7.3734 | 1 | 2.856 | 184 | 64.4258
13 | 7.9529 | 1 | 2.856 | 184 | 64.4258
13 | 6.9893 | 1 | 2.856 | 184 | 64.4258
12.7 | 7.2578 | 1 | 2.856 | 184 | 64.4258
12 | 6.6048 | 1 | 2.856 | 184 | 64.4258
11 | 7.1192 | 1 | 2.856 | 184 | 64.4258
10.5 | 6.7163 | 1 | 2.856 | 184 | 64.4258
9.7 | 6.485 | 1 | 2.856 | 184 | 64.4258
9 | 6.1373 | 1 | 2.856 | 184 | 64.4258
8.3 | 5.9544 | 1 | 2.856 | 184 | 64.4258
8.7 | 5.5828 | 1 | 2.856 | 184 | 64.4258
8 | 5.2254 | 1 | 2.856 | 184 | 64.4258
7.9 | 5.3353 | 1 | 2.856 | 184 | 64.4258
8 | 5.1053 | 1 | 2.856 | 184 | 64.4258
8 | 4.8354 | 1 | 2.856 | 184 | 64.4258
7.6 | 5.0168 | 1 | 2.856 | 184 | 64.4258
7.7 | 5.4794 | 1 | 2.856 | 184 | 64.4258
7 | 5.5574 | 1 | 2.856 | 184 | 64.4258
7.6 | 5.597 | 1 | 2.856 | 184 | 64.4258
8 | 5.6282 | 1 | 2.856 | 184 | 64.4258
9 | 6.1287 | 1 | 2.856 | 184 | 64.4258
9.1 | 6.0947 | 1 | 2.856 | 184 | 64.4258
9 | 5.7216 | 1 | 2.856 | 184 | 64.4258
9 | 6.1244 | 1 | 2.856 | 184 | 64.4258
9.4 | 6.1579 | 1 | 2.856 | 184 | 64.4258
9.3 | 6.5633 | 1 | 2.856 | 184 | 64.4258
7.9 | 6.7875 | 1 | 2.856 | 184 | 64.4258
7.6 | 6.9346 | 1 | 2.856 | 184 | 64.4258
7.8 | 7.1301 | 1 | 2.856 | 184 | 64.4258
8 | 7.3256 | 1 | 2.856 | 184 | 64.4258
8.2 | 7.987 | 1 | 2.856 | 184 | 64.4258
9.1 | 8.4553 | 1 | 2.856 | 184 | 64.4258
9.1 | 8.1959 | 1 | 2.856 | 184 | 64.4258
7.9 | 6.9763 | 1 | 2.856 | 184 | 64.4258
6.3 | 5.6089 | 1 | 2.856 | 184 | 64.4258
6.3 | 5.5133 | 1 | 2.856 | 184 | 64.4258
6.2 | 5.4158 | 1 | 2.856 | 184 | 64.4258
6.1 | 5.178 | 1 | 2.856 | 184 | 64.4258
6 | 5.0804 | 1 | 2.856 | 184 | 64.4258
4.9 | 4.4228 | 1 | 2.856 | 184 | 64.4258
5.1 | 4.7615 | 1 | 2.856 | 184 | 64.4258
6.4 | 5.949 | 1 | 2.856 | 184 | 64.4258
6 | 4.9899 | 1 | 2.856 | 184 | 64.4258
5.6 | 4.4693 | 1 | 2.856 | 184 | 64.4258
5.1 | 3.858 | 1 | 2.856 | 184 | 64.4258
3.6 | 2.9251 | 1 | 2.856 | 184 | 64.4258
4.5 | 3.8056 | 1 | 2.856 | 184 | 64.4258
5 | 3.7668 | 1 | 2.856 | 184 | 64.4258
5.9 | 4.3286 | 1 | 2.856 | 184 | 64.4258
5.9 | 3.7555 | 1 | 2.856 | 184 | 64.4258
9 | 3.8029 | 1 | 2.856 | 184 | 64.4258
8.1 | 3.8457 | 1 | 2.856 | 184 | 64.4258
5.7 | 3.7728 | 1 | 2.856 | 184 | 64.4258
3.9 | 2.758 | 1 | 2.856 | 184 | 64.4258
5.2 | 3.1509 | 1 | 2.856 | 184 | 64.4258
4.9 | 3.2247 | 1 | 2.856 | 184 | 64.4258
2.4 | 1.9669 | 1 | 2.856 | 184 | 64.4258
3.4 | 2.1603 | 1 | 2.856 | 184 | 64.4258
3.3 | 1.7786 | 1 | 2.856 | 184 | 64.4258
3.8 | 1.7292 | 1 | 2.856 | 184 | 64.4258
4 | 1.9248 | 1 | 2.856 | 184 | 64.4258
3.4 | 1.3035 | 1 | 2.856 | 184 | 64.4258
3.2 | 1.1896 | 1 | 2.856 | 184 | 64.4258
3.2 | 1.1896 | 1 | 2.856 | 184 | 64.4258
3 | 1.2368 | 1 | 2.856 | 184 | 64.4258
2.5 | 0.9888 | 1 | 2.856 | 184 | 64.4258
2.7 | 1.0655 | 1 | 2.856 | 184 | 64.4258
3.5 | 1.6489 | 1 | 2.856 | 184 | 64.4258
5.2 | 2.5674 | 1 | 2.856 | 184 | 64.4258
6.4 | 3.3469 | 1 | 2.856 | 184 | 64.4258
7.2 | 3.4391 | 1 | 2.856 | 184 | 64.4258
7.6 | 3.998 | 1 | 2.856 | 184 | 64.4258
7.8 | 4.1049 | 1 | 2.856 | 184 | 64.4258
8.3 | 4.2561 | 1 | 2.856 | 184 | 64.4258
9.4 | 5.2913 | 1 | 2.856 | 184 | 64.4258
9.2 | 4.6959 | 1 | 2.856 | 184 | 64.4258
9.7 | 4.7413 | 1 | 2.856 | 184 | 64.4258
9.4 | 4.4094 | 1 | 2.856 | 184 | 64.4258
8.9 | 4.6507 | 1 | 2.856 | 184 | 64.4258
8.3 | 4.2582 | 1 | 2.856 | 184 | 64.4258
8 | 3.8052 | 1 | 2.856 | 184 | 64.4258
7 | 3.8784 | 1 | 2.856 | 184 | 64.4258
6 | 3.5301 | 1 | 2.856 | 184 | 64.4258
4.5 | 2.8229 | 1 | 2.856 | 184 | 64.4258
4.5 | 2.9404 | 1 | 2.856 | 184 | 64.4258
5 | 3.3325 | 1 | 2.856 | 184 | 64.4258
4.7 | 3.3712 | 1 | 2.856 | 184 | 64.4258
5.2 | 3.9743 | 1 | 2.856 | 184 | 64.4258
4.9 | 4.1168 | 1 | 2.856 | 184 | 64.4258
5 | 4.576 | 1 | 2.856 | 184 | 64.4258
5.2 | 4.9605 | 1 | 2.856 | 184 | 64.4258
5.9 | 5.6551 | 1 | 2.856 | 184 | 64.4258
6.6 | 6.2513 | 1 | 2.856 | 184 | 64.4258
7.4 | 6.9429 | 1 | 2.856 | 184 | 64.4258
8.4 | 8.0843 | 1 | 2.856 | 184 | 64.4258
10 | 9.3481 | 1 | 2.856 | 184 | 64.4258
11.9 | 10.5627 | 1 | 2.856 | 184 | 64.4258
13.3 | 11.5352 | 1 | 2.856 | 184 | 64.4258
14.5 | 12.518 | 1 | 2.856 | 184 | 64.4258
14.1 | 12.6881 | 1 | 2.856 | 184 | 64.4258
14.9 | 13.0658 | 1 | 2.856 | 184 | 64.4258
16 | 13.176 | 1 | 2.856 | 184 | 64.4258
14.6 | 12.0767 | 1 | 2.856 | 184 | 64.4258
14.2 | 11.8066 | 1 | 2.856 | 184 | 64.4258
13.9 | 11.6286 | 1 | 2.856 | 184 | 64.4258
13.5 | 11.4075 | 1 | 2.856 | 184 | 64.4258
13 | 11.1424 | 1 | 2.856 | 184 | 64.4258
12.6 | 10.9712 | 1 | 2.856 | 184 | 64.4258
11.5 | 10.3881 | 1 | 2.856 | 184 | 64.4258
10.2 | 9.5446 | 1 | 2.856 | 184 | 64.4258
9.7 | 9.0534 | 1 | 2.856 | 184 | 64.4258
9 | 8.6788 | 1 | 2.856 | 184 | 64.4258
10.6 | 9.9377 | 1 | 2.856 | 184 | 64.4258
11.1 | 10.3203 | 1 | 2.856 | 184 | 64.4258
11.5 | 10.4953 | 1 | 2.856 | 184 | 64.4258
12.2 | 10.906 | 1 | 2.856 | 184 | 64.4258
13.9 | 11.7339 | 1 | 2.856 | 184 | 64.4258
14 | 11.8286 | 1 | 2.856 | 184 | 64.4258
14.7 | 11.7582 | 1 | 2.856 | 184 | 64.4258
16 | 12.3975 | 1 | 2.856 | 184 | 64.4258
17.3 | 13.1736 | 1 | 2.856 | 184 | 64.4258
17.1 | 13.4022 | 1 | 2.856 | 184 | 64.4258
17.8 | 14.0964 | 1 | 2.856 | 184 | 64.4258
17.5 | 13.716 | 1 | 2.856 | 184 | 64.4258
16.5 | 13.4826 | 1 | 2.856 | 184 | 64.4258
16.3 | 13.5663 | 1 | 2.856 | 184 | 64.4258
16 | 13.2849 | 1 | 2.856 | 184 | 64.4258
14.9 | 12.5195 | 1 | 2.856 | 184 | 64.4258
12.6 | 11.4025 | 1 | 2.856 | 184 | 64.4258
12.1 | 11.0258 | 1 | 2.856 | 184 | 64.4258
11.1 | 10.3207 | 1 | 2.856 | 184 | 64.4258
10.1 | 9.5536 | 1 | 2.856 | 184 | 64.4258
9.8 | 9.3645 | 1 | 2.856 | 184 | 64.4258
9.7 | 9.1594 | 1 | 2.856 | 184 | 64.4258
9.8 | 9.3645 | 1 | 2.856 | 184 | 64.4258
9.3 | 8.7653 | 1 | 2.856 | 184 | 64.4258
9.2 | 8.8773 | 1 | 2.856 | 184 | 64.4258
10 | 9.5622 | 1 | 2.856 | 184 | 64.4258
10 | 9.455 | 1 | 2.856 | 184 | 64.4258
10.9 | 10.0179 | 1 | 2.856 | 184 | 64.4258
12 | 10.5551 | 1 | 2.856 | 184 | 64.4258
13 | 10.8331 | 1 | 2.856 | 184 | 64.4258
14.1 | 11.3552 | 1 | 2.856 | 184 | 64.4258
14.8 | 11.5509 | 1 | 2.856 | 184 | 64.4258
13 | 10.937 | 1 | 2.856 | 184 | 64.4258
14.1 | 11.3552 | 1 | 2.856 | 184 | 64.4258
16.2 | 12.634 | 1 | 2.856 | 184 | 64.4258
16.1 | 12.1923 | 1 | 2.856 | 184 | 64.4258
15 | 11.6351 | 1 | 2.856 | 184 | 64.4258
15.1 | 11.4805 | 1 | 2.856 | 184 | 64.4258
15.2 | 11.6205 | 1 | 2.856 | 184 | 64.4258
14.5 | 11.6767 | 1 | 2.856 | 184 | 64.4258
13.9 | 11.2702 | 1 | 2.856 | 184 | 64.4258
14 | 11.262 | 1 | 2.856 | 184 | 64.4258
13.6 | 11.0923 | 1 | 2.856 | 184 | 64.4258
13 | 11.2512 | 1 | 2.856 | 184 | 64.4258
12.7 | 11.0699 | 1 | 2.856 | 184 | 64.4258
12.5 | 10.9834 | 1 | 2.856 | 184 | 64.4258
11.7 | 10.4771 | 1 | 2.856 | 184 | 64.4258
10.8 | 9.7097 | 1 | 2.856 | 184 | 64.4258
10.7 | 9.7173 | 1 | 2.856 | 184 | 64.4258
10.4 | 9.7417 | 1 | 2.856 | 184 | 64.4258
9.9 | 9.3565 | 1 | 2.856 | 184 | 64.4258
11.2 | 10.2043 | 1 | 2.856 | 184 | 64.4258
12.3 | 10.791 | 1 | 2.856 | 184 | 64.4258
13.5 | 11.4093 | 1 | 2.856 | 184 | 64.4258
14.2 | 11.8086 | 1 | 2.856 | 184 | 64.4258
16.1 | 12.7459 | 1 | 2.856 | 184 | 64.4258
16.4 | 12.2651 | 1 | 2.856 | 184 | 64.4258
17.2 | 12.0708 | 1 | 2.856 | 184 | 64.4258
17.8 | 12.2271 | 1 | 2.856 | 184 | 64.4258
17.1 | 11.6197 | 1 | 2.856 | 184 | 64.4258
16.7 | 11.5861 | 1 | 2.856 | 184 | 64.4258
16.4 | 11.2774 | 1 | 2.856 | 184 | 64.4258
15.2 | 10.9467 | 1 | 2.856 | 184 | 64.4258
14.6 | 10.6414 | 1 | 2.856 | 184 | 64.4258
13.1 | 10.8213 | 1 | 2.856 | 184 | 64.4258
12.2 | 10.1231 | 1 | 2.856 | 184 | 64.4258
11.5 | 9.3138 | 1 | 2.856 | 184 | 64.4258
11.1 | 9.3303 | 1 | 2.856 | 184 | 64.4258
11.1 | 8.6508 | 1 | 2.856 | 184 | 64.4258
11.2 | 8.5573 | 1 | 2.856 | 184 | 64.4258
11.5 | 8.5122 | 1 | 2.856 | 184 | 64.4258
11 | 8.3696 | 1 | 2.856 | 184 | 64.4258
10.9 | 8.2312 | 1 | 2.856 | 184 | 64.4258
11.1 | 8.3234 | 1 | 2.856 | 184 | 64.4258
11 | 8.1408 | 1 | 2.856 | 184 | 64.4258
11.4 | 8.4178 | 1 | 2.856 | 184 | 64.4258
12 | 8.7854 | 1 | 2.856 | 184 | 64.4258
12.5 | 9.2871 | 1 | 2.856 | 184 | 64.4258
13.3 | 10.1127 | 1 | 2.856 | 184 | 64.4258
14.5 | 11.4111 | 1 | 2.856 | 184 | 64.4258
15.1 | 11.2712 | 1 | 2.856 | 184 | 64.4258
15 | 10.8501 | 1 | 2.856 | 184 | 64.4258
15.5 | 10.7906 | 1 | 2.856 | 184 | 64.4258
16.9 | 11.5176 | 1 | 2.856 | 184 | 64.4258
15.6 | 10.4356 | 1 | 2.856 | 184 | 64.4258
15.8 | 10.6523 | 1 | 2.856 | 184 | 64.4258
15.1 | 10.4813 | 1 | 2.856 | 184 | 64.4258
13.4 | 9.6444 | 1 | 2.856 | 184 | 64.4258
12.6 | 9.1937 | 1 | 2.856 | 184 | 64.4258
12.6 | 9.1937 | 1 | 2.856 | 184 | 64.4258
11.8 | 9.0612 | 1 | 2.856 | 184 | 64.4258
10.9 | 8.6012 | 1 | 2.856 | 184 | 64.4258
8.7 | 7.3736 | 1 | 2.856 | 184 | 64.4258
8 | 6.8902 | 1 | 2.856 | 184 | 64.4258
8.1 | 7.0836 | 1 | 2.856 | 184 | 64.4258
7.7 | 6.7919 | 1 | 2.856 | 184 | 64.4258
8.6 | 7.4706 | 1 | 2.856 | 184 | 64.4258
8.7 | 7.5673 | 1 | 2.856 | 184 | 64.4258
8.4 | 7.4238 | 1 | 2.856 | 184 | 64.4258
9.4 | 7.9475 | 1 | 2.856 | 184 | 64.4258
10.4 | 8.2722 | 1 | 2.856 | 184 | 64.4258
10.7 | 8.2701 | 1 | 2.856 | 184 | 64.4258
12.4 | 8.7402 | 1 | 2.856 | 184 | 64.4258
12.6 | 9.189 | 1 | 2.856 | 184 | 64.4258
13.5 | 9.637 | 1 | 2.856 | 184 | 64.4258
13.6 | 9.4132 | 1 | 2.856 | 184 | 64.4258
14.6 | 9.5198 | 1 | 2.856 | 184 | 64.4258
14.4 | 9.554 | 1 | 2.856 | 184 | 64.4258
14.5 | 9.9852 | 1 | 2.856 | 184 | 64.4258
13.3 | 8.7605 | 1 | 2.856 | 184 | 64.4258
12.5 | 8.7337 | 1 | 2.856 | 184 | 64.4258
11.4 | 8.4964 | 1 | 2.856 | 184 | 64.4258
10.5 | 7.8489 | 1 | 2.856 | 184 | 64.4258
10 | 7.8901 | 1 | 2.856 | 184 | 64.4258
9.6 | 7.7954 | 1 | 2.856 | 184 | 64.4258
9.6 | 7.9394 | 1 | 2.856 | 184 | 64.4258
9.6 | 8.2832 | 1 | 2.856 | 184 | 64.4258
8.7 | 7.9126 | 1 | 2.856 | 184 | 64.4258
9 | 8.2059 | 1 | 2.856 | 184 | 64.4258
9.1 | 8.5633 | 1 | 2.856 | 184 | 64.4258
9.3 | 8.7603 | 1 | 2.856 | 184 | 64.4258
8.8 | 8.2677 | 1 | 2.856 | 184 | 64.4258
8.4 | 7.9773 | 1 | 2.856 | 184 | 64.4258
9.4 | 8.4939 | 1 | 2.856 | 184 | 64.4258
10.2 | 8.8613 | 1 | 2.856 | 184 | 64.4258
11.7 | 9.3897 | 1 | 2.856 | 184 | 64.4258
12.2 | 9.0909 | 1 | 2.856 | 184 | 64.4258
13.2 | 9.678 | 1 | 2.856 | 184 | 64.4258
14 | 9.3665 | 1 | 2.856 | 184 | 64.4258
15.1 | 9.3267 | 1 | 2.856 | 184 | 64.4258
14.6 | 9.6343 | 1 | 2.856 | 184 | 64.4258
15.9 | 9.2667 | 1 | 2.856 | 184 | 64.4258
14.3 | 9.3324 | 1 | 2.856 | 184 | 64.4258
14 | 8.9907 | 1 | 2.856 | 184 | 64.4258
13.3 | 9.0942 | 1 | 2.856 | 184 | 64.4258
12 | 8.1115 | 1 | 2.856 | 184 | 64.4258
11.1 | 7.5187 | 1 | 2.856 | 184 | 64.4258
10 | 7.2087 | 1 | 2.856 | 184 | 64.4258
9.5 | 6.9222 | 1 | 2.856 | 184 | 64.4258
8.7 | 7.319 | 1 | 2.856 | 184 | 64.4258
8.1 | 7.0792 | 1 | 2.856 | 184 | 64.4258
7.7 | 6.4516 | 1 | 2.856 | 184 | 64.4258
8.1 | 6.5542 | 1 | 2.856 | 184 | 64.4258
8.1 | 6.324 | 1 | 2.856 | 184 | 64.4258
7.3 | 6.1595 | 1 | 2.856 | 184 | 64.4258
7.5 | 6.592 | 1 | 2.856 | 184 | 64.4258
8.1 | 7.2249 | 1 | 2.856 | 184 | 64.4258
10 | 8.2191 | 1 | 2.856 | 184 | 64.4258
10.4 | 8.5013 | 1 | 2.856 | 184 | 64.4258
11.5 | 9.0502 | 1 | 2.856 | 184 | 64.4258
12.4 | 9.7434 | 1 | 2.856 | 184 | 64.4258
13.8 | 10.596 | 1 | 2.856 | 184 | 64.4258
14.9 | 10.5927 | 1 | 2.856 | 184 | 64.4258
12.5 | 10.7536 | 1 | 2.856 | 184 | 64.4258
12 | 10.9174 | 1 | 2.856 | 184 | 64.4258
11.8 | 10.6683 | 1 | 2.856 | 184 | 64.4258
12 | 10.6458 | 1 | 2.856 | 184 | 64.4258
12.2 | 11.0022 | 1 | 2.856 | 184 | 64.4258
12.2 | 11.0022 | 1 | 2.856 | 184 | 64.4258
11.9 | 11.1525 | 1 | 2.856 | 184 | 64.4258
11.8 | 11.0546 | 1 | 2.856 | 184 | 64.4258
11.3 | 10.5088 | 1 | 2.856 | 184 | 64.4258
10.8 | 9.9112 | 1 | 2.856 | 184 | 64.4258
10.5 | 9.512 | 1 | 2.856 | 184 | 64.4258
10.3 | 9.2129 | 1 | 2.856 | 184 | 64.4258
10 | 8.7677 | 1 | 2.856 | 184 | 64.4258
9.9 | 8.47 | 1 | 2.856 | 184 | 64.4258
9.4 | 8.3911 | 1 | 2.856 | 184 | 64.4258
8.7 | 7.8114 | 1 | 2.856 | 184 | 64.4258
8.4 | 7.519 | 1 | 2.856 | 184 | 64.4258
8.9 | 7.8061 | 1 | 2.856 | 184 | 64.4258
9.9 | 8.2261 | 1 | 2.856 | 184 | 64.4258
11.3 | 8.9683 | 1 | 2.856 | 184 | 64.4258
12.7 | 9.1374 | 1 | 2.856 | 184 | 64.4258
13 | 9.1391 | 1 | 2.856 | 184 | 64.4258
14.1 | 8.7651 | 1 | 2.856 | 184 | 64.4258
14 | 9.8108 | 1 | 2.856 | 184 | 64.4258
14.9 | 10.7035 | 1 | 2.856 | 184 | 64.4258
15.3 | 10.1243 | 1 | 2.856 | 184 | 64.4258
14.6 | 10.2108 | 1 | 2.856 | 184 | 64.4258
14.9 | 10.0344 | 1 | 2.856 | 184 | 64.4258
14.8 | 9.9472 | 1 | 2.856 | 184 | 64.4258
14.1 | 10.0367 | 1 | 2.856 | 184 | 64.4258
13 | 9.1444 | 1 | 2.856 | 184 | 64.4258
12 | 9.147 | 1 | 2.856 | 184 | 64.4258
11 | 9.0304 | 1 | 2.856 | 184 | 64.4258
10.8 | 9.1374 | 1 | 2.856 | 184 | 64.4258
10.5 | 8.9509 | 1 | 2.856 | 184 | 64.4258
10.4 | 9.3145 | 1 | 2.856 | 184 | 64.4258
10.9 | 9.6944 | 1 | 2.856 | 184 | 64.4258
11.5 | 9.8553 | 1 | 2.856 | 184 | 64.4258
11.5 | 9.8553 | 1 | 2.856 | 184 | 64.4258
10.8 | 9.9136 | 1 | 2.856 | 184 | 64.4258
11.5 | 10.3808 | 1 | 2.856 | 184 | 64.4258
11.8 | 9.8347 | 1 | 2.856 | 184 | 64.4258
12 | 9.7726 | 1 | 2.856 | 184 | 64.4258
12.6 | 10.0384 | 1 | 2.856 | 184 | 64.4258
12.8 | 10.2748 | 1 | 2.856 | 184 | 64.4258
12.6 | 10.5937 | 1 | 2.856 | 184 | 64.4258
12 | 10.6511 | 1 | 2.856 | 184 | 64.4258
12.5 | 11.2979 | 1 | 2.856 | 184 | 64.4258
14 | 11.7087 | 1 | 2.856 | 184 | 64.4258
13.1 | 11.12 | 1 | 2.856 | 184 | 64.4258
12.3 | 10.3081 | 1 | 2.856 | 184 | 64.4258
13 | 10.1134 | 1 | 2.856 | 184 | 64.4258
13 | 9.7778 | 1 | 2.856 | 184 | 64.4258
12.7 | 10.1791 | 1 | 2.856 | 184 | 64.4258
12.1 | 9.7662 | 1 | 2.856 | 184 | 64.4258
11.1 | 9.3207 | 1 | 2.856 | 184 | 64.4258
10.9 | 9.2314 | 1 | 2.856 | 184 | 64.4258
10.2 | 8.6621 | 1 | 2.856 | 184 | 64.4258
9.5 | 7.8472 | 1 | 2.856 | 184 | 64.4258
9.2 | 7.5138 | 1 | 2.856 | 184 | 64.4258
8.8 | 7.3703 | 1 | 2.856 | 184 | 64.4258
8.7 | 7.3704 | 1 | 2.856 | 184 | 64.4258
8.6 | 7.131 | 1 | 2.856 | 184 | 64.4258
8.4 | 6.9396 | 1 | 2.856 | 184 | 64.4258
8.2 | 6.8423 | 1 | 2.856 | 184 | 64.4258
8.9 | 7.3236 | 1 | 2.856 | 184 | 64.4258
9.9 | 8.1324 | 1 | 2.856 | 184 | 64.4258
10.9 | 8.1325 | 1 | 2.856 | 184 | 64.4258
11.7 | 7.9394 | 1 | 2.856 | 184 | 64.4258
12 | 7.671 | 1 | 2.856 | 184 | 64.4258
10.6 | 8.847 | 1 | 2.856 | 184 | 64.4258
10.1 | 8.9717 | 1 | 2.856 | 184 | 64.4258
13 | 9.6897 | 1 | 2.856 | 184 | 64.4258
13.6 | 8.498 | 1 | 2.856 | 184 | 64.4258
15.3 | 9.3516 | 1 | 2.856 | 184 | 64.4258
13.1 | 9.4565 | 1 | 2.856 | 184 | 64.4258
11.5 | 9.4025 | 1 | 2.856 | 184 | 64.4258
11.3 | 8.7314 | 1 | 2.856 | 184 | 64.4258
11.1 | 9.3215 | 1 | 2.856 | 184 | 64.4258
10.3 | 8.08 | 1 | 2.856 | 184 | 64.4258
9.9 | 7.6588 | 1 | 2.856 | 184 | 64.4258
8.7 | 7.0373 | 1 | 2.856 | 184 | 64.4258
8.4 | 7.1768 | 1 | 2.856 | 184 | 64.4258
8.2 | 7.5249 | 1 | 2.856 | 184 | 64.4258
8.2 | 7.5246 | 1 | 2.856 | 184 | 64.4258
8.1 | 7.5274 | 1 | 2.856 | 184 | 64.4258
8.1 | 7.6292 | 1 | 2.856 | 184 | 64.4258
8 | 7.5304 | 1 | 2.856 | 184 | 64.4258
8 | 7.6847 | 1 | 2.856 | 184 | 64.4258
8.3 | 7.982 | 1 | 2.856 | 184 | 64.4258
8.3 | 7.8777 | 1 | 2.856 | 184 | 64.4258
7.7 | 6.9334 | 1 | 2.856 | 184 | 64.4258
7.5 | 6.9361 | 1 | 2.856 | 184 | 64.4258
7.2 | 6.3965 | 1 | 2.856 | 184 | 64.4258
7.4 | 6.8383 | 1 | 2.856 | 184 | 64.4258
8.5 | 7.7167 | 1 | 2.856 | 184 | 64.4258
10.7 | 8.123 | 1 | 2.856 | 184 | 64.4258
11.8 | 8.4525 | 1 | 2.856 | 184 | 64.4258
12.6 | 7.8255 | 1 | 2.856 | 184 | 64.4258
12.2 | 8.2914 | 1 | 2.856 | 184 | 64.4258
11.3 | 7.2887 | 1 | 2.856 | 184 | 64.4258
11.7 | 7.4821 | 1 | 2.856 | 184 | 64.4258
11.3 | 7.5375 | 1 | 2.856 | 184 | 64.4258
9.8 | 7.4749 | 1 | 2.856 | 184 | 64.4258
9.7 | 7.0268 | 1 | 2.856 | 184 | 64.4258
8 | 6.3285 | 1 | 2.856 | 184 | 64.4258
7.6 | 6.0396 | 1 | 2.856 | 184 | 64.4258
7.1 | 5.431 | 1 | 2.856 | 184 | 64.4258
4.7 | 3.9175 | 1 | 2.856 | 184 | 64.4258
5.6 | 4.3502 | 1 | 2.856 | 184 | 64.4258
3.8 | 3.1271 | 1 | 2.856 | 184 | 64.4258
5.2 | 4.3157 | 1 | 2.856 | 184 | 64.4258
5 | 4.1219 | 1 | 2.856 | 184 | 64.4258
4.8 | 4.105 | 1 | 2.856 | 184 | 64.4258
7 | 5.428 | 1 | 2.856 | 184 | 64.4258
8.9 | 6.5569 | 1 | 2.856 | 184 | 64.4258
10.3 | 7.3263 | 1 | 2.856 | 184 | 64.4258
10.7 | 7.3925 | 1 | 2.856 | 184 | 64.4258
11.9 | 7.8006 | 1 | 2.856 | 184 | 64.4258
12 | 7.4523 | 1 | 2.856 | 184 | 64.4258
12.4 | 7.7598 | 1 | 2.856 | 184 | 64.4258
12.9 | 7.6937 | 1 | 2.856 | 184 | 64.4258
12.9 | 7.5832 | 1 | 2.856 | 184 | 64.4258
12 | 7.5689 | 1 | 2.856 | 184 | 64.4258
11.8 | 8.0428 | 1 | 2.856 | 184 | 64.4258
11.5 | 7.8589 | 1 | 2.856 | 184 | 64.4258
10.4 | 7.5072 | 1 | 2.856 | 184 | 64.4258
9.6 | 7.2546 | 1 | 2.856 | 184 | 64.4258
8.5 | 6.405 | 1 | 2.856 | 184 | 64.4258
8 | 6.1117 | 1 | 2.856 | 184 | 64.4258
6.7 | 5.1444 | 1 | 2.856 | 184 | 64.4258
6.2 | 4.9739 | 1 | 2.856 | 184 | 64.4258
7 | 5.4296 | 1 | 2.856 | 184 | 64.4258
6.9 | 5.4669 | 1 | 2.856 | 184 | 64.4258
6.9 | 5.5556 | 1 | 2.856 | 184 | 64.4258
7.3 | 5.8483 | 1 | 2.856 | 184 | 64.4258
7.7 | 6.3677 | 1 | 2.856 | 184 | 64.4258
8 | 7.1345 | 1 | 2.856 | 184 | 64.4258
8.6 | 8.1775 | 1 | 2.856 | 184 | 64.4258
9.3 | 8.7635 | 1 | 2.856 | 184 | 64.4258
10 | 8.929 | 1 | 2.856 | 184 | 64.4258
10.2 | 9.4365 | 1 | 2.856 | 184 | 64.4258
11 | 9.8996 | 1 | 2.856 | 184 | 64.4258
11.1 | 9.8907 | 1 | 2.856 | 184 | 64.4258
11 | 10.0052 | 1 | 2.856 | 184 | 64.4258
11 | 10.3284 | 1 | 2.856 | 184 | 64.4258
11.5 | 10.9307 | 1 | 2.856 | 184 | 64.4258
12.4 | 11.4238 | 1 | 2.856 | 184 | 64.4258
12.5 | 11.7456 | 1 | 2.856 | 184 | 64.4258
13.2 | 12.2039 | 1 | 2.856 | 184 | 64.4258
12.6 | 12.0723 | 1 | 2.856 | 184 | 64.4258
12.2 | 11.3388 | 1 | 2.856 | 184 | 64.4258
11.4 | 10.1262 | 1 | 2.856 | 184 | 64.4258
10.9 | 9.436 | 1 | 2.856 | 184 | 64.4258
10.6 | 8.6996 | 1 | 2.856 | 184 | 64.4258
10.5 | 8.2706 | 1 | 2.856 | 184 | 64.4258
9.6 | 7.1128 | 1 | 2.856 | 184 | 64.4258
8.2 | 6.25 | 1 | 2.856 | 184 | 64.4258
7.6 | 5.8621 | 1 | 2.856 | 184 | 64.4258
6.9 | 5.2876 | 1 | 2.856 | 184 | 64.4258
6.9 | 5.4203 | 1 | 2.856 | 184 | 64.4258
7 | 5.3833 | 1 | 2.856 | 184 | 64.4258
7.3 | 5.4064 | 1 | 2.856 | 184 | 64.4258
7.8 | 5.833 | 1 | 2.856 | 184 | 64.4258
8.7 | 6.1983 | 1 | 2.856 | 184 | 64.4258
9.6 | 6.3186 | 1 | 2.856 | 184 | 64.4258
10.2 | 6.6557 | 1 | 2.856 | 184 | 64.4258
10.6 | 6.5801 | 1 | 2.856 | 184 | 64.4258
8.7 | 7.188 | 1 | 2.856 | 184 | 64.4258
8.1 | 6.9434 | 1 | 2.856 | 184 | 64.4258
8.4 | 6.4015 | 1 | 2.856 | 184 | 64.4258
8.4 | 6.4895 | 1 | 2.856 | 184 | 64.4258
9.2 | 6.7083 | 1 | 2.856 | 184 | 64.4258
9.7 | 6.956 | 1 | 2.856 | 184 | 64.4258
9.4 | 6.5959 | 1 | 2.856 | 184 | 64.4258
9.3 | 6.8044 | 1 | 2.856 | 184 | 64.4258
9.1 | 6.706 | 1 | 2.856 | 184 | 64.4258
8.9 | 6.6951 | 1 | 2.856 | 184 | 64.4258
8.8 | 6.69 | 1 | 2.856 | 184 | 64.4258
8.6 | 6.5913 | 1 | 2.856 | 184 | 64.4258
8.4 | 6.4478 | 1 | 2.856 | 184 | 64.4258
8.1 | 6.3881 | 1 | 2.856 | 184 | 64.4258
7.7 | 6.1878 | 1 | 2.856 | 184 | 64.4258
6.9 | 5.6484 | 1 | 2.856 | 184 | 64.4258
7.1 | 5.7945 | 1 | 2.856 | 184 | 64.4258
7.8 | 6.3281 | 1 | 2.856 | 184 | 64.4258
8.4 | 6.7165 | 1 | 2.856 | 184 | 64.4258
8.9 | 7.1906 | 1 | 2.856 | 184 | 64.4258
8.9 | 7.1442 | 1 | 2.856 | 184 | 64.4258
8.6 | 7.3292 | 1 | 2.856 | 184 | 64.4258
8.4 | 7.6248 | 1 | 2.856 | 184 | 64.4258
8.6 | 7.5221 | 1 | 2.856 | 184 | 64.4258
8.5 | 7.5723 | 1 | 2.856 | 184 | 64.4258
9.4 | 8.3972 | 1 | 2.856 | 184 | 64.4258
12 | 9.9303 | 1 | 2.856 | 184 | 64.4258
14.8 | 9.2962 | 1 | 2.856 | 184 | 64.4258
14 | 9.1754 | 1 | 2.856 | 184 | 64.4258
13.1 | 9.3281 | 1 | 2.856 | 184 | 64.4258
11.9 | 8.3376 | 1 | 2.856 | 184 | 64.4258
10.4 | 7.5869 | 1 | 2.856 | 184 | 64.4258
9.6 | 6.9821 | 1 | 2.856 | 184 | 64.4258
8.7 | 6.3665 | 1 | 2.856 | 184 | 64.4258
8.2 | 6.3382 | 1 | 2.856 | 184 | 64.4258
7.9 | 6.3703 | 1 | 2.856 | 184 | 64.4258
7.3 | 5.8885 | 1 | 2.856 | 184 | 64.4258
7.2 | 5.7019 | 1 | 2.856 | 184 | 64.4258
6.9 | 5.3274 | 1 | 2.856 | 184 | 64.4258
6.9 | 4.8968 | 1 | 2.856 | 184 | 64.4258
7.2 | 4.372 | 1 | 2.856 | 184 | 64.4258
7.5 | 4.3026 | 1 | 2.856 | 184 | 64.4258
9.7 | 5.3333 | 1 | 2.856 | 184 | 64.4258
10.8 | 5.5106 | 1 | 2.856 | 184 | 64.4258
12.9 | 7.096 | 1 | 2.856 | 184 | 64.4258
13.9 | 7.7469 | 1 | 2.856 | 184 | 64.4258
15.4 | 8.9028 | 1 | 2.856 | 184 | 64.4258
16.9 | 9.5052 | 1 | 2.856 | 184 | 64.4258
16.5 | 10.1105 | 1 | 2.856 | 184 | 64.4258
15.4 | 10.7768 | 1 | 2.856 | 184 | 64.4258
14.1 | 10.0786 | 1 | 2.856 | 184 | 64.4258
13.5 | 9.5401 | 1 | 2.856 | 184 | 64.4258
13.3 | 9.5864 | 1 | 2.856 | 184 | 64.4258
13.4 | 9.8609 | 1 | 2.856 | 184 | 64.4258
11.2 | 9.3156 | 1 | 2.856 | 184 | 64.4258
9.8 | 7.8923 | 1 | 2.856 | 184 | 64.4258
8.8 | 7.04 | 1 | 2.856 | 184 | 64.4258
8.6 | 6.943 | 1 | 2.856 | 184 | 64.4258
8.1 | 6.6059 | 1 | 2.856 | 184 | 64.4258
7.6 | 6.3597 | 1 | 2.856 | 184 | 64.4258
7.6 | 5.9928 | 1 | 2.856 | 184 | 64.4258
6.9 | 5.8247 | 1 | 2.856 | 184 | 64.4258
6.8 | 5.4095 | 1 | 2.856 | 184 | 64.4258
6.7 | 5.007 | 1 | 2.856 | 184 | 64.4258
6.3 | 4.757 | 1 | 2.856 | 184 | 64.4258
5.8 | 4.5407 | 1 | 2.856 | 184 | 64.4258
6.5 | 4.8615 | 1 | 2.856 | 184 | 64.4258
8.1 | 5.7654 | 1 | 2.856 | 184 | 64.4258
9.2 | 5.7527 | 1 | 2.856 | 184 | 64.4258
10.3 | 5.7175 | 1 | 2.856 | 184 | 64.4258
10.4 | 5.9454 | 1 | 2.856 | 184 | 64.4258
12.3 | 7.2436 | 1 | 2.856 | 184 | 64.4258
11.9 | 6.7246 | 1 | 2.856 | 184 | 64.4258
12.4 | 6.9336 | 1 | 2.856 | 184 | 64.4258
12.5 | 6.7453 | 1 | 2.856 | 184 | 64.4258
12.3 | 6.4967 | 1 | 2.856 | 184 | 64.4258
12.5 | 7.1613 | 1 | 2.856 | 184 | 64.4258
12 | 6.7409 | 1 | 2.856 | 184 | 64.4258
11.4 | 6.6638 | 1 | 2.856 | 184 | 64.4258
10.3 | 5.9357 | 1 | 2.856 | 184 | 64.4258
9.1 | 5.5538 | 1 | 2.856 | 184 | 64.4258
7.9 | 4.8628 | 1 | 2.856 | 184 | 64.4258
6.9 | 4.4179 | 1 | 2.856 | 184 | 64.4258
6.1 | 4.0344 | 1 | 2.856 | 184 | 64.4258
5.2 | 3.6759 | 1 | 2.856 | 184 | 64.4258
4.7 | 3.3648 | 1 | 2.856 | 184 | 64.4258
4 | 3.025 | 1 | 2.856 | 184 | 64.4258
3.8 | 3.0003 | 1 | 2.856 | 184 | 64.4258
3.7 | 2.903 | 1 | 2.856 | 184 | 64.4258
5 | 4.0361 | 1 | 2.856 | 184 | 64.4258
6.8 | 5.3272 | 1 | 2.856 | 184 | 64.4258
8.7 | 6.034 | 1 | 2.856 | 184 | 64.4258
9.7 | 6.2918 | 1 | 2.856 | 184 | 64.4258
10.6 | 6.3553 | 1 | 2.856 | 184 | 64.4258
11.7 | 6.7172 | 1 | 2.856 | 184 | 64.4258
11.8 | 6.9103 | 1 | 2.856 | 184 | 64.4258
12.3 | 7.1539 | 1 | 2.856 | 184 | 64.4258
12.2 | 6.7877 | 1 | 2.856 | 184 | 64.4258
12.2 | 6.6172 | 1 | 2.856 | 184 | 64.4258
12.2 | 7.1053 | 1 | 2.856 | 184 | 64.4258
11.7 | 6.6463 | 1 | 2.856 | 184 | 64.4258
11.4 | 6.0707 | 1 | 2.856 | 184 | 64.4258
9.9 | 5.195 | 1 | 2.856 | 184 | 64.4258
8.2 | 4.5859 | 1 | 2.856 | 184 | 64.4258
7.5 | 3.937 | 1 | 2.856 | 184 | 64.4258
6.5 | 3.5603 | 1 | 2.856 | 184 | 64.4258
5.7 | 3.3621 | 1 | 2.856 | 184 | 64.4258
5.7 | 3.7088 | 1 | 2.856 | 184 | 64.4258
4.8 | 3.2609 | 1 | 2.856 | 184 | 64.4258
4.3 | 2.9872 | 1 | 2.856 | 184 | 64.4258
5.1 | 3.5859 | 1 | 2.856 | 184 | 64.4258
5.3 | 3.7346 | 1 | 2.856 | 184 | 64.4258
5.5 | 3.8013 | 1 | 2.856 | 184 | 64.4258
5.7 | 4.031 | 1 | 2.856 | 184 | 64.4258
6.5 | 4.4551 | 1 | 2.856 | 184 | 64.4258
7.3 | 4.8342 | 1 | 2.856 | 184 | 64.4258
8.2 | 5.4605 | 1 | 2.856 | 184 | 64.4258
9.4 | 5.9519 | 1 | 2.856 | 184 | 64.4258
9.9 | 6.2417 | 1 | 2.856 | 184 | 64.4258
9.9 | 6.4378 | 1 | 2.856 | 184 | 64.4258
10.9 | 6.8147 | 1 | 2.856 | 184 | 64.4258
11.1 | 6.5385 | 1 | 2.856 | 184 | 64.4258
11.9 | 6.579 | 1 | 2.856 | 184 | 64.4258
11.7 | 6.6186 | 1 | 2.856 | 184 | 64.4258
12 | 6.1934 | 1 | 2.856 | 184 | 64.4258
12.1 | 5.7959 | 1 | 2.856 | 184 | 64.4258
11.1 | 5.1561 | 1 | 2.856 | 184 | 64.4258
10.2 | 4.7907 | 1 | 2.856 | 184 | 64.4258
9.2 | 4.9951 | 1 | 2.856 | 184 | 64.4258
7.8 | 5.3388 | 1 | 2.856 | 184 | 64.4258
6.9 | 5.1245 | 1 | 2.856 | 184 | 64.4258
6 | 5.0079 | 1 | 2.856 | 184 | 64.4258
5.8 | 4.7255 | 1 | 2.856 | 184 | 64.4258
5.6 | 4.5764 | 1 | 2.856 | 184 | 64.4258
5.3 | 4.4183 | 1 | 2.856 | 184 | 64.4258
5.3 | 4.3736 | 1 | 2.856 | 184 | 64.4258
5.6 | 4.5759 | 1 | 2.856 | 184 | 64.4258
6.2 | 5.1116 | 1 | 2.856 | 184 | 64.4258
6.9 | 5.6509 | 1 | 2.856 | 184 | 64.4258
8.1 | 6.4357 | 1 | 2.856 | 184 | 64.4258
10.4 | 7.5168 | 1 | 2.856 | 184 | 64.4258
12.3 | 8.4607 | 1 | 2.856 | 184 | 64.4258
13.3 | 8.5562 | 1 | 2.856 | 184 | 64.4258
14.3 | 8.6716 | 1 | 2.856 | 184 | 64.4258
14.3 | 8.6716 | 1 | 2.856 | 184 | 64.4258
14.4 | 8.7936 | 1 | 2.856 | 184 | 64.4258
15.2 | 9.0097 | 1 | 2.856 | 184 | 64.4258
14.7 | 9.008 | 1 | 2.856 | 184 | 64.4258
14.4 | 8.87 | 1 | 2.856 | 184 | 64.4258
13.9 | 8.6386 | 1 | 2.856 | 184 | 64.4258
13.3 | 8.2424 | 1 | 2.856 | 184 | 64.4258
12.2 | 7.4918 | 1 | 2.856 | 184 | 64.4258
11 | 6.5688 | 1 | 2.856 | 184 | 64.4258
9.6 | 6.0596 | 1 | 2.856 | 184 | 64.4258
8.2 | 5.3467 | 1 | 2.856 | 184 | 64.4258
7.1 | 5.0203 | 1 | 2.856 | 184 | 64.4258
6.4 | 4.613 | 1 | 2.856 | 184 | 64.4258
5.7 | 4.37 | 1 | 2.856 | 184 | 64.4258
5.4 | 4.428 | 1 | 2.856 | 184 | 64.4258
5 | 4.1279 | 1 | 2.856 | 184 | 64.4258
5 | 4.1279 | 1 | 2.856 | 184 | 64.4258
6.4 | 4.9959 | 1 | 2.856 | 184 | 64.4258
8.4 | 5.9779 | 1 | 2.856 | 184 | 64.4258
10.8 | 6.4716 | 1 | 2.856 | 184 | 64.4258
12.7 | 7.2265 | 1 | 2.856 | 184 | 64.4258
13.9 | 7.9057 | 1 | 2.856 | 184 | 64.4258
14.6 | 8.1683 | 1 | 2.856 | 184 | 64.4258
15.1 | 8.1377 | 1 | 2.856 | 184 | 64.4258
15.7 | 8.4488 | 1 | 2.856 | 184 | 64.4258
16.5 | 9.0158 | 1 | 2.856 | 184 | 64.4258
16.8 | 8.7934 | 1 | 2.856 | 184 | 64.4258
16.7 | 9.0711 | 1 | 2.856 | 184 | 64.4258
17 | 9.0434 | 1 | 2.856 | 184 | 64.4258
15.5 | 8.7865 | 1 | 2.856 | 184 | 64.4258
13.7 | 7.9438 | 1 | 2.856 | 184 | 64.4258
12.3 | 6.8157 | 1 | 2.856 | 184 | 64.4258
10.2 | 5.3218 | 1 | 2.856 | 184 | 64.4258
9.4 | 5.2519 | 1 | 2.856 | 184 | 64.4258
9 | 4.9697 | 1 | 2.856 | 184 | 64.4258
9 | 5.0785 | 1 | 2.856 | 184 | 64.4258
8.2 | 4.7341 | 1 | 2.856 | 184 | 64.4258
7.1 | 4.7711 | 1 | 2.856 | 184 | 64.4258
6.3 | 4.7246 | 1 | 2.856 | 184 | 64.4258
5.7 | 4.4526 | 1 | 2.856 | 184 | 64.4258
5.5 | 4.5666 | 1 | 2.856 | 184 | 64.4258
6.1 | 4.7926 | 1 | 2.856 | 184 | 64.4258
6.6 | 5.2716 | 1 | 2.856 | 184 | 64.4258
7.7 | 5.9637 | 1 | 2.856 | 184 | 64.4258
9.1 | 7.0601 | 1 | 2.856 | 184 | 64.4258
10.4 | 7.5536 | 1 | 2.856 | 184 | 64.4258
12.2 | 8.7084 | 1 | 2.856 | 184 | 64.4258
14.3 | 9.7914 | 1 | 2.856 | 184 | 64.4258
14.6 | 9.9228 | 1 | 2.856 | 184 | 64.4258
13.4 | 10.8985 | 1 | 2.856 | 184 | 64.4258
14.8 | 11.247 | 1 | 2.856 | 184 | 64.4258
16.9 | 12.0295 | 1 | 2.856 | 184 | 64.4258
17.2 | 12.294 | 1 | 2.856 | 184 | 64.4258
17.4 | 12.564 | 1 | 2.856 | 184 | 64.4258
17.2 | 12.7259 | 1 | 2.856 | 184 | 64.4258
17.1 | 13.3429 | 1 | 2.856 | 184 | 64.4258
16.4 | 13.2766 | 1 | 2.856 | 184 | 64.4258
15.6 | 12.7434 | 1 | 2.856 | 184 | 64.4258
15 | 11.4739 | 1 | 2.856 | 184 | 64.4258
13.6 | 10.9799 | 1 | 2.856 | 184 | 64.4258
12.3 | 11.2172 | 1 | 2.856 | 184 | 64.4258
12.3 | 11.4385 | 1 | 2.856 | 184 | 64.4258
11.2 | 10.6357 | 1 | 2.856 | 184 | 64.4258
10.3 | 9.6411 | 1 | 2.856 | 184 | 64.4258
9.8 | 9.0972 | 1 | 2.856 | 184 | 64.4258
10.2 | 9.4896 | 1 | 2.856 | 184 | 64.4258
12.3 | 10.9994 | 1 | 2.856 | 184 | 64.4258
13.8 | 11.9008 | 1 | 2.856 | 184 | 64.4258
16.1 | 13.5364 | 1 | 2.856 | 184 | 64.4258
17.9 | 14.6695 | 1 | 2.856 | 184 | 64.4258
19.8 | 15.7592 | 1 | 2.856 | 184 | 64.4258
21.9 | 16.4557 | 1 | 2.856 | 184 | 64.4258
21.8 | 16.8577 | 1 | 2.856 | 184 | 64.4258
22.4 | 16.0051 | 1 | 2.856 | 184 | 64.4258
22.1 | 16.1036 | 1 | 2.856 | 184 | 64.4258
21.9 | 15.7738 | 1 | 2.856 | 184 | 64.4258
21.9 | 15.4707 | 1 | 2.856 | 184 | 64.4258
20.5 | 15.1071 | 1 | 2.856 | 184 | 64.4258
19.5 | 14.6319 | 1 | 2.856 | 184 | 64.4258
18.9 | 14.6678 | 1 | 2.856 | 184 | 64.4258
18.5 | 14.3588 | 1 | 2.856 | 184 | 64.4258
17.5 | 13.8154 | 1 | 2.856 | 184 | 64.4258
16.4 | 13.0665 | 1 | 2.856 | 184 | 64.4258
15.7 | 12.4208 | 1 | 2.856 | 184 | 64.4258
15 | 11.9791 | 1 | 2.856 | 184 | 64.4258
14.4 | 11.6266 | 1 | 2.856 | 184 | 64.4258
13.7 | 11.3319 | 1 | 2.856 | 184 | 64.4258
13.2 | 11.1196 | 1 | 2.856 | 184 | 64.4258
13 | 11.0875 | 1 | 2.856 | 184 | 64.4258
13.8 | 11.5838 | 1 | 2.856 | 184 | 64.4258
15.1 | 12.1763 | 1 | 2.856 | 184 | 64.4258
15.8 | 12.7747 | 1 | 2.856 | 184 | 64.4258
18 | 14.0121 | 1 | 2.856 | 184 | 64.4258
21.1 | 15.2334 | 1 | 2.856 | 184 | 64.4258
23.6 | 15.3847 | 1 | 2.856 | 184 | 64.4258
24.6 | 16.2117 | 1 | 2.856 | 184 | 64.4258
25.9 | 15.7402 | 1 | 2.856 | 184 | 64.4258
25.8 | 14.5516 | 1 | 2.856 | 184 | 64.4258
25.7 | 14.7357 | 1 | 2.856 | 184 | 64.4258
25.5 | 14.4378 | 1 | 2.856 | 184 | 64.4258
24.3 | 13.7173 | 1 | 2.856 | 184 | 64.4258
22.5 | 13.671 | 1 | 2.856 | 184 | 64.4258
20.7 | 13.9233 | 1 | 2.856 | 184 | 64.4258
19 | 12.8895 | 1 | 2.856 | 184 | 64.4258
16.9 | 12.0823 | 1 | 2.856 | 184 | 64.4258
17 | 12.3129 | 1 | 2.856 | 184 | 64.4258
15.5 | 11.5943 | 1 | 2.856 | 184 | 64.4258
14.8 | 11.1532 | 1 | 2.856 | 184 | 64.4258
13.8 | 10.675 | 1 | 2.856 | 184 | 64.4258
12.8 | 10.1893 | 1 | 2.856 | 184 | 64.4258
12.4 | 9.9142 | 1 | 2.856 | 184 | 64.4258
11.6 | 9.5072 | 1 | 2.856 | 184 | 64.4258
11.1 | 9.2317 | 1 | 2.856 | 184 | 64.4258
12.6 | 10.0029 | 1 | 2.856 | 184 | 64.4258
14.4 | 10.5546 | 1 | 2.856 | 184 | 64.4258
16.8 | 11.7146 | 1 | 2.856 | 184 | 64.4258
18.9 | 11.8144 | 1 | 2.856 | 184 | 64.4258
20.9 | 11.9891 | 1 | 2.856 | 184 | 64.4258
22 | 12.9238 | 1 | 2.856 | 184 | 64.4258
23.3 | 13.0336 | 1 | 2.856 | 184 | 64.4258
24 | 13.6329 | 1 | 2.856 | 184 | 64.4258
24.6 | 13.9401 | 1 | 2.856 | 184 | 64.4258
24.4 | 14.2 | 1 | 2.856 | 184 | 64.4258
23.8 | 15.4489 | 1 | 2.856 | 184 | 64.4258
22.2 | 14.8569 | 1 | 2.856 | 184 | 64.4258
21.5 | 14.0872 | 1 | 2.856 | 184 | 64.4258
19.8 | 13.612 | 1 | 2.856 | 184 | 64.4258
17.5 | 12.7472 | 1 | 2.856 | 184 | 64.4258
17.8 | 12.9143 | 1 | 2.856 | 184 | 64.4258
17.3 | 12.7135 | 1 | 2.856 | 184 | 64.4258
16 | 12.3843 | 1 | 2.856 | 184 | 64.4258
14.7 | 11.8499 | 1 | 2.856 | 184 | 64.4258
13.7 | 11.2751 | 1 | 2.856 | 184 | 64.4258
13.1 | 10.8125 | 1 | 2.856 | 184 | 64.4258
12.4 | 10.4065 | 1 | 2.856 | 184 | 64.4258
12 | 10.1291 | 1 | 2.856 | 184 | 64.4258
11.9 | 10.0844 | 1 | 2.856 | 184 | 64.4258
12.3 | 10.3108 | 1 | 2.856 | 184 | 64.4258
13.6 | 11.1254 | 1 | 2.856 | 184 | 64.4258
15.3 | 12.2472 | 1 | 2.856 | 184 | 64.4258
17.7 | 13.6176 | 1 | 2.856 | 184 | 64.4258
19.8 | 14.676 | 1 | 2.856 | 184 | 64.4258
21.9 | 15.756 | 1 | 2.856 | 184 | 64.4258
23 | 16.3534 | 1 | 2.856 | 184 | 64.4258
24.7 | 15.8384 | 1 | 2.856 | 184 | 64.4258
24 | 16.1063 | 1 | 2.856 | 184 | 64.4258
23.8 | 15.4182 | 1 | 2.856 | 184 | 64.4258
22.6 | 14.5206 | 1 | 2.856 | 184 | 64.4258
21.5 | 14.6152 | 1 | 2.856 | 184 | 64.4258
20.3 | 14.7587 | 1 | 2.856 | 184 | 64.4258
18.8 | 14.6679 | 1 | 2.856 | 184 | 64.4258
15.9 | 13.4492 | 1 | 2.856 | 184 | 64.4258
15.1 | 12.4251 | 1 | 2.856 | 184 | 64.4258
14.4 | 11.5124 | 1 | 2.856 | 184 | 64.4258
13.6 | 10.5222 | 1 | 2.856 | 184 | 64.4258
13.1 | 10.0136 | 1 | 2.856 | 184 | 64.4258
12.9 | 10.1185 | 1 | 2.856 | 184 | 64.4258
12.8 | 10.3729 | 1 | 2.856 | 184 | 64.4258
12.6 | 10.2859 | 1 | 2.856 | 184 | 64.4258
12 | 9.9727 | 1 | 2.856 | 184 | 64.4258
11.7 | 9.9427 | 1 | 2.856 | 184 | 64.4258
12.2 | 10.1112 | 1 | 2.856 | 184 | 64.4258
12.3 | 10.3073 | 1 | 2.856 | 184 | 64.4258
12.4 | 10.61 | 1 | 2.856 | 184 | 64.4258
12.5 | 10.7055 | 1 | 2.856 | 184 | 64.4258
12.3 | 10.8858 | 1 | 2.856 | 184 | 64.4258
12.6 | 11.4491 | 1 | 2.856 | 184 | 64.4258
13.1 | 11.8235 | 1 | 2.856 | 184 | 64.4258
13.5 | 12.0994 | 1 | 2.856 | 184 | 64.4258
13.9 | 12.4861 | 1 | 2.856 | 184 | 64.4258
14.4 | 12.5753 | 1 | 2.856 | 184 | 64.4258
14.6 | 12.5454 | 1 | 2.856 | 184 | 64.4258
14.8 | 12.5713 | 1 | 2.856 | 184 | 64.4258
14.7 | 12.3671 | 1 | 2.856 | 184 | 64.4258
13.9 | 12.0967 | 1 | 2.856 | 184 | 64.4258
13.3 | 11.9049 | 1 | 2.856 | 184 | 64.4258
12.8 | 11.6983 | 1 | 2.856 | 184 | 64.4258
12.6 | 11.7278 | 1 | 2.856 | 184 | 64.4258
12.6 | 11.7844 | 1 | 2.856 | 184 | 64.4258
13.1 | 10.0136 | 1 | 2.856 | 184 | 64.4258
12.5 | 11.6299 | 1 | 2.856 | 184 | 64.4258
12.4 | 11.309 | 1 | 2.856 | 184 | 64.4258
11 | 10.3255 | 1 | 2.856 | 184 | 64.4258
10.4 | 9.7897 | 1 | 2.856 | 184 | 64.4258
11.1 | 10.4786 | 1 | 2.856 | 184 | 64.4258
10.9 | 9.7966 | 1 | 2.856 | 184 | 64.4258
11.2 | 9.9288 | 1 | 2.856 | 184 | 64.4258
12.6 | 10.9054 | 1 | 2.856 | 184 | 64.4258
13.7 | 11.5281 | 1 | 2.856 | 184 | 64.4258
15.4 | 12.1768 | 1 | 2.856 | 184 | 64.4258
15.8 | 12.0342 | 1 | 2.856 | 184 | 64.4258
16.8 | 11.9581 | 1 | 2.856 | 184 | 64.4258
18.7 | 12.6821 | 1 | 2.856 | 184 | 64.4258
18.5 | 12.2827 | 1 | 2.856 | 184 | 64.4258
18.5 | 11.8899 | 1 | 2.856 | 184 | 64.4258
18.1 | 12.2075 | 1 | 2.856 | 184 | 64.4258
15.8 | 11.9314 | 1 | 2.856 | 184 | 64.4258
15.6 | 12.6197 | 1 | 2.856 | 184 | 64.4258
15.3 | 12.0805 | 1 | 2.856 | 184 | 64.4258
14.7 | 11.5776 | 1 | 2.856 | 184 | 64.4258
14.4 | 11.8164 | 1 | 2.856 | 184 | 64.4258
13.5 | 11.1265 | 1 | 2.856 | 184 | 64.4258
12.6 | 11.2267 | 1 | 2.856 | 184 | 64.4258
12.1 | 11.0157 | 1 | 2.856 | 184 | 64.4258
11.9 | 11.0412 | 1 | 2.856 | 184 | 64.4258
11.8 | 10.6683 | 1 | 2.856 | 184 | 64.4258
11.8 | 10.6141 | 1 | 2.856 | 184 | 64.4258
11.2 | 10.6872 | 1 | 2.856 | 184 | 64.4258
11.3 | 10.5081 | 1 | 2.856 | 184 | 64.4258
11.1 | 10.3666 | 1 | 2.856 | 184 | 64.4258
11.4 | 10.8282 | 1 | 2.856 | 184 | 64.4258
11.7 | 10.9555 | 1 | 2.856 | 184 | 64.4258
13.4 | 12.109 | 1 | 2.856 | 184 | 64.4258
13.3 | 12.1814 | 1 | 2.856 | 184 | 64.4258
14.1 | 12.5605 | 1 | 2.856 | 184 | 64.4258
15.2 | 12.7228 | 1 | 2.856 | 184 | 64.4258
14.9 | 13.1614 | 1 | 2.856 | 184 | 64.4258
14.7 | 12.5248 | 1 | 2.856 | 184 | 64.4258
13.4 | 11.6129 | 1 | 2.856 | 184 | 64.4258
14.9 | 12.442 | 1 | 2.856 | 184 | 64.4258
14.3 | 11.4597 | 1 | 2.856 | 184 | 64.4258
13.8 | 11.199 | 1 | 2.856 | 184 | 64.4258
13.2 | 10.4879 | 1 | 2.856 | 184 | 64.4258
12.6 | 9.6864 | 1 | 2.856 | 184 | 64.4258
11.6 | 9.7395 | 1 | 2.856 | 184 | 64.4258
11.2 | 9.7171 | 1 | 2.856 | 184 | 64.4258
10.9 | 9.4804 | 1 | 2.856 | 184 | 64.4258
10.9 | 9.3774 | 1 | 2.856 | 184 | 64.4258
10.5 | 9.2492 | 1 | 2.856 | 184 | 64.4258
10.5 | 9.0431 | 1 | 2.856 | 184 | 64.4258
10.6 | 8.9358 | 1 | 2.856 | 184 | 64.4258
10.4 | 9.1509 | 1 | 2.856 | 184 | 64.4258
9 | 7.3598 | 1 | 2.856 | 184 | 64.4258
8.6 | 6.6999 | 1 | 2.856 | 184 | 64.4258
8.4 | 6.4658 | 1 | 2.856 | 184 | 64.4258
8.3 | 6.4177 | 1 | 2.856 | 184 | 64.4258
7.4 | 6.021 | 1 | 2.856 | 184 | 64.4258
7.3 | 6.2056 | 1 | 2.856 | 184 | 64.4258
7.6 | 5.849 | 1 | 2.856 | 184 | 64.4258
7.4 | 6.3503 | 1 | 2.856 | 184 | 64.4258
7.8 | 6.4531 | 1 | 2.856 | 184 | 64.4258
7.7 | 6.594 | 1 | 2.856 | 184 | 64.4258
7 | 6.0589 | 1 | 2.856 | 184 | 64.4258
7.7 | 6.6425 | 1 | 2.856 | 184 | 64.4258
8.2 | 7.1274 | 1 | 2.856 | 184 | 64.4258
8.6 | 7.9166 | 1 | 2.856 | 184 | 64.4258
9 | 8.3092 | 1 | 2.856 | 184 | 64.4258
9.2 | 8.4539 | 1 | 2.856 | 184 | 64.4258
8.9 | 8.1093 | 1 | 2.856 | 184 | 64.4258
8.7 | 8.0156 | 1 | 2.856 | 184 | 64.4258
9.4 | 8.4956 | 1 | 2.856 | 184 | 64.4258
9.6 | 8.5368 | 1 | 2.856 | 184 | 64.4258
9.7 | 8.6855 | 1 | 2.856 | 184 | 64.4258
10 | 8.5714 | 1 | 2.856 | 184 | 64.4258
9.8 | 7.2525 | 1 | 2.856 | 184 | 64.4258
9.3 | 6.9218 | 1 | 2.856 | 184 | 64.4258
8.6 | 7.0388 | 1 | 2.856 | 184 | 64.4258
8.7 | 6.5417 | 1 | 2.856 | 184 | 64.4258
9.1 | 6.7834 | 1 | 2.856 | 184 | 64.4258
10.1 | 7.314 | 1 | 2.856 | 184 | 64.4258
11.3 | 8.1053 | 1 | 2.856 | 184 | 64.4258
11.5 | 8.3329 | 1 | 2.856 | 184 | 64.4258
12.3 | 8.5752 | 1 | 2.856 | 184 | 64.4258
13.4 | 8.9963 | 1 | 2.856 | 184 | 64.4258
15 | 9.2011 | 1 | 2.856 | 184 | 64.4258
14.9 | 8.9647 | 1 | 2.856 | 184 | 64.4258
15.3 | 9.2606 | 1 | 2.856 | 184 | 64.4258
14.2 | 9.1973 | 1 | 2.856 | 184 | 64.4258
14.1 | 9.1518 | 1 | 2.856 | 184 | 64.4258
14.7 | 9.5874 | 1 | 2.856 | 184 | 64.4258
13.9 | 9.4397 | 1 | 2.856 | 184 | 64.4258
13.3 | 8.9545 | 1 | 2.856 | 184 | 64.4258
11.4 | 8.3364 | 1 | 2.856 | 184 | 64.4258
10.2 | 7.9997 | 1 | 2.856 | 184 | 64.4258
9.1 | 7.6667 | 1 | 2.856 | 184 | 64.4258
7.7 | 6.7959 | 1 | 2.856 | 184 | 64.4258
7.9 | 7.1371 | 1 | 2.856 | 184 | 64.4258
9.4 | 8.3999 | 1 | 2.856 | 184 | 64.4258
7.9 | 7.3356 | 1 | 2.856 | 184 | 64.4258
7.1 | 6.6469 | 1 | 2.856 | 184 | 64.4258
8.3 | 7.7798 | 1 | 2.856 | 184 | 64.4258
8.9 | 8.3711 | 1 | 2.856 | 184 | 64.4258
10.3 | 9.4844 | 1 | 2.856 | 184 | 64.4258
12.1 | 10.3892 | 1 | 2.856 | 184 | 64.4258
13.7 | 11.1838 | 1 | 2.856 | 184 | 64.4258
14.5 | 11.5738 | 1 | 2.856 | 184 | 64.4258
15.4 | 11.8014 | 1 | 2.856 | 184 | 64.4258
15.4 | 11.318 | 1 | 2.856 | 184 | 64.4258
15.5 | 10.8986 | 1 | 2.856 | 184 | 64.4258
15.5 | 11.1732 | 1 | 2.856 | 184 | 64.4258
15.6 | 11.309 | 1 | 2.856 | 184 | 64.4258
15.8 | 11.5346 | 1 | 2.856 | 184 | 64.4258
15.2 | 11.4727 | 1 | 2.856 | 184 | 64.4258
15.5 | 11.4078 | 1 | 2.856 | 184 | 64.4258
15.5 | 11.4078 | 1 | 2.856 | 184 | 64.4258
14.8 | 11.4011 | 1 | 2.856 | 184 | 64.4258
14.8 | 11.1098 | 1 | 2.856 | 184 | 64.4258
13.5 | 10.9965 | 1 | 2.856 | 184 | 64.4258
13.6 | 10.7887 | 1 | 2.856 | 184 | 64.4258
12.8 | 10.4911 | 1 | 2.856 | 184 | 64.4258
11.7 | 10.059 | 1 | 2.856 | 184 | 64.4258
11.5 | 10.0737 | 1 | 2.856 | 184 | 64.4258
11.5 | 10.0737 | 1 | 2.856 | 184 | 64.4258
11 | 9.8515 | 1 | 2.856 | 184 | 64.4258
11.3 | 10.1424 | 1 | 2.856 | 184 | 64.4258
12.2 | 10.7477 | 1 | 2.856 | 184 | 64.4258
13.6 | 11.4525 | 1 | 2.856 | 184 | 64.4258
15.3 | 12.2157 | 1 | 2.856 | 184 | 64.4258
15.9 | 12.4114 | 1 | 2.856 | 184 | 64.4258
16 | 12.1033 | 1 | 2.856 | 184 | 64.4258
16.9 | 11.9525 | 1 | 2.856 | 184 | 64.4258
18.1 | 12.4934 | 1 | 2.856 | 184 | 64.4258
17.4 | 12.3453 | 1 | 2.856 | 184 | 64.4258
17.8 | 12.2792 | 1 | 2.856 | 184 | 64.4258
17.5 | 12.2934 | 1 | 2.856 | 184 | 64.4258
17.6 | 12.568 | 1 | 2.856 | 184 | 64.4258
17.4 | 12.1578 | 1 | 2.856 | 184 | 64.4258
17.3 | 11.8912 | 1 | 2.856 | 184 | 64.4258
16.2 | 11.7517 | 1 | 2.856 | 184 | 64.4258
16.5 | 11.6012 | 1 | 2.856 | 184 | 64.4258
13.7 | 10.4933 | 1 | 2.856 | 184 | 64.4258
12.5 | 9.2558 | 1 | 2.856 | 184 | 64.4258
11.5 | 8.8449 | 1 | 2.856 | 184 | 64.4258
10.6 | 8.5215 | 1 | 2.856 | 184 | 64.4258
10.5 | 8.6671 | 1 | 2.856 | 184 | 64.4258
9.8 | 8.5884 | 1 | 2.856 | 184 | 64.4258
9.1 | 8.0598 | 1 | 2.856 | 184 | 64.4258
8.4 | 7.627 | 1 | 2.856 | 184 | 64.4258
9 | 8.0125 | 1 | 2.856 | 184 | 64.4258
10.3 | 8.7698 | 1 | 2.856 | 184 | 64.4258
12.3 | 9.3961 | 1 | 2.856 | 184 | 64.4258
14.6 | 10.1529 | 1 | 2.856 | 184 | 64.4258
16.3 | 10.2301 | 1 | 2.856 | 184 | 64.4258
16.4 | 10.5575 | 1 | 2.856 | 184 | 64.4258
17 | 10.9413 | 1 | 2.856 | 184 | 64.4258
17.7 | 11.4484 | 1 | 2.856 | 184 | 64.4258
17.6 | 11.7461 | 1 | 2.856 | 184 | 64.4258
17.3 | 11.1921 | 1 | 2.856 | 184 | 64.4258
17.8 | 11.4436 | 1 | 2.856 | 184 | 64.4258
17.4 | 11.1904 | 1 | 2.856 | 184 | 64.4258
17.2 | 11.1468 | 1 | 2.856 | 184 | 64.4258
16.8 | 10.6447 | 1 | 2.856 | 184 | 64.4258
15.4 | 9.7857 | 1 | 2.856 | 184 | 64.4258
13.9 | 8.5518 | 1 | 2.856 | 184 | 64.4258
12.9 | 8.4035 | 1 | 2.856 | 184 | 64.4258
12.3 | 7.8801 | 1 | 2.856 | 184 | 64.4258
11.5 | 7.7424 | 1 | 2.856 | 184 | 64.4258
10.9 | 7.006 | 1 | 2.856 | 184 | 64.4258
10.3 | 6.6324 | 1 | 2.856 | 184 | 64.4258
9.5 | 6.3967 | 1 | 2.856 | 184 | 64.4258
8.9 | 6.1384 | 1 | 2.856 | 184 | 64.4258
8.7 | 6.2057 | 1 | 2.856 | 184 | 64.4258
8.8 | 6.5132 | 1 | 2.856 | 184 | 64.4258
10.5 | 7.6029 | 1 | 2.856 | 184 | 64.4258
12.4 | 8.8906 | 1 | 2.856 | 184 | 64.4258
14.4 | 9.9706 | 1 | 2.856 | 184 | 64.4258
16.1 | 10.8888 | 1 | 2.856 | 184 | 64.4258
16.5 | 10.9315 | 1 | 2.856 | 184 | 64.4258
17.6 | 11.443 | 1 | 2.856 | 184 | 64.4258
17.9 | 11.3206 | 1 | 2.856 | 184 | 64.4258
18.5 | 11.6558 | 1 | 2.856 | 184 | 64.4258
19 | 12.2784 | 1 | 2.856 | 184 | 64.4258
18.7 | 11.9434 | 1 | 2.856 | 184 | 64.4258
18.5 | 11.7352 | 1 | 2.856 | 184 | 64.4258
18.4 | 11.4484 | 1 | 2.856 | 184 | 64.4258
17.4 | 10.9416 | 1 | 2.856 | 184 | 64.4258
16.2 | 10.5042 | 1 | 2.856 | 184 | 64.4258
15.6 | 9.6741 | 1 | 2.856 | 184 | 64.4258
14.3 | 9.9261 | 1 | 2.856 | 184 | 64.4258
13.1 | 9.2548 | 1 | 2.856 | 184 | 64.4258
12.4 | 8.8906 | 1 | 2.856 | 184 | 64.4258
11.7 | 8.5671 | 1 | 2.856 | 184 | 64.4258
11 | 8.4228 | 1 | 2.856 | 184 | 64.4258
10.4 | 8.2821 | 1 | 2.856 | 184 | 64.4258
9.6 | 7.9526 | 1 | 2.856 | 184 | 64.4258
9.1 | 7.7149 | 1 | 2.856 | 184 | 64.4258
9 | 7.8132 | 1 | 2.856 | 184 | 64.4258
11 | 9.2874 | 1 | 2.856 | 184 | 64.4258
12.3 | 10.4759 | 1 | 2.856 | 184 | 64.4258
14.6 | 11.7175 | 1 | 2.856 | 184 | 64.4258
16.7 | 12.8335 | 1 | 2.856 | 184 | 64.4258
18.9 | 13.5609 | 1 | 2.856 | 184 | 64.4258
20 | 13.8007 | 1 | 2.856 | 184 | 64.4258
21.3 | 14.2571 | 1 | 2.856 | 184 | 64.4258
22 | 13.6533 | 1 | 2.856 | 184 | 64.4258
22.2 | 13.9383 | 1 | 2.856 | 184 | 64.4258
22.5 | 13.4806 | 1 | 2.856 | 184 | 64.4258
22.3 | 13.2052 | 1 | 2.856 | 184 | 64.4258
21.8 | 13.0056 | 1 | 2.856 | 184 | 64.4258
21 | 12.8029 | 1 | 2.856 | 184 | 64.4258
19.3 | 12.0272 | 1 | 2.856 | 184 | 64.4258
17.4 | 11.4864 | 1 | 2.856 | 184 | 64.4258
15.3 | 10.4545 | 1 | 2.856 | 184 | 64.4258
13.9 | 9.9712 | 1 | 2.856 | 184 | 64.4258
13.9 | 10.1552 | 1 | 2.856 | 184 | 64.4258
13.8 | 10.297 | 1 | 2.856 | 184 | 64.4258
13.1 | 9.752 | 1 | 2.856 | 184 | 64.4258
12.2 | 9.394 | 1 | 2.856 | 184 | 64.4258
11.1 | 8.9887 | 1 | 2.856 | 184 | 64.4258
10.7 | 8.9518 | 1 | 2.856 | 184 | 64.4258
10.8 | 9.0966 | 1 | 2.856 | 184 | 64.4258
12.3 | 9.823 | 1 | 2.856 | 184 | 64.4258
15.2 | 10.7672 | 1 | 2.856 | 184 | 64.4258
17.6 | 11.8755 | 1 | 2.856 | 184 | 64.4258
18 | 11.7412 | 1 | 2.856 | 184 | 64.4258
19.5 | 12.8332 | 1 | 2.856 | 184 | 64.4258
20.2 | 13.1549 | 1 | 2.856 | 184 | 64.4258
21.7 | 14.0509 | 1 | 2.856 | 184 | 64.4258
22.3 | 14.1514 | 1 | 2.856 | 184 | 64.4258
22.7 | 14.1315 | 1 | 2.856 | 184 | 64.4258
23.3 | 14.2783 | 1 | 2.856 | 184 | 64.4258
22.6 | 14.0088 | 1 | 2.856 | 184 | 64.4258
21 | 14.4645 | 1 | 2.856 | 184 | 64.4258
19.4 | 13.283 | 1 | 2.856 | 184 | 64.4258
18.2 | 12.5709 | 1 | 2.856 | 184 | 64.4258
16.3 | 10.9725 | 1 | 2.856 | 184 | 64.4258
14.6 | 10.738 | 1 | 2.856 | 184 | 64.4258
13.2 | 10.1259 | 1 | 2.856 | 184 | 64.4258
11.9 | 9.7923 | 1 | 2.856 | 184 | 64.4258
11.3 | 9.8799 | 1 | 2.856 | 184 | 64.4258
12.1 | 10.6502 | 1 | 2.856 | 184 | 64.4258
11.8 | 10.4139 | 1 | 2.856 | 184 | 64.4258
11.5 | 10.124 | 1 | 2.856 | 184 | 64.4258
11.3 | 9.725 | 1 | 2.856 | 184 | 64.4258
10.9 | 9.4432 | 1 | 2.856 | 184 | 64.4258
10.5 | 8.8592 | 1 | 2.856 | 184 | 64.4258
10.8 | 8.9969 | 1 | 2.856 | 184 | 64.4258
11.4 | 9.3194 | 1 | 2.856 | 184 | 64.4258
12.2 | 9.7772 | 1 | 2.856 | 184 | 64.4258
14.2 | 10.9953 | 1 | 2.856 | 184 | 64.4258
16 | 12.0478 | 1 | 2.856 | 184 | 64.4258
16.6 | 12.1966 | 1 | 2.856 | 184 | 64.4258
18.2 | 12.9404 | 1 | 2.856 | 184 | 64.4258
19.3 | 13.1464 | 1 | 2.856 | 184 | 64.4258
20.1 | 13.83 | 1 | 2.856 | 184 | 64.4258
20.4 | 14.2306 | 1 | 2.856 | 184 | 64.4258
20.3 | 14.0966 | 1 | 2.856 | 184 | 64.4258
19.4 | 13.9918 | 1 | 2.856 | 184 | 64.4258
18.1 | 13.5857 | 1 | 2.856 | 184 | 64.4258
16.6 | 12.9918 | 1 | 2.856 | 184 | 64.4258
15.5 | 12.6008 | 1 | 2.856 | 184 | 64.4258
15 | 12.7191 | 1 | 2.856 | 184 | 64.4258
14.5 | 12.7367 | 1 | 2.856 | 184 | 64.4258
15.1 | 13.0331 | 1 | 2.856 | 184 | 64.4258
14.4 | 12.6964 | 1 | 2.856 | 184 | 64.4258
14.2 | 12.5043 | 1 | 2.856 | 184 | 64.4258
13.4 | 12.0102 | 1 | 2.856 | 184 | 64.4258
12.5 | 11.5235 | 1 | 2.856 | 184 | 64.4258
12.3 | 11.0551 | 1 | 2.856 | 184 | 64.4258
13.1 | 11.4487 | 1 | 2.856 | 184 | 64.4258
14.2 | 12.2848 | 1 | 2.856 | 184 | 64.4258
15.2 | 13.073 | 1 | 2.856 | 184 | 64.4258
16.9 | 13.6896 | 1 | 2.856 | 184 | 64.4258
18.6 | 14.2413 | 1 | 2.856 | 184 | 64.4258
20.4 | 15.1275 | 1 | 2.856 | 184 | 64.4258
21.5 | 15.0337 | 1 | 2.856 | 184 | 64.4258
21.3 | 14.7646 | 1 | 2.856 | 184 | 64.4258
22.3 | 15.976 | 1 | 2.856 | 184 | 64.4258
22.7 | 16.3736 | 1 | 2.856 | 184 | 64.4258
22.8 | 16.7759 | 1 | 2.856 | 184 | 64.4258
22.1 | 16.5302 | 1 | 2.856 | 184 | 64.4258
21.2 | 16.3745 | 1 | 2.856 | 184 | 64.4258
20.2 | 15.9621 | 1 | 2.856 | 184 | 64.4258
19.4 | 16.0702 | 1 | 2.856 | 184 | 64.4258
17.8 | 15.1424 | 1 | 2.856 | 184 | 64.4258
16.4 | 14.3298 | 1 | 2.856 | 184 | 64.4258
15.6 | 13.4543 | 1 | 2.856 | 184 | 64.4258
14.5 | 12.9049 | 1 | 2.856 | 184 | 64.4258
14.3 | 12.7683 | 1 | 2.856 | 184 | 64.4258
14.2 | 12.7842 | 1 | 2.856 | 184 | 64.4258
14.4 | 12.9205 | 1 | 2.856 | 184 | 64.4258
14.4 | 13.0908 | 1 | 2.856 | 184 | 64.4258
14.2 | 13.0114 | 1 | 2.856 | 184 | 64.4258
14 | 12.5908 | 1 | 2.856 | 184 | 64.4258
14.3 | 12.7683 | 1 | 2.856 | 184 | 64.4258
14.9 | 13.0651 | 1 | 2.856 | 184 | 64.4258
16.2 | 13.6356 | 1 | 2.856 | 184 | 64.4258
17.7 | 14.4347 | 1 | 2.856 | 184 | 64.4258
19.2 | 15.5464 | 1 | 2.856 | 184 | 64.4258
19.7 | 15.9522 | 1 | 2.856 | 184 | 64.4258
19.7 | 15.9535 | 1 | 2.856 | 184 | 64.4258
20.8 | 16.5149 | 1 | 2.856 | 184 | 64.4258
19.8 | 16.3304 | 1 | 2.856 | 184 | 64.4258
19.8 | 16.3879 | 1 | 2.856 | 184 | 64.4258
20.5 | 16.8643 | 1 | 2.856 | 184 | 64.4258
20.2 | 16.8177 | 1 | 2.856 | 184 | 64.4258
19.6 | 16.4899 | 1 | 2.856 | 184 | 64.4258
19 | 16.2779 | 1 | 2.856 | 184 | 64.4258
18.3 | 15.9087 | 1 | 2.856 | 184 | 64.4258
17.4 | 15.2858 | 1 | 2.856 | 184 | 64.4258
16.9 | 15.0414 | 1 | 2.856 | 184 | 64.4258
16.7 | 14.8493 | 1 | 2.856 | 184 | 64.4258
16.8 | 15.0041 | 1 | 2.856 | 184 | 64.4258
16.2 | 14.8381 | 1 | 2.856 | 184 | 64.4258
15.8 | 14.5682 | 1 | 2.856 | 184 | 64.4258
15.7 | 14.4709 | 1 | 2.856 | 184 | 64.4258
15.7 | 14.4709 | 1 | 2.856 | 184 | 64.4258
15.9 | 14.6656 | 1 | 2.856 | 184 | 64.4258
16.4 | 14.9131 | 1 | 2.856 | 184 | 64.4258
17.1 | 15.2329 | 1 | 2.856 | 184 | 64.4258
18.4 | 15.8265 | 1 | 2.856 | 184 | 64.4258
19 | 16.2181 | 1 | 2.856 | 184 | 64.4258
20.6 | 16.6693 | 1 | 2.856 | 184 | 64.4258
21.1 | 16.7878 | 1 | 2.856 | 184 | 64.4258
22.8 | 17.4872 | 1 | 2.856 | 184 | 64.4258
23.1 | 17.813 | 1 | 2.856 | 184 | 64.4258
23.4 | 18.0265 | 1 | 2.856 | 184 | 64.4258
23.3 | 17.8224 | 1 | 2.856 | 184 | 64.4258
23.5 | 18.1146 | 1 | 2.856 | 184 | 64.4258
22.6 | 17.6991 | 1 | 2.856 | 184 | 64.4258
21.1 | 17.0141 | 1 | 2.856 | 184 | 64.4258
19.3 | 16.1507 | 1 | 2.856 | 184 | 64.4258
17.9 | 15.4109 | 1 | 2.856 | 184 | 64.4258
17.3 | 15.3658 | 1 | 2.856 | 184 | 64.4258
15.9 | 14.6656 | 1 | 2.856 | 184 | 64.4258
15.4 | 14.2379 | 1 | 2.856 | 184 | 64.4258
14.4 | 12.9776 | 1 | 2.856 | 184 | 64.4258
13.3 | 11.9699 | 1 | 2.856 | 184 | 64.4258
12.2 | 11.0134 | 1 | 2.856 | 184 | 64.4258
11.4 | 10.397 | 1 | 2.856 | 184 | 64.4258
12.1 | 10.8624 | 1 | 2.856 | 184 | 64.4258
13.2 | 11.3855 | 1 | 2.856 | 184 | 64.4258
14.6 | 11.972 | 1 | 2.856 | 184 | 64.4258
15.8 | 12.517 | 1 | 2.856 | 184 | 64.4258
17.4 | 13.111 | 1 | 2.856 | 184 | 64.4258
18.7 | 13.1425 | 1 | 2.856 | 184 | 64.4258
19.6 | 13.8303 | 1 | 2.856 | 184 | 64.4258
21 | 14.0445 | 1 | 2.856 | 184 | 64.4258
21 | 14.0445 | 1 | 2.856 | 184 | 64.4258
21.7 | 14.4937 | 1 | 2.856 | 184 | 64.4258
22.2 | 14.4115 | 1 | 2.856 | 184 | 64.4258
22.2 | 14.5917 | 1 | 2.856 | 184 | 64.4258
22 | 14.3772 | 1 | 2.856 | 184 | 64.4258
21.1 | 14.309 | 1 | 2.856 | 184 | 64.4258
19.8 | 13.7132 | 1 | 2.856 | 184 | 64.4258
18.8 | 13.4668 | 1 | 2.856 | 184 | 64.4258
17.7 | 13.3795 | 1 | 2.856 | 184 | 64.4258
17.5 | 13.6086 | 1 | 2.856 | 184 | 64.4258
16.4 | 13.3336 | 1 | 2.856 | 184 | 64.4258
14.9 | 12.7886 | 1 | 2.856 | 184 | 64.4258
14.2 | 12.1764 | 1 | 2.856 | 184 | 64.4258
13.1 | 11.3416 | 1 | 2.856 | 184 | 64.4258
12 | 10.8183 | 1 | 2.856 | 184 | 64.4258
12.6 | 11.075 | 1 | 2.856 | 184 | 64.4258
12.4 | 11.0973 | 1 | 2.856 | 184 | 64.4258
13.1 | 11.448 | 1 | 2.856 | 184 | 64.4258
14.5 | 12.1382 | 1 | 2.856 | 184 | 64.4258
16.1 | 12.8418 | 1 | 2.856 | 184 | 64.4258
18.2 | 13.7246 | 1 | 2.856 | 184 | 64.4258
19.1 | 13.152 | 1 | 2.856 | 184 | 64.4258
20.6 | 12.9128 | 1 | 2.856 | 184 | 64.4258
21.4 | 11.7916 | 1 | 2.856 | 184 | 64.4258
21.7 | 13.1032 | 1 | 2.856 | 184 | 64.4258
23 | 12.8616 | 1 | 2.856 | 184 | 64.4258
23.1 | 13.3048 | 1 | 2.856 | 184 | 64.4258
21.4 | 12.9803 | 1 | 2.856 | 184 | 64.4258
22.2 | 13.4181 | 1 | 2.856 | 184 | 64.4258
21.4 | 13.0173 | 1 | 2.856 | 184 | 64.4258
19.8 | 12.6242 | 1 | 2.856 | 184 | 64.4258
18.5 | 13.1451 | 1 | 2.856 | 184 | 64.4258
16.9 | 12.6506 | 1 | 2.856 | 184 | 64.4258
15.5 | 12.0292 | 1 | 2.856 | 184 | 64.4258
14.1 | 11.4985 | 1 | 2.856 | 184 | 64.4258
13 | 11.085 | 1 | 2.856 | 184 | 64.4258
12.5 | 10.8712 | 1 | 2.856 | 184 | 64.4258
12.1 | 10.6458 | 1 | 2.856 | 184 | 64.4258
12 | 10.7092 | 1 | 2.856 | 184 | 64.4258
11.7 | 10.5795 | 1 | 2.856 | 184 | 64.4258
11.6 | 9.9575 | 1 | 2.856 | 184 | 64.4258
12.6 | 9.8042 | 1 | 2.856 | 184 | 64.4258
13.2 | 9.8357 | 1 | 2.856 | 184 | 64.4258
14.5 | 10.5465 | 1 | 2.856 | 184 | 64.4258
15.5 | 11.0236 | 1 | 2.856 | 184 | 64.4258
15.7 | 11.2028 | 1 | 2.856 | 184 | 64.4258
15.9 | 10.6633 | 1 | 2.856 | 184 | 64.4258
15.9 | 10.2828 | 1 | 2.856 | 184 | 64.4258
16.8 | 10.2759 | 1 | 2.856 | 184 | 64.4258
18.4 | 10.6019 | 1 | 2.856 | 184 | 64.4258
18.4 | 11.0492 | 1 | 2.856 | 184 | 64.4258
18.4 | 10.9727 | 1 | 2.856 | 184 | 64.4258
16.9 | 10.6396 | 1 | 2.856 | 184 | 64.4258
16.9 | 10.7207 | 1 | 2.856 | 184 | 64.4258
16.8 | 10.8866 | 1 | 2.856 | 184 | 64.4258
15.9 | 10.5393 | 1 | 2.856 | 184 | 64.4258
14.3 | 10.0551 | 1 | 2.856 | 184 | 64.4258
13 | 9.7044 | 1 | 2.856 | 184 | 64.4258
12 | 9.301 | 1 | 2.856 | 184 | 64.4258
11.9 | 9.3032 | 1 | 2.856 | 184 | 64.4258
10.6 | 9.003 | 1 | 2.856 | 184 | 64.4258
10 | 8.3795 | 1 | 2.856 | 184 | 64.4258
8.5 | 7.376 | 1 | 2.856 | 184 | 64.4258
8.3 | 6.9903 | 1 | 2.856 | 184 | 64.4258
8.8 | 7.375 | 1 | 2.856 | 184 | 64.4258
11.2 | 8.9802 | 1 | 2.856 | 184 | 64.4258
13.4 | 9.4223 | 1 | 2.856 | 184 | 64.4258
15.5 | 11.3465 | 1 | 2.856 | 184 | 64.4258
18 | 13.4385 | 1 | 2.856 | 184 | 64.4258
20.7 | 14.3812 | 1 | 2.856 | 184 | 64.4258
22.1 | 15.048 | 1 | 2.856 | 184 | 64.4258
23.2 | 14.8533 | 1 | 2.856 | 184 | 64.4258
24.3 | 15.349 | 1 | 2.856 | 184 | 64.4258
24.8 | 16.0251 | 1 | 2.856 | 184 | 64.4258
24.5 | 16.4858 | 1 | 2.856 | 184 | 64.4258
24.7 | 17.0499 | 1 | 2.856 | 184 | 64.4258
24.3 | 17.0632 | 1 | 2.856 | 184 | 64.4258
23.5 | 16.9969 | 1 | 2.856 | 184 | 64.4258
22.4 | 17.2175 | 1 | 2.856 | 184 | 64.4258
21.9 | 17.159 | 1 | 2.856 | 184 | 64.4258
19.8 | 15.9153 | 1 | 2.856 | 184 | 64.4258
19 | 15.7413 | 1 | 2.856 | 184 | 64.4258
17.8 | 14.734 | 1 | 2.856 | 184 | 64.4258
16 | 13.8248 | 1 | 2.856 | 184 | 64.4258
15.4 | 12.7621 | 1 | 2.856 | 184 | 64.4258
14.6 | 12.4932 | 1 | 2.856 | 184 | 64.4258
16 | 13.8248 | 1 | 2.856 | 184 | 64.4258
12.9 | 11.4653 | 1 | 2.856 | 184 | 64.4258
12.2 | 11.2261 | 1 | 2.856 | 184 | 64.4258
12.4 | 11.0912 | 1 | 2.856 | 184 | 64.4258
12.5 | 11.4077 | 1 | 2.856 | 184 | 64.4258
13 | 11.4527 | 1 | 2.856 | 184 | 64.4258
13.7 | 11.7443 | 1 | 2.856 | 184 | 64.4258
14.8 | 12.4096 | 1 | 2.856 | 184 | 64.4258
14.9 | 12.3964 | 1 | 2.856 | 184 | 64.4258
16.6 | 13.6657 | 1 | 2.856 | 184 | 64.4258
17.3 | 13.5619 | 1 | 2.856 | 184 | 64.4258
16.8 | 13.5268 | 1 | 2.856 | 184 | 64.4258
18.4 | 14.5703 | 1 | 2.856 | 184 | 64.4258
18.3 | 13.9467 | 1 | 2.856 | 184 | 64.4258
18.5 | 13.5652 | 1 | 2.856 | 184 | 64.4258
18.3 | 13.1415 | 1 | 2.856 | 184 | 64.4258
17 | 12.7234 | 1 | 2.856 | 184 | 64.4258
16 | 12.7323 | 1 | 2.856 | 184 | 64.4258
15 | 12.3835 | 1 | 2.856 | 184 | 64.4258
14.6 | 12.7119 | 1 | 2.856 | 184 | 64.4258
13.6 | 12.9408 | 1 | 2.856 | 184 | 64.4258
13.5 | 12.6098 | 1 | 2.856 | 184 | 64.4258
12.2 | 10.5231 | 1 | 2.856 | 184 | 64.4258
11.9 | 10.6602 | 1 | 2.856 | 184 | 64.4258
12.2 | 11.0047 | 1 | 2.856 | 184 | 64.4258
12.6 | 11.5037 | 1 | 2.856 | 184 | 64.4258
12.9 | 10.9265 | 1 | 2.856 | 184 | 64.4258
13 | 10.4552 | 1 | 2.856 | 184 | 64.4258
13.3 | 10.5345 | 1 | 2.856 | 184 | 64.4258
13.9 | 10.5959 | 1 | 2.856 | 184 | 64.4258
15.4 | 11.234 | 1 | 2.856 | 184 | 64.4258
15 | 11.4545 | 1 | 2.856 | 184 | 64.4258
15 | 11.6026 | 1 | 2.856 | 184 | 64.4258
17 | 11.6222 | 1 | 2.856 | 184 | 64.4258
17.2 | 11.9334 | 1 | 2.856 | 184 | 64.4258
17.2 | 11.1376 | 1 | 2.856 | 184 | 64.4258
15.1 | 10.9163 | 1 | 2.856 | 184 | 64.4258
15.5 | 10.3219 | 1 | 2.856 | 184 | 64.4258
14.7 | 9.5044 | 1 | 2.856 | 184 | 64.4258
11.7 | 9.5837 | 1 | 2.856 | 184 | 64.4258
12.3 | 9.7505 | 1 | 2.856 | 184 | 64.4258
12.6 | 10.3835 | 1 | 2.856 | 184 | 64.4258
12 | 10.8107 | 1 | 2.856 | 184 | 64.4258
12.3 | 10.778 | 1 | 2.856 | 184 | 64.4258
11.5 | 10.7065 | 1 | 2.856 | 184 | 64.4258
11.1 | 10.2063 | 1 | 2.856 | 184 | 64.4258
10.9 | 9.7976 | 1 | 2.856 | 184 | 64.4258
10.6 | 9.0438 | 1 | 2.856 | 184 | 64.4258
9.6 | 8.2838 | 1 | 2.856 | 184 | 64.4258
9.4 | 7.8461 | 1 | 2.856 | 184 | 64.4258
9.1 | 7.7532 | 1 | 2.856 | 184 | 64.4258
9.9 | 8.2261 | 1 | 2.856 | 184 | 64.4258
10.5 | 8.8479 | 1 | 2.856 | 184 | 64.4258
11.2 | 9.773 | 1 | 2.856 | 184 | 64.4258
12 | 9.9212 | 1 | 2.856 | 184 | 64.4258
12 | 9.7696 | 1 | 2.856 | 184 | 64.4258
11.7 | 10.148 | 1 | 2.856 | 184 | 64.4258
11.8 | 10.3487 | 1 | 2.856 | 184 | 64.4258
11.6 | 10.4755 | 1 | 2.856 | 184 | 64.4258
11.9 | 11.0415 | 1 | 2.856 | 184 | 64.4258
11.4 | 10.7174 | 1 | 2.856 | 184 | 64.4258
11.6 | 10.914 | 1 | 2.856 | 184 | 64.4258
11.3 | 10.5642 | 1 | 2.856 | 184 | 64.4258
10.6 | 9.8236 | 1 | 2.856 | 184 | 64.4258
10.5 | 9.6193 | 1 | 2.856 | 184 | 64.4258
10.3 | 9.0593 | 1 | 2.856 | 184 | 64.4258
9.1 | 8.1009 | 1 | 2.856 | 184 | 64.4258
8.8 | 7.9106 | 1 | 2.856 | 184 | 64.4258
8.7 | 7.7135 | 1 | 2.856 | 184 | 64.4258
8.5 | 7.0367 | 1 | 2.856 | 184 | 64.4258
8 | 6.3293 | 1 | 2.856 | 184 | 64.4258
7.2 | 6.3054 | 1 | 2.856 | 184 | 64.4258
6.9 | 6.014 | 1 | 2.856 | 184 | 64.4258
6 | 5.3239 | 1 | 2.856 | 184 | 64.4258
6.1 | 5.4218 | 1 | 2.856 | 184 | 64.4258
8.1 | 6.9885 | 1 | 2.856 | 184 | 64.4258
9.8 | 7.9004 | 1 | 2.856 | 184 | 64.4258
11.7 | 8.6063 | 1 | 2.856 | 184 | 64.4258
12.8 | 8.5941 | 1 | 2.856 | 184 | 64.4258
13.6 | 9.0876 | 1 | 2.856 | 184 | 64.4258
14.4 | 8.4399 | 1 | 2.856 | 184 | 64.4258
15.5 | 9.4685 | 1 | 2.856 | 184 | 64.4258
16.1 | 9.7349 | 1 | 2.856 | 184 | 64.4258
15.3 | 9.5712 | 1 | 2.856 | 184 | 64.4258
15.5 | 9.6608 | 1 | 2.856 | 184 | 64.4258
16.5 | 10.5858 | 1 | 2.856 | 184 | 64.4258
15.6 | 10.2345 | 1 | 2.856 | 184 | 64.4258
15 | 9.1626 | 1 | 2.856 | 184 | 64.4258
13.9 | 8.8159 | 1 | 2.856 | 184 | 64.4258
12.9 | 9.6102 | 1 | 2.856 | 184 | 64.4258
12.5 | 9.2914 | 1 | 2.856 | 184 | 64.4258
12.6 | 9.6161 | 1 | 2.856 | 184 | 64.4258
12.4 | 10.7767 | 1 | 2.856 | 184 | 64.4258
11.9 | 10.9379 | 1 | 2.856 | 184 | 64.4258
11.4 | 11.0572 | 1 | 2.856 | 184 | 64.4258
11.4 | 11.1706 | 1 | 2.856 | 184 | 64.4258
11.7 | 11.4688 | 1 | 2.856 | 184 | 64.4258
12.1 | 11.7511 | 1 | 2.856 | 184 | 64.4258
12.5 | 12.1477 | 1 | 2.856 | 184 | 64.4258
13.1 | 12.5671 | 1 | 2.856 | 184 | 64.4258
13.5 | 12.9623 | 1 | 2.856 | 184 | 64.4258
14.8 | 13.7104 | 1 | 2.856 | 184 | 64.4258
15.3 | 14.0215 | 1 | 2.856 | 184 | 64.4258
16.4 | 14.6752 | 1 | 2.856 | 184 | 64.4258
16.5 | 14.3084 | 1 | 2.856 | 184 | 64.4258
17.8 | 15.0842 | 1 | 2.856 | 184 | 64.4258
19.3 | 15.6361 | 1 | 2.856 | 184 | 64.4258
19.6 | 16.2555 | 1 | 2.856 | 184 | 64.4258
20.4 | 16.2005 | 1 | 2.856 | 184 | 64.4258
20.9 | 16.6019 | 1 | 2.856 | 184 | 64.4258
21.4 | 16.5551 | 1 | 2.856 | 184 | 64.4258
20.9 | 16.2662 | 1 | 2.856 | 184 | 64.4258
20.4 | 16.0877 | 1 | 2.856 | 184 | 64.4258
18.8 | 15.4522 | 1 | 2.856 | 184 | 64.4258
17.5 | 15.6757 | 1 | 2.856 | 184 | 64.4258
16.1 | 14.7996 | 1 | 2.856 | 184 | 64.4258
15.2 | 13.9834 | 1 | 2.856 | 184 | 64.4258
14.5 | 13.0732 | 1 | 2.856 | 184 | 64.4258
13.5 | 12.1063 | 1 | 2.856 | 184 | 64.4258
13 | 11.7882 | 1 | 2.856 | 184 | 64.4258
13 | 11.8994 | 1 | 2.856 | 184 | 64.4258
12.9 | 11.9139 | 1 | 2.856 | 184 | 64.4258
13 | 12.0115 | 1 | 2.856 | 184 | 64.4258
13.4 | 12.2893 | 1 | 2.856 | 184 | 64.4258
14.1 | 12.9137 | 1 | 2.856 | 184 | 64.4258
14.9 | 12.8427 | 1 | 2.856 | 184 | 64.4258
15.4 | 13.2079 | 1 | 2.856 | 184 | 64.4258
16.4 | 13.7668 | 1 | 2.856 | 184 | 64.4258
17.3 | 14.1698 | 1 | 2.856 | 184 | 64.4258
18.5 | 14.6808 | 1 | 2.856 | 184 | 64.4258
18.8 | 14.6865 | 1 | 2.856 | 184 | 64.4258
19.4 | 14.9649 | 1 | 2.856 | 184 | 64.4258
19.7 | 15.2349 | 1 | 2.856 | 184 | 64.4258
21.1 | 15.695 | 1 | 2.856 | 184 | 64.4258
20.6 | 15.7254 | 1 | 2.856 | 184 | 64.4258
19.6 | 15.3599 | 1 | 2.856 | 184 | 64.4258
19 | 14.975 | 1 | 2.856 | 184 | 64.4258
17 | 13.7274 | 1 | 2.856 | 184 | 64.4258
16.2 | 13.2532 | 1 | 2.856 | 184 | 64.4258
15.3 | 13.2236 | 1 | 2.856 | 184 | 64.4258
13.8 | 12.3963 | 1 | 2.856 | 184 | 64.4258
13 | 12.0119 | 1 | 2.856 | 184 | 64.4258
12.6 | 11.8457 | 1 | 2.856 | 184 | 64.4258
12.8 | 12.042 | 1 | 2.856 | 184 | 64.4258
13.1 | 12.1092 | 1 | 2.856 | 184 | 64.4258
13.2 | 12.2068 | 1 | 2.856 | 184 | 64.4258
13.4 | 11.8447 | 1 | 2.856 | 184 | 64.4258
13.4 | 11.8447 | 1 | 2.856 | 184 | 64.4258
12.7 | 11.9441 | 1 | 2.856 | 184 | 64.4258
13.1 | 12.3369 | 1 | 2.856 | 184 | 64.4258
13.9 | 12.2714 | 1 | 2.856 | 184 | 64.4258
14.2 | 12.4498 | 1 | 2.856 | 184 | 64.4258
15.4 | 11.9448 | 1 | 2.856 | 184 | 64.4258
12.6 | 9.8561 | 1 | 2.856 | 184 | 64.4258
14.2 | 11.2404 | 1 | 2.856 | 184 | 64.4258
16.4 | 10.7116 | 1 | 2.856 | 184 | 64.4258
16.6 | 11.0101 | 1 | 2.856 | 184 | 64.4258
16.3 | 9.9447 | 1 | 2.856 | 184 | 64.4258
15.7 | 8.8663 | 1 | 2.856 | 184 | 64.4258
15 | 8.9438 | 1 | 2.856 | 184 | 64.4258
13.7 | 8.536 | 1 | 2.856 | 184 | 64.4258
12.9 | 7.5958 | 1 | 2.856 | 184 | 64.4258
11.2 | 7.1167 | 1 | 2.856 | 184 | 64.4258
10.1 | 6.7798 | 1 | 2.856 | 184 | 64.4258
9.2 | 6.3339 | 1 | 2.856 | 184 | 64.4258
7.4 | 5.7263 | 1 | 2.856 | 184 | 64.4258
6.9 | 5.6956 | 1 | 2.856 | 184 | 64.4258
6.3 | 4.9862 | 1 | 2.856 | 184 | 64.4258
6.6 | 5.4972 | 1 | 2.856 | 184 | 64.4258
7 | 5.8834 | 1 | 2.856 | 184 | 64.4258
8.3 | 6.8552 | 1 | 2.856 | 184 | 64.4258
10 | 7.9089 | 1 | 2.856 | 184 | 64.4258
11.5 | 9.1757 | 1 | 2.856 | 184 | 64.4258
12.9 | 10.0462 | 1 | 2.856 | 184 | 64.4258
13.4 | 10.46 | 1 | 2.856 | 184 | 64.4258
13.8 | 10.2083 | 1 | 2.856 | 184 | 64.4258
14 | 10.1586 | 1 | 2.856 | 184 | 64.4258
14.8 | 10.6466 | 1 | 2.856 | 184 | 64.4258
15.2 | 10.5953 | 1 | 2.856 | 184 | 64.4258
15 | 10.506 | 1 | 2.856 | 184 | 64.4258
15 | 10.2876 | 1 | 2.856 | 184 | 64.4258
14.7 | 10.199 | 1 | 2.856 | 184 | 64.4258
14.4 | 10.3349 | 1 | 2.856 | 184 | 64.4258
13.6 | 9.9812 | 1 | 2.856 | 184 | 64.4258
13.7 | 9.889 | 1 | 2.856 | 184 | 64.4258
13.4 | 9.8936 | 1 | 2.856 | 184 | 64.4258
13.5 | 9.9843 | 1 | 2.856 | 184 | 64.4258
13 | 10.0439 | 1 | 2.856 | 184 | 64.4258
12.6 | 9.9623 | 1 | 2.856 | 184 | 64.4258
12.4 | 9.8731 | 1 | 2.856 | 184 | 64.4258
12.1 | 9.7868 | 1 | 2.856 | 184 | 64.4258
12 | 9.9403 | 1 | 2.856 | 184 | 64.4258
11.9 | 9.5019 | 1 | 2.856 | 184 | 64.4258
11.1 | 9.5877 | 1 | 2.856 | 184 | 64.4258
11 | 9.4411 | 1 | 2.856 | 184 | 64.4258
11.5 | 9.4193 | 1 | 2.856 | 184 | 64.4258
12.4 | 9.444 | 1 | 2.856 | 184 | 64.4258
12.7 | 9.3043 | 1 | 2.856 | 184 | 64.4258
13.6 | 9.6665 | 1 | 2.856 | 184 | 64.4258
13.8 | 9.8471 | 1 | 2.856 | 184 | 64.4258
14.7 | 9.9859 | 1 | 2.856 | 184 | 64.4258
15.8 | 10.5566 | 1 | 2.856 | 184 | 64.4258
16.3 | 10.9451 | 1 | 2.856 | 184 | 64.4258
15.6 | 10.6853 | 1 | 2.856 | 184 | 64.4258
16.2 | 10.8589 | 1 | 2.856 | 184 | 64.4258
15.8 | 10.904 | 1 | 2.856 | 184 | 64.4258
15.5 | 10.6857 | 1 | 2.856 | 184 | 64.4258
14.5 | 10.5669 | 1 | 2.856 | 184 | 64.4258
14.1 | 10.3916 | 1 | 2.856 | 184 | 64.4258
13.5 | 10.1267 | 1 | 2.856 | 184 | 64.4258
12.8 | 9.9587 | 1 | 2.856 | 184 | 64.4258
12.2 | 9.1259 | 1 | 2.856 | 184 | 64.4258
11.6 | 8.8497 | 1 | 2.856 | 184 | 64.4258
10.7 | 8.5247 | 1 | 2.856 | 184 | 64.4258
10 | 8.2438 | 1 | 2.856 | 184 | 64.4258
9.5 | 7.9591 | 1 | 2.856 | 184 | 64.4258
8.3 | 7.0938 | 1 | 2.856 | 184 | 64.4258
7.6 | 6.5124 | 1 | 2.856 | 184 | 64.4258
8.4 | 6.7239 | 1 | 2.856 | 184 | 64.4258
10.6 | 8.7169 | 1 | 2.856 | 184 | 64.4258
11.6 | 9.7649 | 1 | 2.856 | 184 | 64.4258
12.1 | 10.0385 | 1 | 2.856 | 184 | 64.4258
14.2 | 10.7185 | 1 | 2.856 | 184 | 64.4258
15.3 | 11.1467 | 1 | 2.856 | 184 | 64.4258
16.2 | 11.7627 | 1 | 2.856 | 184 | 64.4258
16.9 | 12.102 | 1 | 2.856 | 184 | 64.4258
17.8 | 12.6129 | 1 | 2.856 | 184 | 64.4258
18.6 | 12.527 | 1 | 2.856 | 184 | 64.4258
18 | 12.5532 | 1 | 2.856 | 184 | 64.4258
19 | 12.6022 | 1 | 2.856 | 184 | 64.4258
18.1 | 12.1442 | 1 | 2.856 | 184 | 64.4258
18.4 | 12.0947 | 1 | 2.856 | 184 | 64.4258
17.5 | 11.6319 | 1 | 2.856 | 184 | 64.4258
15 | 11.3021 | 1 | 2.856 | 184 | 64.4258
13.1 | 10.4802 | 1 | 2.856 | 184 | 64.4258
12.7 | 10.2065 | 1 | 2.856 | 184 | 64.4258
11.4 | 9.5755 | 1 | 2.856 | 184 | 64.4258
10.3 | 9.0744 | 1 | 2.856 | 184 | 64.4258
10 | 8.9363 | 1 | 2.856 | 184 | 64.4258
10 | 8.9363 | 1 | 2.856 | 184 | 64.4258
8.8 | 8.2746 | 1 | 2.856 | 184 | 64.4258
8.2 | 7.6835 | 1 | 2.856 | 184 | 64.4258
9.2 | 8.4114 | 1 | 2.856 | 184 | 64.4258
10.8 | 9.7131 | 1 | 2.856 | 184 | 64.4258
12.1 | 10.4475 | 1 | 2.856 | 184 | 64.4258
14 | 11.2712 | 1 | 2.856 | 184 | 64.4258
15.8 | 12.2293 | 1 | 2.856 | 184 | 64.4258
18 | 12.8867 | 1 | 2.856 | 184 | 64.4258
18.6 | 13.1736 | 1 | 2.856 | 184 | 64.4258
19.5 | 13.7679 | 1 | 2.856 | 184 | 64.4258
19 | 13.1471 | 1 | 2.856 | 184 | 64.4258
19.7 | 13.5183 | 1 | 2.856 | 184 | 64.4258
20 | 14.0563 | 1 | 2.856 | 184 | 64.4258
19.8 | 13.9785 | 1 | 2.856 | 184 | 64.4258
20 | 14.1522 | 1 | 2.856 | 184 | 64.4258
19.5 | 14.0067 | 1 | 2.856 | 184 | 64.4258
19.7 | 14.0844 | 1 | 2.856 | 184 | 64.4258
18.6 | 13.7535 | 1 | 2.856 | 184 | 64.4258
16.4 | 12.3748 | 1 | 2.856 | 184 | 64.4258
15.5 | 11.7087 | 1 | 2.856 | 184 | 64.4258
15.4 | 11.0528 | 1 | 2.856 | 184 | 64.4258
14.5 | 10.8031 | 1 | 2.856 | 184 | 64.4258
14.2 | 10.72 | 1 | 2.856 | 184 | 64.4258
12.7 | 10.8643 | 1 | 2.856 | 184 | 64.4258
11.7 | 10.27 | 1 | 2.856 | 184 | 64.4258
11.2 | 9.8919 | 1 | 2.856 | 184 | 64.4258
11.4 | 9.9812 | 1 | 2.856 | 184 | 64.4258
12.2 | 10.4383 | 1 | 2.856 | 184 | 64.4258
14.3 | 11.7019 | 1 | 2.856 | 184 | 64.4258
16 | 12.309 | 1 | 2.856 | 184 | 64.4258
17.8 | 13.1399 | 1 | 2.856 | 184 | 64.4258
18.6 | 13.8516 | 1 | 2.856 | 184 | 64.4258
19.5 | 14.0046 | 1 | 2.856 | 184 | 64.4258
20.9 | 14.9824 | 1 | 2.856 | 184 | 64.4258
21.7 | 15.5775 | 1 | 2.856 | 184 | 64.4258
22.5 | 15.4751 | 1 | 2.856 | 184 | 64.4258
23 | 15.4686 | 1 | 2.856 | 184 | 64.4258
23 | 15.4658 | 1 | 2.856 | 184 | 64.4258
23.1 | 16.0823 | 1 | 2.856 | 184 | 64.4258
22.5 | 16.2707 | 1 | 2.856 | 184 | 64.4258
21.8 | 16.2265 | 1 | 2.856 | 184 | 64.4258
20.8 | 15.4964 | 1 | 2.856 | 184 | 64.4258
19.8 | 15.3923 | 1 | 2.856 | 184 | 64.4258
18.4 | 15.147 | 1 | 2.856 | 184 | 64.4258
17.1 | 14.377 | 1 | 2.856 | 184 | 64.4258
16.1 | 13.9343 | 1 | 2.856 | 184 | 64.4258
14.5 | 12.9648 | 1 | 2.856 | 184 | 64.4258
14.1 | 12.803 | 1 | 2.856 | 184 | 64.4258
13.4 | 12.292 | 1 | 2.856 | 184 | 64.4258
12.7 | 11.946 | 1 | 2.856 | 184 | 64.4258
13.2 | 11.9859 | 1 | 2.856 | 184 | 64.4258
14 | 11.9376 | 1 | 2.856 | 184 | 64.4258
16.4 | 12.4624 | 1 | 2.856 | 184 | 64.4258
17.5 | 13.4615 | 1 | 2.856 | 184 | 64.4258
18.5 | 13.9554 | 1 | 2.856 | 184 | 64.4258
19.9 | 14.6956 | 1 | 2.856 | 184 | 64.4258
21.1 | 15.5012 | 1 | 2.856 | 184 | 64.4258
22.3 | 15.2946 | 1 | 2.856 | 184 | 64.4258
23.1 | 15.4473 | 1 | 2.856 | 184 | 64.4258
23.9 | 15.6937 | 1 | 2.856 | 184 | 64.4258
24.1 | 16.4323 | 1 | 2.856 | 184 | 64.4258
23.5 | 15.9743 | 1 | 2.856 | 184 | 64.4258
23.4 | 15.9355 | 1 | 2.856 | 184 | 64.4258
22.5 | 15.3659 | 1 | 2.856 | 184 | 64.4258
20.7 | 14.3098 | 1 | 2.856 | 184 | 64.4258
18.7 | 12.5977 | 1 | 2.856 | 184 | 64.4258
16.5 | 11.4629 | 1 | 2.856 | 184 | 64.4258
15 | 10.7299 | 1 | 2.856 | 184 | 64.4258
13.3 | 9.5728 | 1 | 2.856 | 184 | 64.4258
12.1 | 8.8912 | 1 | 2.856 | 184 | 64.4258
11 | 8.2427 | 1 | 2.856 | 184 | 64.4258
10 | 7.8153 | 1 | 2.856 | 184 | 64.4258
9.3 | 7.4337 | 1 | 2.856 | 184 | 64.4258
8.5 | 6.8591 | 1 | 2.856 | 184 | 64.4258
9.3 | 7.5261 | 1 | 2.856 | 184 | 64.4258
10.5 | 7.9603 | 1 | 2.856 | 184 | 64.4258
12.5 | 9.2073 | 1 | 2.856 | 184 | 64.4258
13.8 | 10.0651 | 1 | 2.856 | 184 | 64.4258
14.9 | 10.5014 | 1 | 2.856 | 184 | 64.4258
16.5 | 11.595 | 1 | 2.856 | 184 | 64.4258
17.8 | 11.9147 | 1 | 2.856 | 184 | 64.4258
19.6 | 12.5238 | 1 | 2.856 | 184 | 64.4258
21 | 13.8182 | 1 | 2.856 | 184 | 64.4258
22 | 14.2017 | 1 | 2.856 | 184 | 64.4258
22.5 | 14.3491 | 1 | 2.856 | 184 | 64.4258
23 | 14.8898 | 1 | 2.856 | 184 | 64.4258
23.1 | 15.4332 | 1 | 2.856 | 184 | 64.4258
22.7 | 15.6685 | 1 | 2.856 | 184 | 64.4258
22.3 | 14.6237 | 1 | 2.856 | 184 | 64.4258
20.8 | 13.9593 | 1 | 2.856 | 184 | 64.4258
19.1 | 13.7751 | 1 | 2.856 | 184 | 64.4258
17.6 | 12.6969 | 1 | 2.856 | 184 | 64.4258
16.4 | 11.9168 | 1 | 2.856 | 184 | 64.4258
15.5 | 11.5411 | 1 | 2.856 | 184 | 64.4258
13.9 | 10.9601 | 1 | 2.856 | 184 | 64.4258
13.1 | 11.2339 | 1 | 2.856 | 184 | 64.4258
12.5 | 10.8719 | 1 | 2.856 | 184 | 64.4258
12.9 | 11.1489 | 1 | 2.856 | 184 | 64.4258
12.7 | 11.1699 | 1 | 2.856 | 184 | 64.4258
13.5 | 11.6146 | 1 | 2.856 | 184 | 64.4258
15 | 12.2896 | 1 | 2.856 | 184 | 64.4258
15.9 | 12.97 | 1 | 2.856 | 184 | 64.4258
18 | 13.7457 | 1 | 2.856 | 184 | 64.4258
19.6 | 14.6161 | 1 | 2.856 | 184 | 64.4258
20.5 | 14.8524 | 1 | 2.856 | 184 | 64.4258
21.6 | 15.5627 | 1 | 2.856 | 184 | 64.4258
22.1 | 15.4916 | 1 | 2.856 | 184 | 64.4258
21.7 | 15.5462 | 1 | 2.856 | 184 | 64.4258
23 | 15.8676 | 1 | 2.856 | 184 | 64.4258
22.9 | 14.6613 | 1 | 2.856 | 184 | 64.4258
23 | 14.6547 | 1 | 2.856 | 184 | 64.4258
22.8 | 14.3175 | 1 | 2.856 | 184 | 64.4258
22.3 | 13.9121 | 1 | 2.856 | 184 | 64.4258
20.9 | 13.9441 | 1 | 2.856 | 184 | 64.4258
19.6 | 13.3913 | 1 | 2.856 | 184 | 64.4258
18.2 | 12.743 | 1 | 2.856 | 184 | 64.4258
16.2 | 13.1428 | 1 | 2.856 | 184 | 64.4258
14.9 | 12.6217 | 1 | 2.856 | 184 | 64.4258
13.9 | 12.0504 | 1 | 2.856 | 184 | 64.4258
13.6 | 11.763 | 1 | 2.856 | 184 | 64.4258
12.8 | 11.5926 | 1 | 2.856 | 184 | 64.4258
11.7 | 10.7961 | 1 | 2.856 | 184 | 64.4258
11.7 | 10.7961 | 1 | 2.856 | 184 | 64.4258
12.7 | 11.6061 | 1 | 2.856 | 184 | 64.4258
14.1 | 12.461 | 1 | 2.856 | 184 | 64.4258
16.4 | 13.4351 | 1 | 2.856 | 184 | 64.4258
17.9 | 14.0716 | 1 | 2.856 | 184 | 64.4258
19.9 | 15.0367 | 1 | 2.856 | 184 | 64.4258
21.2 | 15.1085 | 1 | 2.856 | 184 | 64.4258
22.2 | 15.4762 | 1 | 2.856 | 184 | 64.4258
23.6 | 15.3665 | 1 | 2.856 | 184 | 64.4258
24.6 | 16.6764 | 1 | 2.856 | 184 | 64.4258
24.9 | 16.3444 | 1 | 2.856 | 184 | 64.4258
24 | 15.9766 | 1 | 2.856 | 184 | 64.4258
23.8 | 15.998 | 1 | 2.856 | 184 | 64.4258
23.3 | 15.4837 | 1 | 2.856 | 184 | 64.4258
22 | 15.9532 | 1 | 2.856 | 184 | 64.4258
20.2 | 14.8828 | 1 | 2.856 | 184 | 64.4258
18.7 | 13.7045 | 1 | 2.856 | 184 | 64.4258
17.6 | 13.0233 | 1 | 2.856 | 184 | 64.4258
16.7 | 12.5614 | 1 | 2.856 | 184 | 64.4258
15.7 | 12.2068 | 1 | 2.856 | 184 | 64.4258
14.9 | 12.0314 | 1 | 2.856 | 184 | 64.4258
14.3 | 11.8888 | 1 | 2.856 | 184 | 64.4258
13 | 11.2393 | 1 | 2.856 | 184 | 64.4258
12.5 | 11.1896 | 1 | 2.856 | 184 | 64.4258
12.5 | 11.1896 | 1 | 2.856 | 184 | 64.4258
13.4 | 11.3021 | 1 | 2.856 | 184 | 64.4258
14.7 | 11.949 | 1 | 2.856 | 184 | 64.4258
14.8 | 12.0435 | 1 | 2.856 | 184 | 64.4258
16.8 | 12.8533 | 1 | 2.856 | 184 | 64.4258
18.1 | 13.5191 | 1 | 2.856 | 184 | 64.4258
19 | 13.524 | 1 | 2.856 | 184 | 64.4258
19 | 13.524 | 1 | 2.856 | 184 | 64.4258
20.8 | 14.5062 | 1 | 2.856 | 184 | 64.4258
21.4 | 14.9749 | 1 | 2.856 | 184 | 64.4258
21.8 | 15.2705 | 1 | 2.856 | 184 | 64.4258
22.7 | 15.648 | 1 | 2.856 | 184 | 64.4258
21.8 | 15.6221 | 1 | 2.856 | 184 | 64.4258
20.8 | 15.2551 | 1 | 2.856 | 184 | 64.4258
21.1 | 15.0101 | 1 | 2.856 | 184 | 64.4258
18.6 | 14.3313 | 1 | 2.856 | 184 | 64.4258
17 | 13.7185 | 1 | 2.856 | 184 | 64.4258
15.5 | 12.8581 | 1 | 2.856 | 184 | 64.4258
14 | 12.1421 | 1 | 2.856 | 184 | 64.4258
13.5 | 11.8816 | 1 | 2.856 | 184 | 64.4258
13.9 | 12.1559 | 1 | 2.856 | 184 | 64.4258
13.4 | 11.731 | 1 | 2.856 | 184 | 64.4258
12.9 | 11.4677 | 1 | 2.856 | 184 | 64.4258
12.7 | 11.3837 | 1 | 2.856 | 184 | 64.4258
13.6 | 11.8684 | 1 | 2.856 | 184 | 64.4258
14.6 | 12.2793 | 1 | 2.856 | 184 | 64.4258
15.1 | 12.3776 | 1 | 2.856 | 184 | 64.4258
16.4 | 13.1112 | 1 | 2.856 | 184 | 64.4258
17 | 13.5062 | 1 | 2.856 | 184 | 64.4258
18.2 | 14.0766 | 1 | 2.856 | 184 | 64.4258
17.1 | 13.7063 | 1 | 2.856 | 184 | 64.4258
17.1 | 13.5997 | 1 | 2.856 | 184 | 64.4258
19.3 | 14.7585 | 1 | 2.856 | 184 | 64.4258
19.7 | 14.908 | 1 | 2.856 | 184 | 64.4258
20.3 | 15.0807 | 1 | 2.856 | 184 | 64.4258
20.3 | 15.1848 | 1 | 2.856 | 184 | 64.4258
20 | 14.9173 | 1 | 2.856 | 184 | 64.4258
19.3 | 14.7602 | 1 | 2.856 | 184 | 64.4258
18.5 | 14.2471 | 1 | 2.856 | 184 | 64.4258
17.5 | 13.7057 | 1 | 2.856 | 184 | 64.4258
16.9 | 13.6309 | 1 | 2.856 | 184 | 64.4258
16.3 | 13.5588 | 1 | 2.856 | 184 | 64.4258
16.1 | 13.264 | 1 | 2.856 | 184 | 64.4258
15.8 | 12.9835 | 1 | 2.856 | 184 | 64.4258
15.5 | 12.5447 | 1 | 2.856 | 184 | 64.4258
15 | 12.2885 | 1 | 2.856 | 184 | 64.4258
14.1 | 12.3511 | 1 | 2.856 | 184 | 64.4258
13.6 | 12.2018 | 1 | 2.856 | 184 | 64.4258
13.7 | 12.2985 | 1 | 2.856 | 184 | 64.4258
14.2 | 12.0126 | 1 | 2.856 | 184 | 64.4258
15.2 | 12.4756 | 1 | 2.856 | 184 | 64.4258
16 | 12.5914 | 1 | 2.856 | 184 | 64.4258
16.2 | 12.0228 | 1 | 2.856 | 184 | 64.4258
16.3 | 12.1616 | 1 | 2.856 | 184 | 64.4258
16.9 | 12.7519 | 1 | 2.856 | 184 | 64.4258
16.8 | 12.7618 | 1 | 2.856 | 184 | 64.4258
17.7 | 13.1716 | 1 | 2.856 | 184 | 64.4258
17.7 | 12.9249 | 1 | 2.856 | 184 | 64.4258
17.9 | 13.1026 | 1 | 2.856 | 184 | 64.4258
18.2 | 13.8234 | 1 | 2.856 | 184 | 64.4258
17.4 | 13.7208 | 1 | 2.856 | 184 | 64.4258
18 | 13.9535 | 1 | 2.856 | 184 | 64.4258
17.7 | 14.1029 | 1 | 2.856 | 184 | 64.4258
17 | 13.5117 | 1 | 2.856 | 184 | 64.4258
16.3 | 13.5599 | 1 | 2.856 | 184 | 64.4258
15.5 | 13.4124 | 1 | 2.856 | 184 | 64.4258
14.9 | 13.1745 | 1 | 2.856 | 184 | 64.4258
14.1 | 12.6852 | 1 | 2.856 | 184 | 64.4258
13.7 | 12.4104 | 1 | 2.856 | 184 | 64.4258
14.1 | 12.4616 | 1 | 2.856 | 184 | 64.4258
14.4 | 13.0893 | 1 | 2.856 | 184 | 64.4258
14.9 | 12.9507 | 1 | 2.856 | 184 | 64.4258
15 | 12.8254 | 1 | 2.856 | 184 | 64.4258
14.5 | 13.3014 | 1 | 2.856 | 184 | 64.4258
14.6 | 13.7499 | 1 | 2.856 | 184 | 64.4258
15.2 | 13.8649 | 1 | 2.856 | 184 | 64.4258
16 | 14.2888 | 1 | 2.856 | 184 | 64.4258
15.7 | 13.6577 | 1 | 2.856 | 184 | 64.4258
16.6 | 13.8945 | 1 | 2.856 | 184 | 64.4258
17.2 | 14.2911 | 1 | 2.856 | 184 | 64.4258
17.2 | 14.684 | 1 | 2.856 | 184 | 64.4258
16.6 | 14.8653 | 1 | 2.856 | 184 | 64.4258
16.9 | 14.86 | 1 | 2.856 | 184 | 64.4258
16.1 | 15.0381 | 1 | 2.856 | 184 | 64.4258
16.6 | 14.9836 | 1 | 2.856 | 184 | 64.4258
16.8 | 15.0579 | 1 | 2.856 | 184 | 64.4258
16.6 | 15.1634 | 1 | 2.856 | 184 | 64.4258
16.8 | 15.1774 | 1 | 2.856 | 184 | 64.4258
16.8 | 15.1774 | 1 | 2.856 | 184 | 64.4258
16.4 | 14.9694 | 1 | 2.856 | 184 | 64.4258
16.2 | 14.7755 | 1 | 2.856 | 184 | 64.4258
16.2 | 14.7755 | 1 | 2.856 | 184 | 64.4258
16 | 14.8206 | 1 | 2.856 | 184 | 64.4258
16.1 | 14.679 | 1 | 2.856 | 184 | 64.4258
16.1 | 14.1538 | 1 | 2.856 | 184 | 64.4258
15.6 | 13.2294 | 1 | 2.856 | 184 | 64.4258
15.6 | 12.429 | 1 | 2.856 | 184 | 64.4258
16.1 | 12.8405 | 1 | 2.856 | 184 | 64.4258
16.7 | 13.082 | 1 | 2.856 | 184 | 64.4258
17 | 13.3048 | 1 | 2.856 | 184 | 64.4258
18 | 13.5465 | 1 | 2.856 | 184 | 64.4258
19.1 | 13.7792 | 1 | 2.856 | 184 | 64.4258
19.4 | 13.1862 | 1 | 2.856 | 184 | 64.4258
20.3 | 13.2329 | 1 | 2.856 | 184 | 64.4258
21.3 | 13.4985 | 1 | 2.856 | 184 | 64.4258
21.4 | 13.5805 | 1 | 2.856 | 184 | 64.4258
21 | 13.3832 | 1 | 2.856 | 184 | 64.4258
21.4 | 13.5836 | 1 | 2.856 | 184 | 64.4258
20.5 | 13.2281 | 1 | 2.856 | 184 | 64.4258
20.2 | 13.3729 | 1 | 2.856 | 184 | 64.4258
19.6 | 13.3188 | 1 | 2.856 | 184 | 64.4258
18.3 | 12.989 | 1 | 2.856 | 184 | 64.4258
17 | 12.6591 | 1 | 2.856 | 184 | 64.4258
15.9 | 12.309 | 1 | 2.856 | 184 | 64.4258
13.5 | 11.3057 | 1 | 2.856 | 184 | 64.4258
12.9 | 10.945 | 1 | 2.856 | 184 | 64.4258
12.2 | 10.9077 | 1 | 2.856 | 184 | 64.4258
11.8 | 10.681 | 1 | 2.856 | 184 | 64.4258
10.9 | 10.1254 | 1 | 2.856 | 184 | 64.4258
10.5 | 9.9482 | 1 | 2.856 | 184 | 64.4258
10.6 | 9.9388 | 1 | 2.856 | 184 | 64.4258
12.2 | 10.9082 | 1 | 2.856 | 184 | 64.4258
15.3 | 12.0121 | 1 | 2.856 | 184 | 64.4258
17 | 12.3224 | 1 | 2.856 | 184 | 64.4258
18.2 | 12.672 | 1 | 2.856 | 184 | 64.4258
19.7 | 13.4092 | 1 | 2.856 | 184 | 64.4258
20.3 | 13.0278 | 1 | 2.856 | 184 | 64.4258
22 | 13.9955 | 1 | 2.856 | 184 | 64.4258
22.5 | 13.6074 | 1 | 2.856 | 184 | 64.4258
23.1 | 14.3305 | 1 | 2.856 | 184 | 64.4258
23.8 | 14.2655 | 1 | 2.856 | 184 | 64.4258
23.2 | 14.9737 | 1 | 2.856 | 184 | 64.4258
23 | 14.8958 | 1 | 2.856 | 184 | 64.4258
22.4 | 14.1374 | 1 | 2.856 | 184 | 64.4258
21.4 | 13.9261 | 1 | 2.856 | 184 | 64.4258
19 | 13.7894 | 1 | 2.856 | 184 | 64.4258
17.4 | 12.8119 | 1 | 2.856 | 184 | 64.4258
16.3 | 11.5971 | 1 | 2.856 | 184 | 64.4258
15.6 | 11.3469 | 1 | 2.856 | 184 | 64.4258
15.6 | 11.2048 | 1 | 2.856 | 184 | 64.4258
15.3 | 11.3607 | 1 | 2.856 | 184 | 64.4258
14.9 | 11.3841 | 1 | 2.856 | 184 | 64.4258
15 | 11.6225 | 1 | 2.856 | 184 | 64.4258
14.8 | 11.739 | 1 | 2.856 | 184 | 64.4258
14.7 | 11.9547 | 1 | 2.856 | 184 | 64.4258
15.9 | 12.3944 | 1 | 2.856 | 184 | 64.4258
17.7 | 13.2162 | 1 | 2.856 | 184 | 64.4258
18.9 | 13.8859 | 1 | 2.856 | 184 | 64.4258
22 | 15.598 | 1 | 2.856 | 184 | 64.4258
24.9 | 16.7754 | 1 | 2.856 | 184 | 64.4258
26.5 | 17.323 | 1 | 2.856 | 184 | 64.4258
27.6 | 18.7843 | 1 | 2.856 | 184 | 64.4258
28.1 | 19.3074 | 1 | 2.856 | 184 | 64.4258
29.1 | 19.6738 | 1 | 2.856 | 184 | 64.4258
28.8 | 20.0048 | 1 | 2.856 | 184 | 64.4258
29.2 | 20.3971 | 1 | 2.856 | 184 | 64.4258
28.6 | 20.6615 | 1 | 2.856 | 184 | 64.4258
28.1 | 20.1713 | 1 | 2.856 | 184 | 64.4258
22 | 18.1214 | 1 | 2.856 | 184 | 64.4258
19.3 | 17.59 | 1 | 2.856 | 184 | 64.4258
19.5 | 17.0998 | 1 | 2.856 | 184 | 64.4258
18 | 17.3423 | 1 | 2.856 | 184 | 64.4258
18 | 17.342 | 1 | 2.856 | 184 | 64.4258
17.9 | 17.373 | 1 | 2.856 | 184 | 64.4258
17.1 | 16.7742 | 1 | 2.856 | 184 | 64.4258
17 | 16.5462 | 1 | 2.856 | 184 | 64.4258
16.2 | 15.7536 | 1 | 2.856 | 184 | 64.4258
16 | 15.368 | 1 | 2.856 | 184 | 64.4258
15.9 | 15.2693 | 1 | 2.856 | 184 | 64.4258
15.9 | 15.4563 | 1 | 2.856 | 184 | 64.4258
16.2 | 15.4413 | 1 | 2.856 | 184 | 64.4258
15.9 | 14.9015 | 1 | 2.856 | 184 | 64.4258
16.3 | 14.9896 | 1 | 2.856 | 184 | 64.4258
16.4 | 15.0874 | 1 | 2.856 | 184 | 64.4258
18.1 | 15.7089 | 1 | 2.856 | 184 | 64.4258
20.2 | 17.042 | 1 | 2.856 | 184 | 64.4258
20.6 | 16.3715 | 1 | 2.856 | 184 | 64.4258
21 | 16.6812 | 1 | 2.856 | 184 | 64.4258
21.4 | 16.5431 | 1 | 2.856 | 184 | 64.4258
21.5 | 16.6335 | 1 | 2.856 | 184 | 64.4258
21.8 | 16.7382 | 1 | 2.856 | 184 | 64.4258
21.2 | 16.4176 | 1 | 2.856 | 184 | 64.4258
20.8 | 16.1673 | 1 | 2.856 | 184 | 64.4258
19.1 | 15.6118 | 1 | 2.856 | 184 | 64.4258
18.2 | 14.8325 | 1 | 2.856 | 184 | 64.4258
17.1 | 14.5884 | 1 | 2.856 | 184 | 64.4258
16.1 | 14.3838 | 1 | 2.856 | 184 | 64.4258
14.9 | 13.8063 | 1 | 2.856 | 184 | 64.4258
13.9 | 12.8883 | 1 | 2.856 | 184 | 64.4258
13.5 | 12.7278 | 1 | 2.856 | 184 | 64.4258
14 | 12.9287 | 1 | 2.856 | 184 | 64.4258
13.2 | 12.3189 | 1 | 2.856 | 184 | 64.4258
12.3 | 11.6628 | 1 | 2.856 | 184 | 64.4258
13.8 | 12.6201 | 1 | 2.856 | 184 | 64.4258
15.3 | 13.332 | 1 | 2.856 | 184 | 64.4258
16.9 | 13.6309 | 1 | 2.856 | 184 | 64.4258
17.8 | 14.195 | 1 | 2.856 | 184 | 64.4258
17.3 | 13.5766 | 1 | 2.856 | 184 | 64.4258
17.9 | 13.6553 | 1 | 2.856 | 184 | 64.4258
17.7 | 13.5771 | 1 | 2.856 | 184 | 64.4258
18.1 | 13.5317 | 1 | 2.856 | 184 | 64.4258
19 | 13.7813 | 1 | 2.856 | 184 | 64.4258
19.4 | 13.9855 | 1 | 2.856 | 184 | 64.4258
20.6 | 14.9402 | 1 | 2.856 | 184 | 64.4258
20.4 | 14.8655 | 1 | 2.856 | 184 | 64.4258
18.5 | 14.1476 | 1 | 2.856 | 184 | 64.4258
17.7 | 13.8916 | 1 | 2.856 | 184 | 64.4258
17.1 | 13.9281 | 1 | 2.856 | 184 | 64.4258
16 | 13.3895 | 1 | 2.856 | 184 | 64.4258
15.3 | 13.3343 | 1 | 2.856 | 184 | 64.4258
14.9 | 12.9531 | 1 | 2.856 | 184 | 64.4258
14.9 | 12.9531 | 1 | 2.856 | 184 | 64.4258
14.8 | 12.8576 | 1 | 2.856 | 184 | 64.4258
14.5 | 12.4076 | 1 | 2.856 | 184 | 64.4258
13.9 | 12.2714 | 1 | 2.856 | 184 | 64.4258
13.4 | 11.9556 | 1 | 2.856 | 184 | 64.4258
13.8 | 12.2862 | 1 | 2.856 | 184 | 64.4258
14.5 | 12.8495 | 1 | 2.856 | 184 | 64.4258
15.2 | 13.2411 | 1 | 2.856 | 184 | 64.4258
16.5 | 14.1982 | 1 | 2.856 | 184 | 64.4258
18.5 | 15.1223 | 1 | 2.856 | 184 | 64.4258
20.3 | 16.2812 | 1 | 2.856 | 184 | 64.4258
21.9 | 17.068 | 1 | 2.856 | 184 | 64.4258
23.9 | 17.9721 | 1 | 2.856 | 184 | 64.4258
24 | 18.1723 | 1 | 2.856 | 184 | 64.4258
24.5 | 18.2827 | 1 | 2.856 | 184 | 64.4258
25.3 | 18.6564 | 1 | 2.856 | 184 | 64.4258
25.4 | 18.634 | 1 | 2.856 | 184 | 64.4258
24.8 | 18.2699 | 1 | 2.856 | 184 | 64.4258
24.3 | 18.1589 | 1 | 2.856 | 184 | 64.4258
22.9 | 16.657 | 1 | 2.856 | 184 | 64.4258
21.4 | 15.4497 | 1 | 2.856 | 184 | 64.4258
19.5 | 15.2735 | 1 | 2.856 | 184 | 64.4258
18.3 | 14.8263 | 1 | 2.856 | 184 | 64.4258
16.9 | 14.4078 | 1 | 2.856 | 184 | 64.4258
15.9 | 13.9668 | 1 | 2.856 | 184 | 64.4258
15.2 | 13.0197 | 1 | 2.856 | 184 | 64.4258
14.6 | 12.5043 | 1 | 2.856 | 184 | 64.4258
14 | 12.4797 | 1 | 2.856 | 184 | 64.4258
14 | 12.479 | 1 | 2.856 | 184 | 64.4258
13.9 | 12.8338 | 1 | 2.856 | 184 | 64.4258
15.4 | 13.3197 | 1 | 2.856 | 184 | 64.4258
17.5 | 13.9244 | 1 | 2.856 | 184 | 64.4258
19.9 | 12.4698 | 1 | 2.856 | 184 | 64.4258
22.1 | 14.7347 | 1 | 2.856 | 184 | 64.4258
24.1 | 15.9824 | 1 | 2.856 | 184 | 64.4258
26 | 17.2736 | 1 | 2.856 | 184 | 64.4258
26.8 | 18.3427 | 1 | 2.856 | 184 | 64.4258
27.2 | 17.8237 | 1 | 2.856 | 184 | 64.4258
27.9 | 18.1028 | 1 | 2.856 | 184 | 64.4258
27.4 | 18.1323 | 1 | 2.856 | 184 | 64.4258
27.3 | 18.1457 | 1 | 2.856 | 184 | 64.4258
26.9 | 17.8638 | 1 | 2.856 | 184 | 64.4258
25.8 | 17.2912 | 1 | 2.856 | 184 | 64.4258
24.6 | 16.8278 | 1 | 2.856 | 184 | 64.4258
23.5 | 16.8011 | 1 | 2.856 | 184 | 64.4258
22.1 | 16.7933 | 1 | 2.856 | 184 | 64.4258
21.7 | 16.2737 | 1 | 2.856 | 184 | 64.4258
20.7 | 16.0252 | 1 | 2.856 | 184 | 64.4258
19.8 | 14.8948 | 1 | 2.856 | 184 | 64.4258
19.6 | 14.6105 | 1 | 2.856 | 184 | 64.4258
18.2 | 15.8075 | 1 | 2.856 | 184 | 64.4258
17.2 | 15.0308 | 1 | 2.856 | 184 | 64.4258
16.1 | 14.4434 | 1 | 2.856 | 184 | 64.4258
16.2 | 13.7961 | 1 | 2.856 | 184 | 64.4258
15.8 | 12.5117 | 1 | 2.856 | 184 | 64.4258
15.9 | 11.9493 | 1 | 2.856 | 184 | 64.4258
16.6 | 12.143 | 1 | 2.856 | 184 | 64.4258
17.4 | 12.282 | 1 | 2.856 | 184 | 64.4258
18.1 | 12.2062 | 1 | 2.856 | 184 | 64.4258
19.5 | 12.9552 | 1 | 2.856 | 184 | 64.4258
21.4 | 14.0152 | 1 | 2.856 | 184 | 64.4258
20.6 | 13.3082 | 1 | 2.856 | 184 | 64.4258
21.5 | 13.3669 | 1 | 2.856 | 184 | 64.4258
21.1 | 12.8399 | 1 | 2.856 | 184 | 64.4258
21 | 12.8399 | 1 | 2.856 | 184 | 64.4258
20.7 | 12.6415 | 1 | 2.856 | 184 | 64.4258
20.1 | 12.3567 | 1 | 2.856 | 184 | 64.4258
19 | 12.029 | 1 | 2.856 | 184 | 64.4258
18 | 11.5697 | 1 | 2.856 | 184 | 64.4258
16.5 | 11.4587 | 1 | 2.856 | 184 | 64.4258
15.1 | 11.0488 | 1 | 2.856 | 184 | 64.4258
13.4 | 10.1221 | 1 | 2.856 | 184 | 64.4258
12.3 | 9.6798 | 1 | 2.856 | 184 | 64.4258
12.9 | 10.1404 | 1 | 2.856 | 184 | 64.4258
12.2 | 9.8786 | 1 | 2.856 | 184 | 64.4258
11.5 | 9.7658 | 1 | 2.856 | 184 | 64.4258
10.8 | 9.3491 | 1 | 2.856 | 184 | 64.4258
11.4 | 9.8742 | 1 | 2.856 | 184 | 64.4258
13.1 | 10.5729 | 1 | 2.856 | 184 | 64.4258
15.5 | 11.6977 | 1 | 2.856 | 184 | 64.4258
17.5 | 12.478 | 1 | 2.856 | 184 | 64.4258
18.5 | 12.9772 | 1 | 2.856 | 184 | 64.4258
19.3 | 12.9772 | 1 | 2.856 | 184 | 64.4258
20.6 | 13.4507 | 1 | 2.856 | 184 | 64.4258
22.1 | 14.5199 | 1 | 2.856 | 184 | 64.4258
23.5 | 15.1814 | 1 | 2.856 | 184 | 64.4258
22.7 | 14.9253 | 1 | 2.856 | 184 | 64.4258
23.1 | 14.7615 | 1 | 2.856 | 184 | 64.4258
23.4 | 15.505 | 1 | 2.856 | 184 | 64.4258
22.6 | 15.3523 | 1 | 2.856 | 184 | 64.4258
21 | 14.6105 | 1 | 2.856 | 184 | 64.4258
20.5 | 14.2283 | 1 | 2.856 | 184 | 64.4258
18.8 | 13.1352 | 1 | 2.856 | 184 | 64.4258
17 | 13.2043 | 1 | 2.856 | 184 | 64.4258
16.3 | 13.0792 | 1 | 2.856 | 184 | 64.4258
14.4 | 12.3108 | 1 | 2.856 | 184 | 64.4258
14.3 | 12.2682 | 1 | 2.856 | 184 | 64.4258
13.8 | 12.1169 | 1 | 2.856 | 184 | 64.4258
13.6 | 12.034 | 1 | 2.856 | 184 | 64.4258
13.3 | 11.7446 | 1 | 2.856 | 184 | 64.4258
12.4 | 11.6471 | 1 | 2.856 | 184 | 64.4258
13.1 | 12.2199 | 1 | 2.856 | 184 | 64.4258
14.6 | 13.1659 | 1 | 2.856 | 184 | 64.4258
15.9 | 13.9601 | 1 | 2.856 | 184 | 64.4258
17.9 | 14.5541 | 1 | 2.856 | 184 | 64.4258
19.4 | 14.9533 | 1 | 2.856 | 184 | 64.4258
19.3 | 14.6534 | 1 | 2.856 | 184 | 64.4258
20.2 | 14.8868 | 1 | 2.856 | 184 | 64.4258
20.3 | 14.7712 | 1 | 2.856 | 184 | 64.4258
20.5 | 14.9474 | 1 | 2.856 | 184 | 64.4258
20.4 | 15.5367 | 1 | 2.856 | 184 | 64.4258
19.9 | 15.5724 | 1 | 2.856 | 184 | 64.4258
18.5 | 16.2121 | 1 | 2.856 | 184 | 64.4258
17.8 | 16.2049 | 1 | 2.856 | 184 | 64.4258
17.7 | 15.7455 | 1 | 2.856 | 184 | 64.4258
17.8 | 15.7221 | 1 | 2.856 | 184 | 64.4258
17.6 | 15.6495 | 1 | 2.856 | 184 | 64.4258
17.4 | 15.5774 | 1 | 2.856 | 184 | 64.4258
16.9 | 15.9449 | 1 | 2.856 | 184 | 64.4258
16.5 | 15.8631 | 1 | 2.856 | 184 | 64.4258
16.6 | 15.9619 | 1 | 2.856 | 184 | 64.4258
16.6 | 16.1511 | 1 | 2.856 | 184 | 64.4258
16.6 | 16.2784 | 1 | 2.856 | 184 | 64.4258
16.7 | 16.1869 | 1 | 2.856 | 184 | 64.4258
16.7 | 16.0608 | 1 | 2.856 | 184 | 64.4258
16.4 | 16.0797 | 1 | 2.856 | 184 | 64.4258
16.8 | 16.0342 | 1 | 2.856 | 184 | 64.4258
17.6 | 16.382 | 1 | 2.856 | 184 | 64.4258
18.5 | 16.3344 | 1 | 2.856 | 184 | 64.4258
20.1 | 16.6626 | 1 | 2.856 | 184 | 64.4258
19.8 | 16.1538 | 1 | 2.856 | 184 | 64.4258
20.2 | 15.9605 | 1 | 2.856 | 184 | 64.4258
20.6 | 16.382 | 1 | 2.856 | 184 | 64.4258
21.6 | 16.9574 | 1 | 2.856 | 184 | 64.4258
20.8 | 16.9071 | 1 | 2.856 | 184 | 64.4258
21.1 | 17.2424 | 1 | 2.856 | 184 | 64.4258
20.7 | 16.9301 | 1 | 2.856 | 184 | 64.4258
19.6 | 16.2543 | 1 | 2.856 | 184 | 64.4258
19.5 | 16.3929 | 1 | 2.856 | 184 | 64.4258
19 | 16.274 | 1 | 2.856 | 184 | 64.4258
18 | 15.387 | 1 | 2.856 | 184 | 64.4258
17 | 14.7269 | 1 | 2.856 | 184 | 64.4258
16.2 | 14.4827 | 1 | 2.856 | 184 | 64.4258
15.2 | 13.6921 | 1 | 2.856 | 184 | 64.4258
14.4 | 13.0898 | 1 | 2.856 | 184 | 64.4258
13.9 | 12.7178 | 1 | 2.856 | 184 | 64.4258
13.8 | 12.5074 | 1 | 2.856 | 184 | 64.4258
13.5 | 12.3853 | 1 | 2.856 | 184 | 64.4258
13.3 | 12.3032 | 1 | 2.856 | 184 | 64.4258
13.5 | 12.4989 | 1 | 2.856 | 184 | 64.4258
14.6 | 13.2833 | 1 | 2.856 | 184 | 64.4258
16.2 | 13.909 | 1 | 2.856 | 184 | 64.4258
18.1 | 14.6347 | 1 | 2.856 | 184 | 64.4258
18.3 | 15.0418 | 1 | 2.856 | 184 | 64.4258
17.5 | 14.9134 | 1 | 2.856 | 184 | 64.4258
18.5 | 15.0049 | 1 | 2.856 | 184 | 64.4258
18.6 | 15.4331 | 1 | 2.856 | 184 | 64.4258
17.7 | 15.5088 | 1 | 2.856 | 184 | 64.4258
16.3 | 15.5414 | 1 | 2.856 | 184 | 64.4258
17.2 | 15.6852 | 1 | 2.856 | 184 | 64.4258
18.6 | 15.6608 | 1 | 2.856 | 184 | 64.4258
19.1 | 15.2795 | 1 | 2.856 | 184 | 64.4258
19.5 | 15.261 | 1 | 2.856 | 184 | 64.4258
19.5 | 14.8334 | 1 | 2.856 | 184 | 64.4258
19 | 15.0749 | 1 | 2.856 | 184 | 64.4258
18 | 15.1521 | 1 | 2.856 | 184 | 64.4258
17.1 | 13.7049 | 1 | 2.856 | 184 | 64.4258
15.5 | 12.9662 | 1 | 2.856 | 184 | 64.4258
14.9 | 12.8352 | 1 | 2.856 | 184 | 64.4258
13.8 | 12.5042 | 1 | 2.856 | 184 | 64.4258
13.9 | 12.1544 | 1 | 2.856 | 184 | 64.4258
13.3 | 11.3111 | 1 | 2.856 | 184 | 64.4258
12.9 | 11.0352 | 1 | 2.856 | 184 | 64.4258
13 | 10.9202 | 1 | 2.856 | 184 | 64.4258
13.3 | 11.0989 | 1 | 2.856 | 184 | 64.4258
14 | 11.6033 | 1 | 2.856 | 184 | 64.4258
15.7 | 11.51 | 1 | 2.856 | 184 | 64.4258
16.7 | 11.9703 | 1 | 2.856 | 184 | 64.4258
16.5 | 11.1974 | 1 | 2.856 | 184 | 64.4258
16.7 | 11.3285 | 1 | 2.856 | 184 | 64.4258
16.5 | 10.7649 | 1 | 2.856 | 184 | 64.4258
14.8 | 11.2779 | 1 | 2.856 | 184 | 64.4258
16.5 | 11.4225 | 1 | 2.856 | 184 | 64.4258
16.9 | 11.1928 | 1 | 2.856 | 184 | 64.4258
16.7 | 11.418 | 1 | 2.856 | 184 | 64.4258
15.9 | 11.2663 | 1 | 2.856 | 184 | 64.4258
12.7 | 10.9517 | 1 | 2.856 | 184 | 64.4258
12.3 | 10.9955 | 1 | 2.856 | 184 | 64.4258
12.2 | 11.0078 | 1 | 2.856 | 184 | 64.4258
12.3 | 10.7813 | 1 | 2.856 | 184 | 64.4258
12.1 | 10.8032 | 1 | 2.856 | 184 | 64.4258
11.6 | 10.5875 | 1 | 2.856 | 184 | 64.4258
11.9 | 10.8257 | 1 | 2.856 | 184 | 64.4258
11.1 | 9.9942 | 1 | 2.856 | 184 | 64.4258
11 | 9.7917 | 1 | 2.856 | 184 | 64.4258
10.5 | 9.5164 | 1 | 2.856 | 184 | 64.4258
10.5 | 9.5164 | 1 | 2.856 | 184 | 64.4258
10.3 | 9.3221 | 1 | 2.856 | 184 | 64.4258
11.1 | 9.7844 | 1 | 2.856 | 184 | 64.4258
12.8 | 10.839 | 1 | 2.856 | 184 | 64.4258
14.5 | 11.8686 | 1 | 2.856 | 184 | 64.4258
16 | 11.8362 | 1 | 2.856 | 184 | 64.4258
16.9 | 12.205 | 1 | 2.856 | 184 | 64.4258
14.8 | 12.9627 | 1 | 2.856 | 184 | 64.4258
15.7 | 13.0991 | 1 | 2.856 | 184 | 64.4258
15.7 | 12.8832 | 1 | 2.856 | 184 | 64.4258
16 | 13.3802 | 1 | 2.856 | 184 | 64.4258
15.3 | 13.7834 | 1 | 2.856 | 184 | 64.4258
15.6 | 13.6124 | 1 | 2.856 | 184 | 64.4258
15.2 | 14.2153 | 1 | 2.856 | 184 | 64.4258
15.4 | 14.5313 | 1 | 2.856 | 184 | 64.4258
15.6 | 14.7276 | 1 | 2.856 | 184 | 64.4258
15.7 | 14.8254 | 1 | 2.856 | 184 | 64.4258
15.7 | 14.7039 | 1 | 2.856 | 184 | 64.4258
15.1 | 14.3573 | 1 | 2.856 | 184 | 64.4258
14 | 13.2161 | 1 | 2.856 | 184 | 64.4258
13.6 | 12.8232 | 1 | 2.856 | 184 | 64.4258
13.2 | 12.6632 | 1 | 2.856 | 184 | 64.4258
13.7 | 13.0391 | 1 | 2.856 | 184 | 64.4258
13.9 | 13.1182 | 1 | 2.856 | 184 | 64.4258
13.6 | 12.8235 | 1 | 2.856 | 184 | 64.4258
13.9 | 12.8851 | 1 | 2.856 | 184 | 64.4258
14.4 | 13.1988 | 1 | 2.856 | 184 | 64.4258
15.5 | 13.5153 | 1 | 2.856 | 184 | 64.4258
16.4 | 13.6429 | 1 | 2.856 | 184 | 64.4258
16.2 | 13.3462 | 1 | 2.856 | 184 | 64.4258
17.4 | 13.342 | 1 | 2.856 | 184 | 64.4258
18.1 | 13.5137 | 1 | 2.856 | 184 | 64.4258
17.2 | 12.1793 | 1 | 2.856 | 184 | 64.4258
17.8 | 12.4235 | 1 | 2.856 | 184 | 64.4258
18.8 | 12.3318 | 1 | 2.856 | 184 | 64.4258
18.9 | 12.1134 | 1 | 2.856 | 184 | 64.4258
19.1 | 11.8617 | 1 | 2.856 | 184 | 64.4258
18.3 | 11.0497 | 1 | 2.856 | 184 | 64.4258
17.5 | 11.4503 | 1 | 2.856 | 184 | 64.4258
16.9 | 11.6416 | 1 | 2.856 | 184 | 64.4258
16.1 | 10.9456 | 1 | 2.856 | 184 | 64.4258
14.9 | 11.1785 | 1 | 2.856 | 184 | 64.4258
14.1 | 10.7891 | 1 | 2.856 | 184 | 64.4258
13.8 | 10.6113 | 1 | 2.856 | 184 | 64.4258
13.5 | 10.5306 | 1 | 2.856 | 184 | 64.4258
13.4 | 10.5366 | 1 | 2.856 | 184 | 64.4258
13.1 | 10.1126 | 1 | 2.856 | 184 | 64.4258
13 | 10.2629 | 1 | 2.856 | 184 | 64.4258
12.8 | 10.476 | 1 | 2.856 | 184 | 64.4258
13.1 | 10.9127 | 1 | 2.856 | 184 | 64.4258
13.6 | 11.4917 | 1 | 2.856 | 184 | 64.4258
14.1 | 12.0198 | 1 | 2.856 | 184 | 64.4258
14.6 | 12.2793 | 1 | 2.856 | 184 | 64.4258
13.7 | 12.8078 | 1 | 2.856 | 184 | 64.4258
14.2 | 12.8932 | 1 | 2.856 | 184 | 64.4258
15.1 | 13.5931 | 1 | 2.856 | 184 | 64.4258
15.5 | 13.7489 | 1 | 2.856 | 184 | 64.4258
17.1 | 14.5894 | 1 | 2.856 | 184 | 64.4258
20 | 14.9173 | 1 | 2.856 | 184 | 64.4258
19.9 | 14.1244 | 1 | 2.856 | 184 | 64.4258
17.3 | 14.6667 | 1 | 2.856 | 184 | 64.4258
17.4 | 14.9325 | 1 | 2.856 | 184 | 64.4258
16.8 | 14.5358 | 1 | 2.856 | 184 | 64.4258
16.6 | 14.7498 | 1 | 2.856 | 184 | 64.4258
16.3 | 14.5783 | 1 | 2.856 | 184 | 64.4258
16.1 | 14.1553 | 1 | 2.856 | 184 | 64.4258
15.8 | 14.0399 | 1 | 2.856 | 184 | 64.4258
15.7 | 14.0591 | 1 | 2.856 | 184 | 64.4258
15.5 | 13.8664 | 1 | 2.856 | 184 | 64.4258
15.3 | 12.8922 | 1 | 2.856 | 184 | 64.4258
14.6 | 12.285 | 1 | 2.856 | 184 | 64.4258
13.9 | 11.943 | 1 | 2.856 | 184 | 64.4258
12.9 | 11.4713 | 1 | 2.856 | 184 | 64.4258
12.9 | 11.3636 | 1 | 2.856 | 184 | 64.4258
13.1 | 11.448 | 1 | 2.856 | 184 | 64.4258
13.6 | 11.7653 | 1 | 2.856 | 184 | 64.4258
15.3 | 11.9004 | 1 | 2.856 | 184 | 64.4258
17.6 | 12.4574 | 1 | 2.856 | 184 | 64.4258
18.4 | 12.8279 | 1 | 2.856 | 184 | 64.4258
18.1 | 13.3337 | 1 | 2.856 | 184 | 64.4258
17.1 | 13.6065 | 1 | 2.856 | 184 | 64.4258
17.1 | 14.037 | 1 | 2.856 | 184 | 64.4258
18 | 14.328 | 1 | 2.856 | 184 | 64.4258
17.9 | 14.0761 | 1 | 2.856 | 184 | 64.4258
19.7 | 14.7091 | 1 | 2.856 | 184 | 64.4258
19.8 | 14.7983 | 1 | 2.856 | 184 | 64.4258
19.1 | 14.7447 | 1 | 2.856 | 184 | 64.4258
18.7 | 14.7009 | 1 | 2.856 | 184 | 64.4258
18.1 | 14.8593 | 1 | 2.856 | 184 | 64.4258
17.7 | 15.1053 | 1 | 2.856 | 184 | 64.4258
17.1 | 14.709 | 1 | 2.856 | 184 | 64.4258
15.7 | 13.718 | 1 | 2.856 | 184 | 64.4258
15.3 | 13.5615 | 1 | 2.856 | 184 | 64.4258
14.8 | 13.1938 | 1 | 2.856 | 184 | 64.4258
14.3 | 13.2239 | 1 | 2.856 | 184 | 64.4258
14.5 | 12.9618 | 1 | 2.856 | 184 | 64.4258
14.6 | 12.9457 | 1 | 2.856 | 184 | 64.4258
14.4 | 12.9782 | 1 | 2.856 | 184 | 64.4258
14.3 | 12.9954 | 1 | 2.856 | 184 | 64.4258
14.4 | 12.9787 | 1 | 2.856 | 184 | 64.4258
15 | 13.3884 | 1 | 2.856 | 184 | 64.4258
15 | 13.5597 | 1 | 2.856 | 184 | 64.4258
15.6 | 13.7378 | 1 | 2.856 | 184 | 64.4258
16.5 | 14.2 | 1 | 2.856 | 184 | 64.4258
16.7 | 14.4467 | 1 | 2.856 | 184 | 64.4258
17.7 | 14.7704 | 1 | 2.856 | 184 | 64.4258
19 | 15.2016 | 1 | 2.856 | 184 | 64.4258
21.3 | 15.8843 | 1 | 2.856 | 184 | 64.4258
21.4 | 15.9205 | 1 | 2.856 | 184 | 64.4258
22.6 | 16.5577 | 1 | 2.856 | 184 | 64.4258
22.1 | 16.5955 | 1 | 2.856 | 184 | 64.4258
21.4 | 16.6757 | 1 | 2.856 | 184 | 64.4258
20.2 | 16.082 | 1 | 2.856 | 184 | 64.4258
18.9 | 15.555 | 1 | 2.856 | 184 | 64.4258
18.3 | 15.6204 | 1 | 2.856 | 184 | 64.4258
17.2 | 15.3923 | 1 | 2.856 | 184 | 64.4258
16.5 | 14.7774 | 1 | 2.856 | 184 | 64.4258
16.2 | 14.6052 | 1 | 2.856 | 184 | 64.4258
15.7 | 14.4146 | 1 | 2.856 | 184 | 64.4258
15.1 | 13.8898 | 1 | 2.856 | 184 | 64.4258
14.5 | 13.5379 | 1 | 2.856 | 184 | 64.4258
14.5 | 13.422 | 1 | 2.856 | 184 | 64.4258
15.1 | 13.7162 | 1 | 2.856 | 184 | 64.4258
16.2 | 14.1451 | 1 | 2.856 | 184 | 64.4258
19.1 | 15.5202 | 1 | 2.856 | 184 | 64.4258
21.6 | 16.643 | 1 | 2.856 | 184 | 64.4258
23.9 | 17.2331 | 1 | 2.856 | 184 | 64.4258
25.3 | 17.3578 | 1 | 2.856 | 184 | 64.4258
26.4 | 17.2973 | 1 | 2.856 | 184 | 64.4258
27.2 | 17.6666 | 1 | 2.856 | 184 | 64.4258
27.9 | 18.287 | 1 | 2.856 | 184 | 64.4258
28.8 | 18.7267 | 1 | 2.856 | 184 | 64.4258
28.6 | 18.8582 | 1 | 2.856 | 184 | 64.4258
29 | 19.0376 | 1 | 2.856 | 184 | 64.4258
28 | 18.5627 | 1 | 2.856 | 184 | 64.4258
27 | 18.7462 | 1 | 2.856 | 184 | 64.4258
25.3 | 17.923 | 1 | 2.856 | 184 | 64.4258
23.8 | 17.7894 | 1 | 2.856 | 184 | 64.4258
22.6 | 17.5465 | 1 | 2.856 | 184 | 64.4258
21.5 | 17.3402 | 1 | 2.856 | 184 | 64.4258
20.2 | 17.1822 | 1 | 2.856 | 184 | 64.4258
19.8 | 16.572 | 1 | 2.856 | 184 | 64.4258
19.5 | 16.4071 | 1 | 2.856 | 184 | 64.4258
19.2 | 16.0683 | 1 | 2.856 | 184 | 64.4258
18.5 | 16.2251 | 1 | 2.856 | 184 | 64.4258
19.1 | 15.9747 | 1 | 2.856 | 184 | 64.4258
19.2 | 16.1847 | 1 | 2.856 | 184 | 64.4258
21 | 16.3799 | 1 | 2.856 | 184 | 64.4258
23.3 | 17.4051 | 1 | 2.856 | 184 | 64.4258
23.3 | 18.1824 | 1 | 2.856 | 184 | 64.4258
24.6 | 17.9561 | 1 | 2.856 | 184 | 64.4258
25.6 | 18.7765 | 1 | 2.856 | 184 | 64.4258
26.1 | 18.8312 | 1 | 2.856 | 184 | 64.4258
26.4 | 19.2557 | 1 | 2.856 | 184 | 64.4258
26.6 | 18.9916 | 1 | 2.856 | 184 | 64.4258
27.3 | 19.0589 | 1 | 2.856 | 184 | 64.4258
27.5 | 18.9667 | 1 | 2.856 | 184 | 64.4258
27 | 17.7969 | 1 | 2.856 | 184 | 64.4258
26.3 | 17.4128 | 1 | 2.856 | 184 | 64.4258
24.3 | 17.7452 | 1 | 2.856 | 184 | 64.4258
22.9 | 16.8891 | 1 | 2.856 | 184 | 64.4258
21.9 | 16.3231 | 1 | 2.856 | 184 | 64.4258
20.9 | 16.5099 | 1 | 2.856 | 184 | 64.4258
20.3 | 16.6352 | 1 | 2.856 | 184 | 64.4258
19.2 | 16.5355 | 1 | 2.856 | 184 | 64.4258
17.4 | 15.352 | 1 | 2.856 | 184 | 64.4258
16.3 | 14.4721 | 1 | 2.856 | 184 | 64.4258
15.5 | 13.8752 | 1 | 2.856 | 184 | 64.4258
14.8 | 12.9773 | 1 | 2.856 | 184 | 64.4258
14.5 | 12.4177 | 1 | 2.856 | 184 | 64.4258
14.7 | 12.4461 | 1 | 2.856 | 184 | 64.4258
16.1 | 13.068 | 1 | 2.856 | 184 | 64.4258
17 | 13.4275 | 1 | 2.856 | 184 | 64.4258
18.7 | 14.1437 | 1 | 2.856 | 184 | 64.4258
20.1 | 14.8318 | 1 | 2.856 | 184 | 64.4258
21.7 | 15.3306 | 1 | 2.856 | 184 | 64.4258
23.4 | 16.0972 | 1 | 2.856 | 184 | 64.4258
25.2 | 16.5965 | 1 | 2.856 | 184 | 64.4258
25.9 | 17.2205 | 1 | 2.856 | 184 | 64.4258
27 | 17.5035 | 1 | 2.856 | 184 | 64.4258
26.9 | 17.1393 | 1 | 2.856 | 184 | 64.4258
26.7 | 17.3501 | 1 | 2.856 | 184 | 64.4258
26.5 | 17.6147 | 1 | 2.856 | 184 | 64.4258
24.3 | 17.3143 | 1 | 2.856 | 184 | 64.4258
22 | 16.6178 | 1 | 2.856 | 184 | 64.4258
20.1 | 16.1047 | 1 | 2.856 | 184 | 64.4258
19.7 | 15.9056 | 1 | 2.856 | 184 | 64.4258
18.4 | 15.6014 | 1 | 2.856 | 184 | 64.4258
17.2 | 15.0412 | 1 | 2.856 | 184 | 64.4258
15.8 | 14.2778 | 1 | 2.856 | 184 | 64.4258
15.4 | 14.1817 | 1 | 2.856 | 184 | 64.4258
15.2 | 14.2228 | 1 | 2.856 | 184 | 64.4258
14.9 | 13.9292 | 1 | 2.856 | 184 | 64.4258
14.9 | 14.0472 | 1 | 2.856 | 184 | 64.4258
16.3 | 14.76 | 1 | 2.856 | 184 | 64.4258
17.8 | 15.5535 | 1 | 2.856 | 184 | 64.4258
20 | 16.637 | 1 | 2.856 | 184 | 64.4258
22.3 | 17.5501 | 1 | 2.856 | 184 | 64.4258
24.5 | 18.4018 | 1 | 2.856 | 184 | 64.4258
26.3 | 18.8257 | 1 | 2.856 | 184 | 64.4258
27.6 | 19.2453 | 1 | 2.856 | 184 | 64.4258
29.1 | 20.3578 | 1 | 2.856 | 184 | 64.4258
29 | 20.2727 | 1 | 2.856 | 184 | 64.4258
28.9 | 19.4965 | 1 | 2.856 | 184 | 64.4258
29.5 | 19.7858 | 1 | 2.856 | 184 | 64.4258
28.5 | 19.7351 | 1 | 2.856 | 184 | 64.4258
28.8 | 20.0431 | 1 | 2.856 | 184 | 64.4258
26.6 | 20.0879 | 1 | 2.856 | 184 | 64.4258
25.2 | 19.8282 | 1 | 2.856 | 184 | 64.4258
23.6 | 19.024 | 1 | 2.856 | 184 | 64.4258
22.4 | 18.5123 | 1 | 2.856 | 184 | 64.4258
21 | 18.1103 | 1 | 2.856 | 184 | 64.4258
20.5 | 17.3955 | 1 | 2.856 | 184 | 64.4258
19.8 | 16.915 | 1 | 2.856 | 184 | 64.4258
19.3 | 16.5023 | 1 | 2.856 | 184 | 64.4258
18.7 | 16.1107 | 1 | 2.856 | 184 | 64.4258
18.3 | 15.7903 | 1 | 2.856 | 184 | 64.4258
18.1 | 15.7176 | 1 | 2.856 | 184 | 64.4258
19 | 16.1012 | 1 | 2.856 | 184 | 64.4258
20.3 | 16.9697 | 1 | 2.856 | 184 | 64.4258
22.1 | 17.9366 | 1 | 2.856 | 184 | 64.4258
24.6 | 19.2239 | 1 | 2.856 | 184 | 64.4258
26.5 | 19.6517 | 1 | 2.856 | 184 | 64.4258
28.1 | 19.9841 | 1 | 2.856 | 184 | 64.4258
28.9 | 19.905 | 1 | 2.856 | 184 | 64.4258
30 | 19.9293 | 1 | 2.856 | 184 | 64.4258
29.5 | 19.7706 | 1 | 2.856 | 184 | 64.4258
30.1 | 18.7301 | 1 | 2.856 | 184 | 64.4258
30.7 | 18.3331 | 1 | 2.856 | 184 | 64.4258
29.4 | 16.6849 | 1 | 2.856 | 184 | 64.4258
28.3 | 16.096 | 1 | 2.856 | 184 | 64.4258
27.2 | 15.6217 | 1 | 2.856 | 184 | 64.4258
25.2 | 16.4564 | 1 | 2.856 | 184 | 64.4258
23.3 | 16.1708 | 1 | 2.856 | 184 | 64.4258
21.7 | 16.167 | 1 | 2.856 | 184 | 64.4258
20.2 | 15.7359 | 1 | 2.856 | 184 | 64.4258
19.6 | 15.573 | 1 | 2.856 | 184 | 64.4258
19.1 | 15.7276 | 1 | 2.856 | 184 | 64.4258
18.1 | 15.4786 | 1 | 2.856 | 184 | 64.4258
17.5 | 15.1993 | 1 | 2.856 | 184 | 64.4258
16.9 | 14.7438 | 1 | 2.856 | 184 | 64.4258
16.7 | 14.8438 | 1 | 2.856 | 184 | 64.4258
17.4 | 15.4568 | 1 | 2.856 | 184 | 64.4258
18.1 | 15.8297 | 1 | 2.856 | 184 | 64.4258
19 | 16.6289 | 1 | 2.856 | 184 | 64.4258
20.8 | 17.3711 | 1 | 2.856 | 184 | 64.4258
22.7 | 17.8387 | 1 | 2.856 | 184 | 64.4258
24.6 | 17.8082 | 1 | 2.856 | 184 | 64.4258
26 | 17.6049 | 1 | 2.856 | 184 | 64.4258
26.1 | 17.5886 | 1 | 2.856 | 184 | 64.4258
27.5 | 18.1562 | 1 | 2.856 | 184 | 64.4258
26.8 | 17.8737 | 1 | 2.856 | 184 | 64.4258
26.2 | 17.1338 | 1 | 2.856 | 184 | 64.4258
26.7 | 17.2103 | 1 | 2.856 | 184 | 64.4258
25.9 | 16.6058 | 1 | 2.856 | 184 | 64.4258
25.7 | 16.3972 | 1 | 2.856 | 184 | 64.4258
23.8 | 16.5481 | 1 | 2.856 | 184 | 64.4258
22.2 | 16.1372 | 1 | 2.856 | 184 | 64.4258
20.9 | 16.0441 | 1 | 2.856 | 184 | 64.4258
19.3 | 15.7446 | 1 | 2.856 | 184 | 64.4258
19 | 14.6492 | 1 | 2.856 | 184 | 64.4258
17.9 | 14.0716 | 1 | 2.856 | 184 | 64.4258
16.7 | 13.6607 | 1 | 2.856 | 184 | 64.4258
15.8 | 13.0899 | 1 | 2.856 | 184 | 64.4258
14.9 | 12.4056 | 1 | 2.856 | 184 | 64.4258
14.8 | 12.1539 | 1 | 2.856 | 184 | 64.4258
15.4 | 11.7894 | 1 | 2.856 | 184 | 64.4258
16.8 | 12.3178 | 1 | 2.856 | 184 | 64.4258
17.5 | 12.3676 | 1 | 2.856 | 184 | 64.4258
18.9 | 13.1191 | 1 | 2.856 | 184 | 64.4258
19.9 | 13.7946 | 1 | 2.856 | 184 | 64.4258
21.2 | 14.0197 | 1 | 2.856 | 184 | 64.4258
21.9 | 14.1988 | 1 | 2.856 | 184 | 64.4258
22.9 | 14.8915 | 1 | 2.856 | 184 | 64.4258
23.1 | 14.7427 | 1 | 2.856 | 184 | 64.4258
23.7 | 15.0079 | 1 | 2.856 | 184 | 64.4258
24 | 15.2074 | 1 | 2.856 | 184 | 64.4258
23.8 | 14.7846 | 1 | 2.856 | 184 | 64.4258
23.5 | 14.9335 | 1 | 2.856 | 184 | 64.4258
22.8 | 14.6712 | 1 | 2.856 | 184 | 64.4258
21.7 | 14.5291 | 1 | 2.856 | 184 | 64.4258
20.8 | 14.62 | 1 | 2.856 | 184 | 64.4258
20.2 | 14.4419 | 1 | 2.856 | 184 | 64.4258
19.4 | 14.1865 | 1 | 2.856 | 184 | 64.4258
17.3 | 14.0583 | 1 | 2.856 | 184 | 64.4258
16.3 | 13.7812 | 1 | 2.856 | 184 | 64.4258
15.3 | 12.8922 | 1 | 2.856 | 184 | 64.4258
15.3 | 12.6756 | 1 | 2.856 | 184 | 64.4258
15 | 12.3941 | 1 | 2.856 | 184 | 64.4258
14.6 | 12.5 | 1 | 2.856 | 184 | 64.4258
15.7 | 12.8911 | 1 | 2.856 | 184 | 64.4258
17.8 | 13.7716 | 1 | 2.856 | 184 | 64.4258
19.9 | 14.5763 | 1 | 2.856 | 184 | 64.4258
21.7 | 15.1988 | 1 | 2.856 | 184 | 64.4258
23.3 | 15.9293 | 1 | 2.856 | 184 | 64.4258
25 | 16.4837 | 1 | 2.856 | 184 | 64.4258
26 | 16.5097 | 1 | 2.856 | 184 | 64.4258
26.9 | 17.1883 | 1 | 2.856 | 184 | 64.4258
28.5 | 17.28 | 1 | 2.856 | 184 | 64.4258
27.9 | 16.8989 | 1 | 2.856 | 184 | 64.4258
28.5 | 17.4087 | 1 | 2.856 | 184 | 64.4258
27.2 | 16.8285 | 1 | 2.856 | 184 | 64.4258
26.5 | 16.4466 | 1 | 2.856 | 184 | 64.4258
25 | 15.959 | 1 | 2.856 | 184 | 64.4258
23.6 | 15.5928 | 1 | 2.856 | 184 | 64.4258
22.2 | 15.0321 | 1 | 2.856 | 184 | 64.4258
21 | 15.1285 | 1 | 2.856 | 184 | 64.4258
19.6 | 14.7103 | 1 | 2.856 | 184 | 64.4258
18.3 | 14.1643 | 1 | 2.856 | 184 | 64.4258
17.6 | 14.1102 | 1 | 2.856 | 184 | 64.4258
17.1 | 14.0263 | 1 | 2.856 | 184 | 64.4258
16.1 | 13.6949 | 1 | 2.856 | 184 | 64.4258
15.9 | 13.7305 | 1 | 2.856 | 184 | 64.4258
15.6 | 13.7269 | 1 | 2.856 | 184 | 64.4258
16.8 | 14.1881 | 1 | 2.856 | 184 | 64.4258
17.7 | 14.7528 | 1 | 2.856 | 184 | 64.4258
19.3 | 15.3995 | 1 | 2.856 | 184 | 64.4258
21.7 | 15.6325 | 1 | 2.856 | 184 | 64.4258
22.3 | 15.2531 | 1 | 2.856 | 184 | 64.4258
22.6 | 15.4087 | 1 | 2.856 | 184 | 64.4258
23.3 | 15.8076 | 1 | 2.856 | 184 | 64.4258
26.4 | 16.3047 | 1 | 2.856 | 184 | 64.4258
24.3 | 15.8304 | 1 | 2.856 | 184 | 64.4258
23.1 | 16.0292 | 1 | 2.856 | 184 | 64.4258
20.7 | 16.9156 | 1 | 2.856 | 184 | 64.4258
21.6 | 17.167 | 1 | 2.856 | 184 | 64.4258
17.7 | 16.7268 | 1 | 2.856 | 184 | 64.4258
17.6 | 15.4069 | 1 | 2.856 | 184 | 64.4258
17.4 | 14.8102 | 1 | 2.856 | 184 | 64.4258
16.2 | 13.2404 | 1 | 2.856 | 184 | 64.4258
15.6 | 12.6293 | 1 | 2.856 | 184 | 64.4258
14.4 | 12.1958 | 1 | 2.856 | 184 | 64.4258
14.1 | 12.3469 | 1 | 2.856 | 184 | 64.4258
14.3 | 12.6499 | 1 | 2.856 | 184 | 64.4258
14.1 | 12.4576 | 1 | 2.856 | 184 | 64.4258
13.7 | 12.2956 | 1 | 2.856 | 184 | 64.4258
13.2 | 11.9793 | 1 | 2.856 | 184 | 64.4258
13.8 | 12.0607 | 1 | 2.856 | 184 | 64.4258
14.1 | 11.9152 | 1 | 2.856 | 184 | 64.4258
15.6 | 12.3232 | 1 | 2.856 | 184 | 64.4258
17.1 | 12.5333 | 1 | 2.856 | 184 | 64.4258
17.5 | 11.6825 | 1 | 2.856 | 184 | 64.4258
18.4 | 11.5091 | 1 | 2.856 | 184 | 64.4258
19.9 | 12.256 | 1 | 2.856 | 184 | 64.4258
21.1 | 12.2416 | 1 | 2.856 | 184 | 64.4258
20.9 | 12.8239 | 1 | 2.856 | 184 | 64.4258
23.1 | 13.6547 | 1 | 2.856 | 184 | 64.4258
23 | 13.7745 | 1 | 2.856 | 184 | 64.4258
22.5 | 13.4594 | 1 | 2.856 | 184 | 64.4258
20.9 | 13.2829 | 1 | 2.856 | 184 | 64.4258
20 | 13.2357 | 1 | 2.856 | 184 | 64.4258
19.3 | 13.1851 | 1 | 2.856 | 184 | 64.4258
18.5 | 13.054 | 1 | 2.856 | 184 | 64.4258
17.7 | 13.2251 | 1 | 2.856 | 184 | 64.4258
17.1 | 13.1896 | 1 | 2.856 | 184 | 64.4258
16.6 | 13.1985 | 1 | 2.856 | 184 | 64.4258
16.6 | 13.3569 | 1 | 2.856 | 184 | 64.4258
15.9 | 13.2954 | 1 | 2.856 | 184 | 64.4258
15.6 | 13.5085 | 1 | 2.856 | 184 | 64.4258
15.5 | 13.7516 | 1 | 2.856 | 184 | 64.4258
14.9 | 13.4028 | 1 | 2.856 | 184 | 64.4258
15.6 | 13.2863 | 1 | 2.856 | 184 | 64.4258
16.8 | 14.0866 | 1 | 2.856 | 184 | 64.4258
17.5 | 13.3496 | 1 | 2.856 | 184 | 64.4258
17.5 | 12.8015 | 1 | 2.856 | 184 | 64.4258
18.3 | 12.9784 | 1 | 2.856 | 184 | 64.4258
19.2 | 12.877 | 1 | 2.856 | 184 | 64.4258
20.7 | 13.2987 | 1 | 2.856 | 184 | 64.4258
22.1 | 13.8475 | 1 | 2.856 | 184 | 64.4258
23.4 | 14.1826 | 1 | 2.856 | 184 | 64.4258
24.3 | 14.3259 | 1 | 2.856 | 184 | 64.4258
24.9 | 14.06 | 1 | 2.856 | 184 | 64.4258
23.7 | 14.0563 | 1 | 2.856 | 184 | 64.4258
24 | 14.3347 | 1 | 2.856 | 184 | 64.4258
23.1 | 14.1119 | 1 | 2.856 | 184 | 64.4258
22 | 13.6435 | 1 | 2.856 | 184 | 64.4258
20.5 | 13.0932 | 1 | 2.856 | 184 | 64.4258
18.7 | 12.8168 | 1 | 2.856 | 184 | 64.4258
17.2 | 12.2081 | 1 | 2.856 | 184 | 64.4258
15.9 | 11.6204 | 1 | 2.856 | 184 | 64.4258
15 | 11.2881 | 1 | 2.856 | 184 | 64.4258
15 | 11.2881 | 1 | 2.856 | 184 | 64.4258
12.9 | 10.4825 | 1 | 2.856 | 184 | 64.4258
12.5 | 10.51 | 1 | 2.856 | 184 | 64.4258
12.5 | 10.8746 | 1 | 2.856 | 184 | 64.4258
12.3 | 10.7884 | 1 | 2.856 | 184 | 64.4258
13.5 | 11.6185 | 1 | 2.856 | 184 | 64.4258
15.8 | 12.4144 | 1 | 2.856 | 184 | 64.4258
16.7 | 12.5781 | 1 | 2.856 | 184 | 64.4258
17.3 | 12.7227 | 1 | 2.856 | 184 | 64.4258
18.3 | 13.1722 | 1 | 2.856 | 184 | 64.4258
18.2 | 13.3276 | 1 | 2.856 | 184 | 64.4258
18.7 | 13.722 | 1 | 2.856 | 184 | 64.4258
20.3 | 14.4351 | 1 | 2.856 | 184 | 64.4258
21.6 | 15.1198 | 1 | 2.856 | 184 | 64.4258
22.3 | 15.2817 | 1 | 2.856 | 184 | 64.4258
23.1 | 15.8625 | 1 | 2.856 | 184 | 64.4258
22.5 | 15.6943 | 1 | 2.856 | 184 | 64.4258
22.6 | 15.6813 | 1 | 2.856 | 184 | 64.4258
21.2 | 15.2682 | 1 | 2.856 | 184 | 64.4258
19.2 | 14.5202 | 1 | 2.856 | 184 | 64.4258
17.4 | 13.7237 | 1 | 2.856 | 184 | 64.4258
15.5 | 12.7596 | 1 | 2.856 | 184 | 64.4258
14.6 | 12.5026 | 1 | 2.856 | 184 | 64.4258
14.2 | 12.3386 | 1 | 2.856 | 184 | 64.4258
13.4 | 11.9544 | 1 | 2.856 | 184 | 64.4258
13.4 | 11.9544 | 1 | 2.856 | 184 | 64.4258
12.7 | 11.7187 | 1 | 2.856 | 184 | 64.4258
12.6 | 11.6207 | 1 | 2.856 | 184 | 64.4258
12.7 | 11.7183 | 1 | 2.856 | 184 | 64.4258
14 | 12.5891 | 1 | 2.856 | 184 | 64.4258
15.4 | 13.3172 | 1 | 2.856 | 184 | 64.4258
16.3 | 14.0049 | 1 | 2.856 | 184 | 64.4258
17.2 | 14.4617 | 1 | 2.856 | 184 | 64.4258
17.2 | 14.5743 | 1 | 2.856 | 184 | 64.4258
18.3 | 15.0418 | 1 | 2.856 | 184 | 64.4258
19.5 | 15.2657 | 1 | 2.856 | 184 | 64.4258
20.1 | 15.6467 | 1 | 2.856 | 184 | 64.4258
20.2 | 15.5209 | 1 | 2.856 | 184 | 64.4258
20.3 | 15.6651 | 1 | 2.856 | 184 | 64.4258
20.3 | 15.6634 | 1 | 2.856 | 184 | 64.4258
21.3 | 15.6551 | 1 | 2.856 | 184 | 64.4258
21.1 | 15.1194 | 1 | 2.856 | 184 | 64.4258
20.7 | 15.2782 | 1 | 2.856 | 184 | 64.4258
19.3 | 14.9713 | 1 | 2.856 | 184 | 64.4258
18.4 | 14.7982 | 1 | 2.856 | 184 | 64.4258
17.9 | 14.7772 | 1 | 2.856 | 184 | 64.4258
17.2 | 14.4565 | 1 | 2.856 | 184 | 64.4258
17.2 | 14.1781 | 1 | 2.856 | 184 | 64.4258
16.5 | 14.0763 | 1 | 2.856 | 184 | 64.4258
16.7 | 14.4364 | 1 | 2.856 | 184 | 64.4258
16.5 | 14.3025 | 1 | 2.856 | 184 | 64.4258
16.5 | 14.6496 | 1 | 2.856 | 184 | 64.4258
16.7 | 14.841 | 1 | 2.856 | 184 | 64.4258
16.7 | 14.7238 | 1 | 2.856 | 184 | 64.4258
17.1 | 14.9313 | 1 | 2.856 | 184 | 64.4258
18.1 | 15.3004 | 1 | 2.856 | 184 | 64.4258
18.2 | 15.2797 | 1 | 2.856 | 184 | 64.4258
18.5 | 15.1072 | 1 | 2.856 | 184 | 64.4258
19 | 15.4027 | 1 | 2.856 | 184 | 64.4258
20.5 | 15.8359 | 1 | 2.856 | 184 | 64.4258
22 | 16.0507 | 1 | 2.856 | 184 | 64.4258
21.7 | 15.9436 | 1 | 2.856 | 184 | 64.4258
21.7 | 16.1531 | 1 | 2.856 | 184 | 64.4258
21.9 | 16.2772 | 1 | 2.856 | 184 | 64.4258
21.7 | 16.3679 | 1 | 2.856 | 184 | 64.4258
21.9 | 16.4904 | 1 | 2.856 | 184 | 64.4258
21 | 16.6751 | 1 | 2.856 | 184 | 64.4258
18.7 | 16.5181 | 1 | 2.856 | 184 | 64.4258
17.7 | 16.5378 | 1 | 2.856 | 184 | 64.4258
17.9 | 15.399 | 1 | 2.856 | 184 | 64.4258
17.1 | 15.1646 | 1 | 2.856 | 184 | 64.4258
16.4 | 14.9053 | 1 | 2.856 | 184 | 64.4258
15.8 | 14.8025 | 1 | 2.856 | 184 | 64.4258
15.6 | 14.6067 | 1 | 2.856 | 184 | 64.4258
15.1 | 14.5403 | 1 | 2.856 | 184 | 64.4258
15.3 | 14.6154 | 1 | 2.856 | 184 | 64.4258
15.5 | 14.9353 | 1 | 2.856 | 184 | 64.4258
15.5 | 14.9353 | 1 | 2.856 | 184 | 64.4258
15.7 | 14.9475 | 1 | 2.856 | 184 | 64.4258
15.7 | 15.0708 | 1 | 2.856 | 184 | 64.4258
15.6 | 15.0337 | 1 | 2.856 | 184 | 64.4258
16.2 | 15.6267 | 1 | 2.856 | 184 | 64.4258
16.4 | 15.9506 | 1 | 2.856 | 184 | 64.4258
16.7 | 16.184 | 1 | 2.856 | 184 | 64.4258
16.7 | 16.184 | 1 | 2.856 | 184 | 64.4258
19.4 | 17.7468 | 1 | 2.856 | 184 | 64.4258
19.9 | 17.1694 | 1 | 2.856 | 184 | 64.4258
20 | 16.8432 | 1 | 2.856 | 184 | 64.4258
21.3 | 16.2139 | 1 | 2.856 | 184 | 64.4258
20.5 | 15.6034 | 1 | 2.856 | 184 | 64.4258
19.5 | 15.1318 | 1 | 2.856 | 184 | 64.4258
18.3 | 15.0235 | 1 | 2.856 | 184 | 64.4258
17.9 | 14.9324 | 1 | 2.856 | 184 | 64.4258
17.4 | 14.9185 | 1 | 2.856 | 184 | 64.4258
16.9 | 14.7331 | 1 | 2.856 | 184 | 64.4258
16.9 | 14.7331 | 1 | 2.856 | 184 | 64.4258
16.4 | 14.7826 | 1 | 2.856 | 184 | 64.4258
15.8 | 15.1685 | 1 | 2.856 | 184 | 64.4258
15.6 | 15.2828 | 1 | 2.856 | 184 | 64.4258
15.7 | 15.2565 | 1 | 2.856 | 184 | 64.4258
16.1 | 15.6528 | 1 | 2.856 | 184 | 64.4258
16.4 | 15.5106 | 1 | 2.856 | 184 | 64.4258
16.4 | 15.082 | 1 | 2.856 | 184 | 64.4258
17 | 15.6656 | 1 | 2.856 | 184 | 64.4258
17.6 | 16.064 | 1 | 2.856 | 184 | 64.4258
15.9 | 15.1435 | 1 | 2.856 | 184 | 64.4258
16.2 | 15.0093 | 1 | 2.856 | 184 | 64.4258
16.5 | 14.644 | 1 | 2.856 | 184 | 64.4258
16.1 | 14.0298 | 1 | 2.856 | 184 | 64.4258
15.5 | 13.5145 | 1 | 2.856 | 184 | 64.4258
15.3 | 13.3242 | 1 | 2.856 | 184 | 64.4258
15.7 | 13.4257 | 1 | 2.856 | 184 | 64.4258
15.8 | 13.0812 | 1 | 2.856 | 184 | 64.4258
15.7 | 12.8798 | 1 | 2.856 | 184 | 64.4258
15.7 | 12.5111 | 1 | 2.856 | 184 | 64.4258
15.6 | 12.6293 | 1 | 2.856 | 184 | 64.4258
15.3 | 12.4554 | 1 | 2.856 | 184 | 64.4258
15 | 12.1755 | 1 | 2.856 | 184 | 64.4258
14.8 | 12.0424 | 1 | 2.856 | 184 | 64.4258
14.6 | 11.8556 | 1 | 2.856 | 184 | 64.4258
14.4 | 11.8774 | 1 | 2.856 | 184 | 64.4258
14.2 | 11.7946 | 1 | 2.856 | 184 | 64.4258
14.1 | 11.7005 | 1 | 2.856 | 184 | 64.4258
14 | 11.7116 | 1 | 2.856 | 184 | 64.4258
14 | 11.8186 | 1 | 2.856 | 184 | 64.4258
14.4 | 12.0904 | 1 | 2.856 | 184 | 64.4258
15.2 | 12.0015 | 1 | 2.856 | 184 | 64.4258
15.9 | 12.0878 | 1 | 2.856 | 184 | 64.4258
17.1 | 12.1917 | 1 | 2.856 | 184 | 64.4258
17.5 | 12.2614 | 1 | 2.856 | 184 | 64.4258
18 | 12.6515 | 1 | 2.856 | 184 | 64.4258
19.2 | 13.175 | 1 | 2.856 | 184 | 64.4258
19.1 | 12.9965 | 1 | 2.856 | 184 | 64.4258
19.6 | 13.3791 | 1 | 2.856 | 184 | 64.4258
19.5 | 13.2933 | 1 | 2.856 | 184 | 64.4258
18.9 | 13.2447 | 1 | 2.856 | 184 | 64.4258
18.5 | 13.4755 | 1 | 2.856 | 184 | 64.4258
18 | 13.0797 | 1 | 2.856 | 184 | 64.4258
17.5 | 12.3529 | 1 | 2.856 | 184 | 64.4258
16.9 | 11.8732 | 1 | 2.856 | 184 | 64.4258
15.9 | 12.4912 | 1 | 2.856 | 184 | 64.4258
15.7 | 12.2053 | 1 | 2.856 | 184 | 64.4258
14.5 | 12.2914 | 1 | 2.856 | 184 | 64.4258
14.1 | 13.1402 | 1 | 2.856 | 184 | 64.4258
14 | 12.6977 | 1 | 2.856 | 184 | 64.4258
13.7 | 12.691 | 1 | 2.856 | 184 | 64.4258
13.5 | 12.8429 | 1 | 2.856 | 184 | 64.4258
13.4 | 12.8616 | 1 | 2.856 | 184 | 64.4258
12.8 | 12.2691 | 1 | 2.856 | 184 | 64.4258
12.9 | 12.3678 | 1 | 2.856 | 184 | 64.4258
12.9 | 12.4846 | 1 | 2.856 | 184 | 64.4258
12.8 | 12.4441 | 1 | 2.856 | 184 | 64.4258
13.3 | 12.8807 | 1 | 2.856 | 184 | 64.4258
13.4 | 12.9797 | 1 | 2.856 | 184 | 64.4258
13.6 | 12.9414 | 1 | 2.856 | 184 | 64.4258
14 | 13.3354 | 1 | 2.856 | 184 | 64.4258
14.4 | 13.8494 | 1 | 2.856 | 184 | 64.4258
14.9 | 14.222 | 1 | 2.856 | 184 | 64.4258
15.1 | 14.4191 | 1 | 2.856 | 184 | 64.4258
15 | 14.5032 | 1 | 2.856 | 184 | 64.4258
15.3 | 14.8618 | 1 | 2.856 | 184 | 64.4258
15.4 | 14.9607 | 1 | 2.856 | 184 | 64.4258
15.5 | 15.0598 | 1 | 2.856 | 184 | 64.4258
15.5 | 15.06 | 1 | 2.856 | 184 | 64.4258
15.5 | 15.1846 | 1 | 2.856 | 184 | 64.4258
15.5 | 15.3101 | 1 | 2.856 | 184 | 64.4258
15.5 | 15.3101 | 1 | 2.856 | 184 | 64.4258
15.3 | 15.1737 | 1 | 2.856 | 184 | 64.4258
15.2 | 15.0739 | 1 | 2.856 | 184 | 64.4258
15.3 | 15.1108 | 1 | 2.856 | 184 | 64.4258
15.5 | 15.3732 | 1 | 2.856 | 184 | 64.4258
15.7 | 15.5726 | 1 | 2.856 | 184 | 64.4258
15.9 | 15.7721 | 1 | 2.856 | 184 | 64.4258
16.1 | 15.9076 | 1 | 2.856 | 184 | 64.4258
16.4 | 16.2708 | 1 | 2.856 | 184 | 64.4258
17 | 16.8043 | 1 | 2.856 | 184 | 64.4258
17.5 | 17.1717 | 1 | 2.856 | 184 | 64.4258
19.2 | 18.4612 | 1 | 2.856 | 184 | 64.4258
21.7 | 19.2002 | 1 | 2.856 | 184 | 64.4258
23.2 | 19.6728 | 1 | 2.856 | 184 | 64.4258
24.4 | 19.1362 | 1 | 2.856 | 184 | 64.4258
22.9 | 18.4776 | 1 | 2.856 | 184 | 64.4258
22.4 | 19.0456 | 1 | 2.856 | 184 | 64.4258
24.9 | 18.7753 | 1 | 2.856 | 184 | 64.4258
23.3 | 18.5471 | 1 | 2.856 | 184 | 64.4258
23.7 | 18.6182 | 1 | 2.856 | 184 | 64.4258
22.3 | 17.9848 | 1 | 2.856 | 184 | 64.4258
20.9 | 17.636 | 1 | 2.856 | 184 | 64.4258
19.5 | 17.2224 | 1 | 2.856 | 184 | 64.4258
18.8 | 16.7358 | 1 | 2.856 | 184 | 64.4258
17.3 | 15.5364 | 1 | 2.856 | 184 | 64.4258
16.5 | 14.7657 | 1 | 2.856 | 184 | 64.4258
16 | 14.5783 | 1 | 2.856 | 184 | 64.4258
15.4 | 14.1738 | 1 | 2.856 | 184 | 64.4258
15.7 | 14.4063 | 1 | 2.856 | 184 | 64.4258
15.2 | 13.9786 | 1 | 2.856 | 184 | 64.4258
14.9 | 13.6872 | 1 | 2.856 | 184 | 64.4258
15.5 | 13.9773 | 1 | 2.856 | 184 | 64.4258
17.2 | 14.3423 | 1 | 2.856 | 184 | 64.4258
17.9 | 14.4418 | 1 | 2.856 | 184 | 64.4258
19.9 | 14.463 | 1 | 2.856 | 184 | 64.4258
19.8 | 14.2251 | 1 | 2.856 | 184 | 64.4258
22.4 | 15.688 | 1 | 2.856 | 184 | 64.4258
21.1 | 14.9128 | 1 | 2.856 | 184 | 64.4258
22 | 14.9552 | 1 | 2.856 | 184 | 64.4258
22.6 | 15.2723 | 1 | 2.856 | 184 | 64.4258
23 | 15.5142 | 1 | 2.856 | 184 | 64.4258
22.5 | 15.3317 | 1 | 2.856 | 184 | 64.4258
20.5 | 14.3927 | 1 | 2.856 | 184 | 64.4258
20.2 | 14.4266 | 1 | 2.856 | 184 | 64.4258
19.9 | 14.5642 | 1 | 2.856 | 184 | 64.4258
19.3 | 14.1847 | 1 | 2.856 | 184 | 64.4258
17.9 | 13.7504 | 1 | 2.856 | 184 | 64.4258
16.7 | 13.6559 | 1 | 2.856 | 184 | 64.4258
15.4 | 13.2009 | 1 | 2.856 | 184 | 64.4258
14.5 | 12.8429 | 1 | 2.856 | 184 | 64.4258
14.1 | 12.5699 | 1 | 2.856 | 184 | 64.4258
13.6 | 12.4237 | 1 | 2.856 | 184 | 64.4258
13.1 | 12.2199 | 1 | 2.856 | 184 | 64.4258
13.4 | 12.629 | 1 | 2.856 | 184 | 64.4258
14.1 | 13.025 | 1 | 2.856 | 184 | 64.4258
14.6 | 13.3963 | 1 | 2.856 | 184 | 64.4258
15.5 | 13.7475 | 1 | 2.856 | 184 | 64.4258
16.1 | 13.8097 | 1 | 2.856 | 184 | 64.4258
17.3 | 13.9423 | 1 | 2.856 | 184 | 64.4258
18.2 | 14.3941 | 1 | 2.856 | 184 | 64.4258
19.3 | 14.4936 | 1 | 2.856 | 184 | 64.4258
20.1 | 14.5385 | 1 | 2.856 | 184 | 64.4258
20.6 | 15.0805 | 1 | 2.856 | 184 | 64.4258
19.5 | 15.2563 | 1 | 2.856 | 184 | 64.4258
21 | 15.6958 | 1 | 2.856 | 184 | 64.4258
19.1 | 14.8384 | 1 | 2.856 | 184 | 64.4258
16.7 | 15.747 | 1 | 2.856 | 184 | 64.4258
16.1 | 15.0977 | 1 | 2.856 | 184 | 64.4258
16.7 | 15.6235 | 1 | 2.856 | 184 | 64.4258
15.8 | 15.233 | 1 | 2.856 | 184 | 64.4258
15.7 | 14.8274 | 1 | 2.856 | 184 | 64.4258
15.9 | 15.1463 | 1 | 2.856 | 184 | 64.4258
15.7 | 15.1342 | 1 | 2.856 | 184 | 64.4258
14.6 | 14.3522 | 1 | 2.856 | 184 | 64.4258
14.7 | 14.2677 | 1 | 2.856 | 184 | 64.4258
14.5 | 14.1916 | 1 | 2.856 | 184 | 64.4258
14.7 | 14.1464 | 1 | 2.856 | 184 | 64.4258
14.7 | 14.0257 | 1 | 2.856 | 184 | 64.4258
14.6 | 13.5127 | 1 | 2.856 | 184 | 64.4258
14.4 | 13.2022 | 1 | 2.856 | 184 | 64.4258
14.8 | 13.4752 | 1 | 2.856 | 184 | 64.4258
15.2 | 13.4599 | 1 | 2.856 | 184 | 64.4258
15.6 | 13.3926 | 1 | 2.856 | 184 | 64.4258
15.9 | 13.5103 | 1 | 2.856 | 184 | 64.4258
17.1 | 14.2518 | 1 | 2.856 | 184 | 64.4258
17 | 14.0487 | 1 | 2.856 | 184 | 64.4258
18.1 | 14.4143 | 1 | 2.856 | 184 | 64.4258
18.8 | 14.5722 | 1 | 2.856 | 184 | 64.4258
19.4 | 14.9567 | 1 | 2.856 | 184 | 64.4258
19.3 | 14.7602 | 1 | 2.856 | 184 | 64.4258
19.3 | 14.7602 | 1 | 2.856 | 184 | 64.4258
19.3 | 14.7602 | 1 | 2.856 | 184 | 64.4258
19 | 14.542 | 1 | 2.856 | 184 | 64.4258
19 | 14.5964 | 1 | 2.856 | 184 | 64.4258
18.5 | 15.3964 | 1 | 2.856 | 184 | 64.4258
17.4 | 13.9337 | 1 | 2.856 | 184 | 64.4258
16 | 13.8889 | 1 | 2.856 | 184 | 64.4258
16.2 | 13.9662 | 1 | 2.856 | 184 | 64.4258
15.6 | 14.0786 | 1 | 2.856 | 184 | 64.4258
15.9 | 14.136 | 1 | 2.856 | 184 | 64.4258
15.1 | 13.9442 | 1 | 2.856 | 184 | 64.4258
15 | 13.7883 | 1 | 2.856 | 184 | 64.4258
14.8 | 13.6519 | 1 | 2.856 | 184 | 64.4258
15.7 | 14.1753 | 1 | 2.856 | 184 | 64.4258
17.1 | 14.9378 | 1 | 2.856 | 184 | 64.4258
18.9 | 15.888 | 1 | 2.856 | 184 | 64.4258
19.3 | 15.9746 | 1 | 2.856 | 184 | 64.4258
20 | 16.1686 | 1 | 2.856 | 184 | 64.4258
20.5 | 16.2331 | 1 | 2.856 | 184 | 64.4258
22.6 | 16.026 | 1 | 2.856 | 184 | 64.4258
23.6 | 16.6325 | 1 | 2.856 | 184 | 64.4258
23.7 | 16.8214 | 1 | 2.856 | 184 | 64.4258
23.4 | 16.6135 | 1 | 2.856 | 184 | 64.4258
23.8 | 15.6305 | 1 | 2.856 | 184 | 64.4258
23.1 | 15.7544 | 1 | 2.856 | 184 | 64.4258
22.1 | 15.1467 | 1 | 2.856 | 184 | 64.4258
21.3 | 14.8982 | 1 | 2.856 | 184 | 64.4258
19.6 | 14.4588 | 1 | 2.856 | 184 | 64.4258
18.1 | 14.0429 | 1 | 2.856 | 184 | 64.4258
16.8 | 13.3262 | 1 | 2.856 | 184 | 64.4258
15.5 | 12.8623 | 1 | 2.856 | 184 | 64.4258
15 | 12.8246 | 1 | 2.856 | 184 | 64.4258
14.2 | 12.5571 | 1 | 2.856 | 184 | 64.4258
14 | 12.5312 | 1 | 2.856 | 184 | 64.4258
13.8 | 12.3381 | 1 | 2.856 | 184 | 64.4258
13.4 | 12.2307 | 1 | 2.856 | 184 | 64.4258
13.6 | 12.5382 | 1 | 2.856 | 184 | 64.4258
14.9 | 13.3999 | 1 | 2.856 | 184 | 64.4258
16.5 | 14.305 | 1 | 2.856 | 184 | 64.4258
18.3 | 15.0382 | 1 | 2.856 | 184 | 64.4258
19.4 | 15.1159 | 1 | 2.856 | 184 | 64.4258
17.7 | 15.6851 | 1 | 2.856 | 184 | 64.4258
20.6 | 15.9861 | 1 | 2.856 | 184 | 64.4258
22.2 | 15.6204 | 1 | 2.856 | 184 | 64.4258
22 | 15.3488 | 1 | 2.856 | 184 | 64.4258
22.6 | 15.5678 | 1 | 2.856 | 184 | 64.4258
15.9 | 14.6022 | 1 | 2.856 | 184 | 64.4258
19.2 | 15.9903 | 1 | 2.856 | 184 | 64.4258
19.1 | 16.0703 | 1 | 2.856 | 184 | 64.4258
18.8 | 15.9046 | 1 | 2.856 | 184 | 64.4258
17.3 | 15.7204 | 1 | 2.856 | 184 | 64.4258
17 | 15.4904 | 1 | 2.856 | 184 | 64.4258
16.7 | 15.1997 | 1 | 2.856 | 184 | 64.4258
16.3 | 14.9916 | 1 | 2.856 | 184 | 64.4258
15.6 | 14.4297 | 1 | 2.856 | 184 | 64.4258
15.5 | 14.2139 | 1 | 2.856 | 184 | 64.4258
15.5 | 13.9796 | 1 | 2.856 | 184 | 64.4258
15.4 | 13.9994 | 1 | 2.856 | 184 | 64.4258
15.2 | 13.9218 | 1 | 2.856 | 184 | 64.4258
15.3 | 14.019 | 1 | 2.856 | 184 | 64.4258
15 | 13.8446 | 1 | 2.856 | 184 | 64.4258
15.6 | 14.1927 | 1 | 2.856 | 184 | 64.4258
16.4 | 14.555 | 1 | 2.856 | 184 | 64.4258
17.1 | 14.6454 | 1 | 2.856 | 184 | 64.4258
18.1 | 14.4657 | 1 | 2.856 | 184 | 64.4258
17.2 | 14.9129 | 1 | 2.856 | 184 | 64.4258
15.5 | 14.3323 | 1 | 2.856 | 184 | 64.4258
16.6 | 14.9243 | 1 | 2.856 | 184 | 64.4258
18.5 | 15.5083 | 1 | 2.856 | 184 | 64.4258
16.4 | 13.7606 | 1 | 2.856 | 184 | 64.4258
19 | 14.9134 | 1 | 2.856 | 184 | 64.4258
16.9 | 14.4569 | 1 | 2.856 | 184 | 64.4258
16.5 | 14.7696 | 1 | 2.856 | 184 | 64.4258
16.7 | 15.2604 | 1 | 2.856 | 184 | 64.4258
16.2 | 15.3198 | 1 | 2.856 | 184 | 64.4258
15.9 | 14.9644 | 1 | 2.856 | 184 | 64.4258
15.1 | 14.0027 | 1 | 2.856 | 184 | 64.4258
14.9 | 13.808 | 1 | 2.856 | 184 | 64.4258
14.6 | 13.6912 | 1 | 2.856 | 184 | 64.4258
15 | 13.906 | 1 | 2.856 | 184 | 64.4258
14.8 | 13.7108 | 1 | 2.856 | 184 | 64.4258
14.7 | 13.6722 | 1 | 2.856 | 184 | 64.4258
14.7 | 13.7309 | 1 | 2.856 | 184 | 64.4258
14.9 | 14.0456 | 1 | 2.856 | 184 | 64.4258
15.2 | 14.043 | 1 | 2.856 | 184 | 64.4258
15.2 | 13.8099 | 1 | 2.856 | 184 | 64.4258
15.3 | 13.4497 | 1 | 2.856 | 184 | 64.4258
15.9 | 13.8541 | 1 | 2.856 | 184 | 64.4258
16.9 | 14.0752 | 1 | 2.856 | 184 | 64.4258
17.7 | 13.9004 | 1 | 2.856 | 184 | 64.4258
19.4 | 14.4001 | 1 | 2.856 | 184 | 64.4258
19.3 | 14.5154 | 1 | 2.856 | 184 | 64.4258
19.4 | 14.6567 | 1 | 2.856 | 184 | 64.4258
20.7 | 15.0935 | 1 | 2.856 | 184 | 64.4258
20.9 | 15.067 | 1 | 2.856 | 184 | 64.4258
22.1 | 15.5085 | 1 | 2.856 | 184 | 64.4258
21.5 | 15.2378 | 1 | 2.856 | 184 | 64.4258
21.6 | 15.127 | 1 | 2.856 | 184 | 64.4258
20 | 14.5779 | 1 | 2.856 | 184 | 64.4258
18.7 | 14.3906 | 1 | 2.856 | 184 | 64.4258
17.6 | 14.0753 | 1 | 2.856 | 184 | 64.4258
16.9 | 13.7496 | 1 | 2.856 | 184 | 64.4258
16.4 | 13.5535 | 1 | 2.856 | 184 | 64.4258
15.4 | 13.3229 | 1 | 2.856 | 184 | 64.4258
14.3 | 12.8832 | 1 | 2.856 | 184 | 64.4258
13.6 | 12.4863 | 1 | 2.856 | 184 | 64.4258
13.4 | 12.2916 | 1 | 2.856 | 184 | 64.4258
12.6 | 11.8475 | 1 | 2.856 | 184 | 64.4258
12.6 | 11.8475 | 1 | 2.856 | 184 | 64.4258
13.1 | 11.9995 | 1 | 2.856 | 184 | 64.4258
13.9 | 12.6091 | 1 | 2.856 | 184 | 64.4258
15.4 | 13.5477 | 1 | 2.856 | 184 | 64.4258
17.5 | 13.7204 | 1 | 2.856 | 184 | 64.4258
18 | 13.5569 | 1 | 2.856 | 184 | 64.4258
18.9 | 13.9091 | 1 | 2.856 | 184 | 64.4258
19.5 | 14.4928 | 1 | 2.856 | 184 | 64.4258
21 | 15.1065 | 1 | 2.856 | 184 | 64.4258
21.9 | 15.5393 | 1 | 2.856 | 184 | 64.4258
22.8 | 16.014 | 1 | 2.856 | 184 | 64.4258
23.2 | 15.6229 | 1 | 2.856 | 184 | 64.4258
24.1 | 16.1873 | 1 | 2.856 | 184 | 64.4258
23.9 | 16.1156 | 1 | 2.856 | 184 | 64.4258
23.1 | 16.2219 | 1 | 2.856 | 184 | 64.4258
21.7 | 16.0268 | 1 | 2.856 | 184 | 64.4258
20.6 | 15.7342 | 1 | 2.856 | 184 | 64.4258
20 | 15.6231 | 1 | 2.856 | 184 | 64.4258
18.7 | 15.822 | 1 | 2.856 | 184 | 64.4258
17.2 | 15.272 | 1 | 2.856 | 184 | 64.4258
16 | 14.8841 | 1 | 2.856 | 184 | 64.4258
17.2 | 15.5693 | 1 | 2.856 | 184 | 64.4258
17.5 | 15.7388 | 1 | 2.856 | 184 | 64.4258
17.7 | 15.6331 | 1 | 2.856 | 184 | 64.4258
17.7 | 15.3399 | 1 | 2.856 | 184 | 64.4258
17.5 | 15.5606 | 1 | 2.856 | 184 | 64.4258
18.1 | 15.9572 | 1 | 2.856 | 184 | 64.4258
19 | 16.3987 | 1 | 2.856 | 184 | 64.4258
20.3 | 17.0921 | 1 | 2.856 | 184 | 64.4258
21.7 | 17.7486 | 1 | 2.856 | 184 | 64.4258
22.5 | 18.1933 | 1 | 2.856 | 184 | 64.4258
21.9 | 17.8748 | 1 | 2.856 | 184 | 64.4258
23 | 18.1277 | 1 | 2.856 | 184 | 64.4258
22.7 | 18.2014 | 1 | 2.856 | 184 | 64.4258
23.5 | 18.6408 | 1 | 2.856 | 184 | 64.4258
24.2 | 18.0215 | 1 | 2.856 | 184 | 64.4258
23.8 | 17.7773 | 1 | 2.856 | 184 | 64.4258
22.5 | 17.4459 | 1 | 2.856 | 184 | 64.4258
22.4 | 17.2442 | 1 | 2.856 | 184 | 64.4258
21.3 | 16.9187 | 1 | 2.856 | 184 | 64.4258
20.2 | 16.7643 | 1 | 2.856 | 184 | 64.4258
19.6 | 16.4361 | 1 | 2.856 | 184 | 64.4258
19.1 | 16.3753 | 1 | 2.856 | 184 | 64.4258
18.5 | 16.2807 | 1 | 2.856 | 184 | 64.4258
17.8 | 16.0891 | 1 | 2.856 | 184 | 64.4258
18.3 | 16.3891 | 1 | 2.856 | 184 | 64.4258
18.1 | 16.3787 | 1 | 2.856 | 184 | 64.4258
17.8 | 16.2716 | 1 | 2.856 | 184 | 64.4258
17.8 | 16.3944 | 1 | 2.856 | 184 | 64.4258
17.5 | 16.2874 | 1 | 2.856 | 184 | 64.4258
18.7 | 16.8351 | 1 | 2.856 | 184 | 64.4258
19.4 | 16.9581 | 1 | 2.856 | 184 | 64.4258
20.3 | 17.3899 | 1 | 2.856 | 184 | 64.4258
21.9 | 17.6996 | 1 | 2.856 | 184 | 64.4258
21.2 | 17.5198 | 1 | 2.856 | 184 | 64.4258
21.6 | 17.4222 | 1 | 2.856 | 184 | 64.4258
21.9 | 17.4674 | 1 | 2.856 | 184 | 64.4258
22 | 17.6164 | 1 | 2.856 | 184 | 64.4258
22.2 | 17.7983 | 1 | 2.856 | 184 | 64.4258
21.8 | 17.1457 | 1 | 2.856 | 184 | 64.4258
22.3 | 17.3179 | 1 | 2.856 | 184 | 64.4258
22 | 17.5 | 1 | 2.856 | 184 | 64.4258
21.4 | 17.0654 | 1 | 2.856 | 184 | 64.4258
20.3 | 16.8551 | 1 | 2.856 | 184 | 64.4258
19.8 | 16.3316 | 1 | 2.856 | 184 | 64.4258
19 | 16.0452 | 1 | 2.856 | 184 | 64.4258
18.1 | 16.0153 | 1 | 2.856 | 184 | 64.4258
17.6 | 15.8346 | 1 | 2.856 | 184 | 64.4258
17.1 | 15.9574 | 1 | 2.856 | 184 | 64.4258
17 | 15.8597 | 1 | 2.856 | 184 | 64.4258
16.5 | 15.4934 | 1 | 2.856 | 184 | 64.4258
16.3 | 15.5431 | 1 | 2.856 | 184 | 64.4258
16.5 | 15.678 | 1 | 2.856 | 184 | 64.4258
17.2 | 15.9934 | 1 | 2.856 | 184 | 64.4258
18.1 | 16.6226 | 1 | 2.856 | 184 | 64.4258
19.2 | 16.9465 | 1 | 2.856 | 184 | 64.4258
19.7 | 17.3022 | 1 | 2.856 | 184 | 64.4258
19.2 | 17.5647 | 1 | 2.856 | 184 | 64.4258
20 | 18.0857 | 1 | 2.856 | 184 | 64.4258
20.8 | 18.0416 | 1 | 2.856 | 184 | 64.4258
22.2 | 17.5651 | 1 | 2.856 | 184 | 64.4258
22.4 | 17.1834 | 1 | 2.856 | 184 | 64.4258
21.8 | 16.7542 | 1 | 2.856 | 184 | 64.4258
21.5 | 17.097 | 1 | 2.856 | 184 | 64.4258
21.7 | 17.0531 | 1 | 2.856 | 184 | 64.4258
21.9 | 16.7874 | 1 | 2.856 | 184 | 64.4258
21.1 | 16.4509 | 1 | 2.856 | 184 | 64.4258
20 | 16.6882 | 1 | 2.856 | 184 | 64.4258
19.6 | 16.964 | 1 | 2.856 | 184 | 64.4258
18.3 | 17.0664 | 1 | 2.856 | 184 | 64.4258
17.7 | 16.6683 | 1 | 2.856 | 184 | 64.4258
17 | 16.2319 | 1 | 2.856 | 184 | 64.4258
16.6 | 15.5297 | 1 | 2.856 | 184 | 64.4258
16.1 | 15.1622 | 1 | 2.856 | 184 | 64.4258
15.4 | 14.7785 | 1 | 2.856 | 184 | 64.4258
15 | 14.4445 | 1 | 2.856 | 184 | 64.4258
14.7 | 14.1481 | 1 | 2.856 | 184 | 64.4258
15.3 | 14.619 | 1 | 2.856 | 184 | 64.4258
15.1 | 14.7885 | 1 | 2.856 | 184 | 64.4258
15.5 | 15.0618 | 1 | 2.856 | 184 | 64.4258
16.8 | 15.4203 | 1 | 2.856 | 184 | 64.4258
18.1 | 16.2539 | 1 | 2.856 | 184 | 64.4258
19.9 | 17.0074 | 1 | 2.856 | 184 | 64.4258
21.8 | 17.3111 | 1 | 2.856 | 184 | 64.4258
21.9 | 17.3438 | 1 | 2.856 | 184 | 64.4258
22.2 | 17.2207 | 1 | 2.856 | 184 | 64.4258
22.8 | 17.5359 | 1 | 2.856 | 184 | 64.4258
22.9 | 17.2927 | 1 | 2.856 | 184 | 64.4258
21.9 | 16.8907 | 1 | 2.856 | 184 | 64.4258
21.1 | 16.6113 | 1 | 2.856 | 184 | 64.4258
20.4 | 16.1402 | 1 | 2.856 | 184 | 64.4258
19.4 | 16.0654 | 1 | 2.856 | 184 | 64.4258
18.6 | 15.7196 | 1 | 2.856 | 184 | 64.4258
18.4 | 15.5891 | 1 | 2.856 | 184 | 64.4258
18.1 | 15.364 | 1 | 2.856 | 184 | 64.4258
17.1 | 15.1115 | 1 | 2.856 | 184 | 64.4258
17.2 | 15.3849 | 1 | 2.856 | 184 | 64.4258
17.3 | 15.7215 | 1 | 2.856 | 184 | 64.4258
17.4 | 15.8177 | 1 | 2.856 | 184 | 64.4258
17.3 | 15.9035 | 1 | 2.856 | 184 | 64.4258
17.3 | 15.9648 | 1 | 2.856 | 184 | 64.4258
17.6 | 16.0119 | 1 | 2.856 | 184 | 64.4258
18 | 16.0342 | 1 | 2.856 | 184 | 64.4258
18.5 | 16.2728 | 1 | 2.856 | 184 | 64.4258
19.2 | 16.5214 | 1 | 2.856 | 184 | 64.4258
20 | 16.6263 | 1 | 2.856 | 184 | 64.4258
20.2 | 16.4073 | 1 | 2.856 | 184 | 64.4258
21.2 | 16.9286 | 1 | 2.856 | 184 | 64.4258
22.6 | 16.6465 | 1 | 2.856 | 184 | 64.4258
23.8 | 17.2217 | 1 | 2.856 | 184 | 64.4258
24 | 16.8743 | 1 | 2.856 | 184 | 64.4258
25 | 17.019 | 1 | 2.856 | 184 | 64.4258
24.7 | 16.9151 | 1 | 2.856 | 184 | 64.4258
23.4 | 16.7686 | 1 | 2.856 | 184 | 64.4258
21.6 | 16.2938 | 1 | 2.856 | 184 | 64.4258
19.8 | 16.1512 | 1 | 2.856 | 184 | 64.4258
19.1 | 15.6734 | 1 | 2.856 | 184 | 64.4258
18.3 | 15.3811 | 1 | 2.856 | 184 | 64.4258
17.4 | 15.0487 | 1 | 2.856 | 184 | 64.4258
16.4 | 14.6746 | 1 | 2.856 | 184 | 64.4258
15.8 | 14.3887 | 1 | 2.856 | 184 | 64.4258
15.4 | 14.177 | 1 | 2.856 | 184 | 64.4258
15.3 | 14.0205 | 1 | 2.856 | 184 | 64.4258
15.8 | 14.2708 | 1 | 2.856 | 184 | 64.4258
16.4 | 14.2115 | 1 | 2.856 | 184 | 64.4258
17 | 14.5544 | 1 | 2.856 | 184 | 64.4258
17.3 | 14.896 | 1 | 2.856 | 184 | 64.4258
18.4 | 14.9677 | 1 | 2.856 | 184 | 64.4258
19.2 | 14.9925 | 1 | 2.856 | 184 | 64.4258
19.5 | 14.6819 | 1 | 2.856 | 184 | 64.4258
20.8 | 15.3708 | 1 | 2.856 | 184 | 64.4258
21.6 | 15.5605 | 1 | 2.856 | 184 | 64.4258
22.3 | 15.8651 | 1 | 2.856 | 184 | 64.4258
23.7 | 16.4626 | 1 | 2.856 | 184 | 64.4258
24.2 | 16.0066 | 1 | 2.856 | 184 | 64.4258
24.7 | 16.1352 | 1 | 2.856 | 184 | 64.4258
24.3 | 15.9922 | 1 | 2.856 | 184 | 64.4258
23.9 | 15.9436 | 1 | 2.856 | 184 | 64.4258
23.3 | 15.6794 | 1 | 2.856 | 184 | 64.4258
22.5 | 15.8316 | 1 | 2.856 | 184 | 64.4258
21.1 | 16.2756 | 1 | 2.856 | 184 | 64.4258
19.4 | 15.7219 | 1 | 2.856 | 184 | 64.4258
17.6 | 14.8917 | 1 | 2.856 | 184 | 64.4258
17.1 | 14.6464 | 1 | 2.856 | 184 | 64.4258
15.9 | 13.9608 | 1 | 2.856 | 184 | 64.4258
15.5 | 13.6917 | 1 | 2.856 | 184 | 64.4258
14 | 12.8136 | 1 | 2.856 | 184 | 64.4258
14 | 12.8136 | 1 | 2.856 | 184 | 64.4258
13.6 | 12.5382 | 1 | 2.856 | 184 | 64.4258
15.3 | 13.9025 | 1 | 2.856 | 184 | 64.4258
16.5 | 14.2489 | 1 | 2.856 | 184 | 64.4258
18.1 | 14.6858 | 1 | 2.856 | 184 | 64.4258
20.3 | 15.2353 | 1 | 2.856 | 184 | 64.4258
21.7 | 15.7462 | 1 | 2.856 | 184 | 64.4258
23.2 | 16.1326 | 1 | 2.856 | 184 | 64.4258
23.9 | 16.3316 | 1 | 2.856 | 184 | 64.4258
25 | 17.161 | 1 | 2.856 | 184 | 64.4258
26.5 | 17.3776 | 1 | 2.856 | 184 | 64.4258
26.7 | 17.4455 | 1 | 2.856 | 184 | 64.4258
26.7 | 17.3975 | 1 | 2.856 | 184 | 64.4258
26.5 | 18.073 | 1 | 2.856 | 184 | 64.4258
25.1 | 17.4496 | 1 | 2.856 | 184 | 64.4258
23.2 | 17.3346 | 1 | 2.856 | 184 | 64.4258
21.5 | 16.9163 | 1 | 2.856 | 184 | 64.4258
19.9 | 16.1842 | 1 | 2.856 | 184 | 64.4258
18.7 | 15.929 | 1 | 2.856 | 184 | 64.4258
17.8 | 15.3688 | 1 | 2.856 | 184 | 64.4258
17 | 14.8981 | 1 | 2.856 | 184 | 64.4258
16.5 | 14.8877 | 1 | 2.856 | 184 | 64.4258
15.9 | 14.6032 | 1 | 2.856 | 184 | 64.4258
15.6 | 14.4898 | 1 | 2.856 | 184 | 64.4258
15.2 | 14.338 | 1 | 2.856 | 184 | 64.4258
15.5 | 14.6324 | 1 | 2.856 | 184 | 64.4258
16.3 | 14.9921 | 1 | 2.856 | 184 | 64.4258
17 | 15.4307 | 1 | 2.856 | 184 | 64.4258
17.5 | 15.7331 | 1 | 2.856 | 184 | 64.4258
19.5 | 16.2742 | 1 | 2.856 | 184 | 64.4258
20.4 | 16.7651 | 1 | 2.856 | 184 | 64.4258
21.1 | 17.1237 | 1 | 2.856 | 184 | 64.4258
22.1 | 17.466 | 1 | 2.856 | 184 | 64.4258
23.4 | 17.8466 | 1 | 2.856 | 184 | 64.4258
23.2 | 17.7235 | 1 | 2.856 | 184 | 64.4258
22.4 | 17.2282 | 1 | 2.856 | 184 | 64.4258
20.5 | 17.1498 | 1 | 2.856 | 184 | 64.4258
20.1 | 16.4279 | 1 | 2.856 | 184 | 64.4258
19.1 | 17.2762 | 1 | 2.856 | 184 | 64.4258
18.8 | 17.0487 | 1 | 2.856 | 184 | 64.4258
19.1 | 17.1521 | 1 | 2.856 | 184 | 64.4258
18.8 | 16.6799 | 1 | 2.856 | 184 | 64.4258
18.3 | 16.9381 | 1 | 2.856 | 184 | 64.4258
18.1 | 17.0581 | 1 | 2.856 | 184 | 64.4258
18.1 | 17.5074 | 1 | 2.856 | 184 | 64.4258
18.5 | 17.8377 | 1 | 2.856 | 184 | 64.4258
18.7 | 17.6461 | 1 | 2.856 | 184 | 64.4258
18.3 | 16.5044 | 1 | 2.856 | 184 | 64.4258
18.1 | 16.4338 | 1 | 2.856 | 184 | 64.4258
18 | 16.5218 | 1 | 2.856 | 184 | 64.4258
18.6 | 17.0419 | 1 | 2.856 | 184 | 64.4258
19.2 | 17.3727 | 1 | 2.856 | 184 | 64.4258
20 | 18.0187 | 1 | 2.856 | 184 | 64.4258
20.1 | 18.2417 | 1 | 2.856 | 184 | 64.4258
21 | 18.3499 | 1 | 2.856 | 184 | 64.4258
21.4 | 18.4812 | 1 | 2.856 | 184 | 64.4258
22.2 | 18.0204 | 1 | 2.856 | 184 | 64.4258
22.7 | 17.8962 | 1 | 2.856 | 184 | 64.4258
21.6 | 17.7618 | 1 | 2.856 | 184 | 64.4258
21.4 | 17.5175 | 1 | 2.856 | 184 | 64.4258
21.4 | 17.6932 | 1 | 2.856 | 184 | 64.4258
21.8 | 17.5353 | 1 | 2.856 | 184 | 64.4258
21.1 | 17.4745 | 1 | 2.856 | 184 | 64.4258
19.9 | 16.825 | 1 | 2.856 | 184 | 64.4258
19.2 | 16.9418 | 1 | 2.856 | 184 | 64.4258
18.4 | 16.5409 | 1 | 2.856 | 184 | 64.4258
18 | 16.7093 | 1 | 2.856 | 184 | 64.4258
17.5 | 16.3465 | 1 | 2.856 | 184 | 64.4258
16.7 | 15.3221 | 1 | 2.856 | 184 | 64.4258
16.1 | 14.8589 | 1 | 2.856 | 184 | 64.4258
15.8 | 14.7464 | 1 | 2.856 | 184 | 64.4258
16 | 14.882 | 1 | 2.856 | 184 | 64.4258
15.7 | 14.47 | 1 | 2.856 | 184 | 64.4258
15.2 | 13.9834 | 1 | 2.856 | 184 | 64.4258
15 | 13.7887 | 1 | 2.856 | 184 | 64.4258
14.8 | 13.5946 | 1 | 2.856 | 184 | 64.4258
17.5 | 14.4111 | 1 | 2.856 | 184 | 64.4258
18.9 | 14.2527 | 1 | 2.856 | 184 | 64.4258
20.2 | 14.1059 | 1 | 2.856 | 184 | 64.4258
21.2 | 13.9351 | 1 | 2.856 | 184 | 64.4258
20.8 | 13.5566 | 1 | 2.856 | 184 | 64.4258
22.3 | 14.7609 | 1 | 2.856 | 184 | 64.4258
23.8 | 14.6638 | 1 | 2.856 | 184 | 64.4258
23.3 | 14.3027 | 1 | 2.856 | 184 | 64.4258
21.9 | 14.6538 | 1 | 2.856 | 184 | 64.4258
20.8 | 14.0955 | 1 | 2.856 | 184 | 64.4258
20.1 | 14.3032 | 1 | 2.856 | 184 | 64.4258
19.3 | 15.0297 | 1 | 2.856 | 184 | 64.4258
18.5 | 14.678 | 1 | 2.856 | 184 | 64.4258
17.8 | 14.4117 | 1 | 2.856 | 184 | 64.4258
17 | 14.6114 | 1 | 2.856 | 184 | 64.4258
16.8 | 14.7078 | 1 | 2.856 | 184 | 64.4258
16.7 | 14.9039 | 1 | 2.856 | 184 | 64.4258
16.7 | 15.2003 | 1 | 2.856 | 184 | 64.4258
17.2 | 15.4439 | 1 | 2.856 | 184 | 64.4258
15.8 | 14.6851 | 1 | 2.856 | 184 | 64.4258
15.4 | 14.2353 | 1 | 2.856 | 184 | 64.4258
15.1 | 14.061 | 1 | 2.856 | 184 | 64.4258
14.9 | 13.748 | 1 | 2.856 | 184 | 64.4258
16.4 | 14.2106 | 1 | 2.856 | 184 | 64.4258
17.6 | 14.7783 | 1 | 2.856 | 184 | 64.4258
18.8 | 14.7862 | 1 | 2.856 | 184 | 64.4258
19.8 | 14.8427 | 1 | 2.856 | 184 | 64.4258
20.4 | 14.4106 | 1 | 2.856 | 184 | 64.4258
21.2 | 14.6641 | 1 | 2.856 | 184 | 64.4258
22.1 | 15.5865 | 1 | 2.856 | 184 | 64.4258
21.3 | 15.3425 | 1 | 2.856 | 184 | 64.4258
23 | 15.3297 | 1 | 2.856 | 184 | 64.4258
23 | 15.7591 | 1 | 2.856 | 184 | 64.4258
21.9 | 15.0167 | 1 | 2.856 | 184 | 64.4258
20.8 | 15.0524 | 1 | 2.856 | 184 | 64.4258
19.7 | 15.0612 | 1 | 2.856 | 184 | 64.4258
18.8 | 14.8343 | 1 | 2.856 | 184 | 64.4258
17.7 | 14.8114 | 1 | 2.856 | 184 | 64.4258
16.6 | 14.5707 | 1 | 2.856 | 184 | 64.4258
16.1 | 14.3818 | 1 | 2.856 | 184 | 64.4258
15.6 | 14.1916 | 1 | 2.856 | 184 | 64.4258
15.4 | 14.233 | 1 | 2.856 | 184 | 64.4258
15.6 | 14.6683 | 1 | 2.856 | 184 | 64.4258
15.2 | 14.4568 | 1 | 2.856 | 184 | 64.4258
15.4 | 14.4719 | 1 | 2.856 | 184 | 64.4258
15.1 | 13.9402 | 1 | 2.856 | 184 | 64.4258
15.4 | 13.7074 | 1 | 2.856 | 184 | 64.4258
16 | 13.4903 | 1 | 2.856 | 184 | 64.4258
16 | 13.2178 | 1 | 2.856 | 184 | 64.4258
18 | 13.48 | 1 | 2.856 | 184 | 64.4258
19.3 | 13.3102 | 1 | 2.856 | 184 | 64.4258
20.2 | 13.8021 | 1 | 2.856 | 184 | 64.4258
19.6 | 13.1517 | 1 | 2.856 | 184 | 64.4258
21.8 | 13.411 | 1 | 2.856 | 184 | 64.4258
22.4 | 13.7279 | 1 | 2.856 | 184 | 64.4258
20.8 | 14.08 | 1 | 2.856 | 184 | 64.4258
16 | 14.0558 | 1 | 2.856 | 184 | 64.4258
17.4 | 14.2545 | 1 | 2.856 | 184 | 64.4258
17.5 | 13.9133 | 1 | 2.856 | 184 | 64.4258
17 | 13.8278 | 1 | 2.856 | 184 | 64.4258
16.9 | 14.0643 | 1 | 2.856 | 184 | 64.4258
16.7 | 14.0988 | 1 | 2.856 | 184 | 64.4258
15.8 | 13.8644 | 1 | 2.856 | 184 | 64.4258
15.4 | 13.7668 | 1 | 2.856 | 184 | 64.4258
15.2 | 13.8633 | 1 | 2.856 | 184 | 64.4258
14.8 | 13.4752 | 1 | 2.856 | 184 | 64.4258
14.3 | 13.5133 | 1 | 2.856 | 184 | 64.4258
13.9 | 13.297 | 1 | 2.856 | 184 | 64.4258
13.8 | 13.2576 | 1 | 2.856 | 184 | 64.4258
13.8 | 13.1392 | 1 | 2.856 | 184 | 64.4258
14.1 | 13.3755 | 1 | 2.856 | 184 | 64.4258
15.3 | 14.0778 | 1 | 2.856 | 184 | 64.4258
15.5 | 14.4511 | 1 | 2.856 | 184 | 64.4258
15.3 | 14.5561 | 1 | 2.856 | 184 | 64.4258
16.9 | 15.5742 | 1 | 2.856 | 184 | 64.4258
18.1 | 15.651 | 1 | 2.856 | 184 | 64.4258
18.4 | 15.4697 | 1 | 2.856 | 184 | 64.4258
19.7 | 15.0081 | 1 | 2.856 | 184 | 64.4258
19.4 | 14.6856 | 1 | 2.856 | 184 | 64.4258
19.5 | 14.6709 | 1 | 2.856 | 184 | 64.4258
19.7 | 13.939 | 1 | 2.856 | 184 | 64.4258
19.4 | 14.6316 | 1 | 2.856 | 184 | 64.4258
18.8 | 14.6694 | 1 | 2.856 | 184 | 64.4258
18.5 | 14.6664 | 1 | 2.856 | 184 | 64.4258
17.9 | 14.9413 | 1 | 2.856 | 184 | 64.4258
16.9 | 15.0923 | 1 | 2.856 | 184 | 64.4258
16.2 | 14.8924 | 1 | 2.856 | 184 | 64.4258
15.5 | 14.6914 | 1 | 2.856 | 184 | 64.4258
15.3 | 14.6772 | 1 | 2.856 | 184 | 64.4258
15.1 | 14.5409 | 1 | 2.856 | 184 | 64.4258
14.2 | 13.8326 | 1 | 2.856 | 184 | 64.4258
15.1 | 14.4799 | 1 | 2.856 | 184 | 64.4258
14.8 | 14.3663 | 1 | 2.856 | 184 | 64.4258
15.5 | 14.813 | 1 | 2.856 | 184 | 64.4258
16.2 | 15.1945 | 1 | 2.856 | 184 | 64.4258
16.9 | 15.5727 | 1 | 2.856 | 184 | 64.4258
17.3 | 15.4765 | 1 | 2.856 | 184 | 64.4258
17.5 | 14.8484 | 1 | 2.856 | 184 | 64.4258
19.3 | 14.9112 | 1 | 2.856 | 184 | 64.4258
20.7 | 14.0834 | 1 | 2.856 | 184 | 64.4258
21.8 | 13.9157 | 1 | 2.856 | 184 | 64.4258
22.3 | 13.9384 | 1 | 2.856 | 184 | 64.4258
22.2 | 13.8572 | 1 | 2.856 | 184 | 64.4258
22.6 | 14.0962 | 1 | 2.856 | 184 | 64.4258
21.4 | 13.5039 | 1 | 2.856 | 184 | 64.4258
21.1 | 13.3008 | 1 | 2.856 | 184 | 64.4258
20.9 | 13.0978 | 1 | 2.856 | 184 | 64.4258
19.6 | 12.6637 | 1 | 2.856 | 184 | 64.4258
18.3 | 12.7253 | 1 | 2.856 | 184 | 64.4258
18.1 | 12.3676 | 1 | 2.856 | 184 | 64.4258
17.1 | 11.9139 | 1 | 2.856 | 184 | 64.4258
16.1 | 11.9747 | 1 | 2.856 | 184 | 64.4258
15.1 | 11.9105 | 1 | 2.856 | 184 | 64.4258
14.8 | 11.889 | 1 | 2.856 | 184 | 64.4258
13.4 | 11.4095 | 1 | 2.856 | 184 | 64.4258
13 | 11.1876 | 1 | 2.856 | 184 | 64.4258
12.5 | 11.0286 | 1 | 2.856 | 184 | 64.4258
12.9 | 11.1985 | 1 | 2.856 | 184 | 64.4258
13.1 | 11.0717 | 1 | 2.856 | 184 | 64.4258
14.4 | 11.5184 | 1 | 2.856 | 184 | 64.4258
16.2 | 12.5656 | 1 | 2.856 | 184 | 64.4258
18.4 | 13.1975 | 1 | 2.856 | 184 | 64.4258
19.8 | 13.2334 | 1 | 2.856 | 184 | 64.4258
20.6 | 13.2387 | 1 | 2.856 | 184 | 64.4258
20.8 | 13.6257 | 1 | 2.856 | 184 | 64.4258
20.8 | 13.7155 | 1 | 2.856 | 184 | 64.4258
21.1 | 13.4758 | 1 | 2.856 | 184 | 64.4258
21 | 13.5707 | 1 | 2.856 | 184 | 64.4258
20.8 | 13.4896 | 1 | 2.856 | 184 | 64.4258
21.2 | 13.7782 | 1 | 2.856 | 184 | 64.4258
20.8 | 13.4896 | 1 | 2.856 | 184 | 64.4258
19.6 | 13.1517 | 1 | 2.856 | 184 | 64.4258
18.6 | 13.0355 | 1 | 2.856 | 184 | 64.4258
17.1 | 12.7757 | 1 | 2.856 | 184 | 64.4258
15.9 | 12.5455 | 1 | 2.856 | 184 | 64.4258
14.9 | 12.6189 | 1 | 2.856 | 184 | 64.4258
13.5 | 11.9921 | 1 | 2.856 | 184 | 64.4258
13 | 11.6746 | 1 | 2.856 | 184 | 64.4258
12.3 | 11.2709 | 1 | 2.856 | 184 | 64.4258
11.9 | 10.5569 | 1 | 2.856 | 184 | 64.4258
10.4 | 9.5782 | 1 | 2.856 | 184 | 64.4258
10.8 | 9.8626 | 1 | 2.856 | 184 | 64.4258
10.8 | 9.6514 | 1 | 2.856 | 184 | 64.4258
12.7 | 10.6412 | 1 | 2.856 | 184 | 64.4258
14.6 | 11.6022 | 1 | 2.856 | 184 | 64.4258
16.5 | 12.5857 | 1 | 2.856 | 184 | 64.4258
18.4 | 12.4489 | 1 | 2.856 | 184 | 64.4258
19.3 | 12.9469 | 1 | 2.856 | 184 | 64.4258
20.7 | 12.4921 | 1 | 2.856 | 184 | 64.4258
21.7 | 12.7396 | 1 | 2.856 | 184 | 64.4258
18.7 | 12.0878 | 1 | 2.856 | 184 | 64.4258
19.3 | 12.5481 | 1 | 2.856 | 184 | 64.4258
20.5 | 12.6943 | 1 | 2.856 | 184 | 64.4258
19.3 | 12.1653 | 1 | 2.856 | 184 | 64.4258
19.4 | 11.8796 | 1 | 2.856 | 184 | 64.4258
18.2 | 11.9706 | 1 | 2.856 | 184 | 64.4258
16.6 | 11.3044 | 1 | 2.856 | 184 | 64.4258
15.6 | 11.6748 | 1 | 2.856 | 184 | 64.4258
14.6 | 11.7079 | 1 | 2.856 | 184 | 64.4258
13.3 | 11.3178 | 1 | 2.856 | 184 | 64.4258
12.9 | 11.2548 | 1 | 2.856 | 184 | 64.4258
12.3 | 11.0536 | 1 | 2.856 | 184 | 64.4258
12.1 | 11.0231 | 1 | 2.856 | 184 | 64.4258
11.9 | 10.9375 | 1 | 2.856 | 184 | 64.4258
11.4 | 10.7777 | 1 | 2.856 | 184 | 64.4258
11.2 | 10.4166 | 1 | 2.856 | 184 | 64.4258
11.9 | 10.9379 | 1 | 2.856 | 184 | 64.4258
13.7 | 12.1886 | 1 | 2.856 | 184 | 64.4258
16.1 | 13.3202 | 1 | 2.856 | 184 | 64.4258
17.5 | 13.8698 | 1 | 2.856 | 184 | 64.4258
19.9 | 13.6093 | 1 | 2.856 | 184 | 64.4258
20.2 | 13.4547 | 1 | 2.856 | 184 | 64.4258
20.2 | 13.6368 | 1 | 2.856 | 184 | 64.4258
21 | 14.0365 | 1 | 2.856 | 184 | 64.4258
22.5 | 14.2992 | 1 | 2.856 | 184 | 64.4258
21.4 | 13.9203 | 1 | 2.856 | 184 | 64.4258
21.2 | 13.7984 | 1 | 2.856 | 184 | 64.4258
20.9 | 13.6371 | 1 | 2.856 | 184 | 64.4258
20.8 | 13.4658 | 1 | 2.856 | 184 | 64.4258
19.2 | 13.5258 | 1 | 2.856 | 184 | 64.4258
17.8 | 13.419 | 1 | 2.856 | 184 | 64.4258
16.6 | 13.1489 | 1 | 2.856 | 184 | 64.4258
15.9 | 12.9747 | 1 | 2.856 | 184 | 64.4258
16.5 | 12.699 | 1 | 2.856 | 184 | 64.4258
15.7 | 13.1104 | 1 | 2.856 | 184 | 64.4258
15.1 | 13.1456 | 1 | 2.856 | 184 | 64.4258
14.4 | 12.9216 | 1 | 2.856 | 184 | 64.4258
14.1 | 12.4649 | 1 | 2.856 | 184 | 64.4258
13.5 | 11.9983 | 1 | 2.856 | 184 | 64.4258
13.4 | 12.0672 | 1 | 2.856 | 184 | 64.4258
13.9 | 12.6075 | 1 | 2.856 | 184 | 64.4258
15.5 | 13.5848 | 1 | 2.856 | 184 | 64.4258
17.5 | 14.471 | 1 | 2.856 | 184 | 64.4258
19 | 14.3495 | 1 | 2.856 | 184 | 64.4258
21 | 14.5171 | 1 | 2.856 | 184 | 64.4258
21.7 | 14.2739 | 1 | 2.856 | 184 | 64.4258
22.3 | 14.1052 | 1 | 2.856 | 184 | 64.4258
23.2 | 14.6215 | 1 | 2.856 | 184 | 64.4258
22.8 | 14.2122 | 1 | 2.856 | 184 | 64.4258
23.1 | 14.6706 | 1 | 2.856 | 184 | 64.4258
22.5 | 14.3991 | 1 | 2.856 | 184 | 64.4258
21.6 | 14.0981 | 1 | 2.856 | 184 | 64.4258
20.3 | 13.8218 | 1 | 2.856 | 184 | 64.4258
18.9 | 13.2715 | 1 | 2.856 | 184 | 64.4258
17.9 | 13.165 | 1 | 2.856 | 184 | 64.4258
17.1 | 13.1973 | 1 | 2.856 | 184 | 64.4258
16.4 | 13.4983 | 1 | 2.856 | 184 | 64.4258
15.7 | 13.4408 | 1 | 2.856 | 184 | 64.4258
15.1 | 13.2029 | 1 | 2.856 | 184 | 64.4258
14.4 | 12.9228 | 1 | 2.856 | 184 | 64.4258
13.9 | 12.7211 | 1 | 2.856 | 184 | 64.4258
13.5 | 12.6155 | 1 | 2.856 | 184 | 64.4258
13.1 | 12.2811 | 1 | 2.856 | 184 | 64.4258
12.8 | 12.0433 | 1 | 2.856 | 184 | 64.4258
13 | 12.1263 | 1 | 2.856 | 184 | 64.4258
14.8 | 13.5386 | 1 | 2.856 | 184 | 64.4258
17.3 | 15.0175 | 1 | 2.856 | 184 | 64.4258
19.7 | 15.8442 | 1 | 2.856 | 184 | 64.4258
22.1 | 16.3277 | 1 | 2.856 | 184 | 64.4258
23.4 | 16.3791 | 1 | 2.856 | 184 | 64.4258
24.7 | 15.9809 | 1 | 2.856 | 184 | 64.4258
25.2 | 15.3264 | 1 | 2.856 | 184 | 64.4258
26.3 | 15.6881 | 1 | 2.856 | 184 | 64.4258
26.6 | 15.5546 | 1 | 2.856 | 184 | 64.4258
27 | 15.8567 | 1 | 2.856 | 184 | 64.4258
26.2 | 15.6892 | 1 | 2.856 | 184 | 64.4258
25.1 | 15.2439 | 1 | 2.856 | 184 | 64.4258
23.4 | 15.8336 | 1 | 2.856 | 184 | 64.4258
21 | 15.1524 | 1 | 2.856 | 184 | 64.4258
19.8 | 14.4999 | 1 | 2.856 | 184 | 64.4258
19.7 | 14.2123 | 1 | 2.856 | 184 | 64.4258
18.5 | 14.2079 | 1 | 2.856 | 184 | 64.4258
17.6 | 13.5991 | 1 | 2.856 | 184 | 64.4258
17 | 13.4672 | 1 | 2.856 | 184 | 64.4258
16.6 | 13.9028 | 1 | 2.856 | 184 | 64.4258
15.7 | 13.3837 | 1 | 2.856 | 184 | 64.4258
15.3 | 12.8961 | 1 | 2.856 | 184 | 64.4258
15.1 | 13.0901 | 1 | 2.856 | 184 | 64.4258
15.7 | 13.6624 | 1 | 2.856 | 184 | 64.4258
17.5 | 13.9791 | 1 | 2.856 | 184 | 64.4258
19.3 | 13.3782 | 1 | 2.856 | 184 | 64.4258
21.8 | 14.6242 | 1 | 2.856 | 184 | 64.4258
23.2 | 15.4258 | 1 | 2.856 | 184 | 64.4258
24.6 | 15.5263 | 1 | 2.856 | 184 | 64.4258
25.1 | 16.7677 | 1 | 2.856 | 184 | 64.4258
25.3 | 16.041 | 1 | 2.856 | 184 | 64.4258
25.2 | 16.187 | 1 | 2.856 | 184 | 64.4258
24.6 | 15.0829 | 1 | 2.856 | 184 | 64.4258
24 | 13.8842 | 1 | 2.856 | 184 | 64.4258
22.3 | 15.0772 | 1 | 2.856 | 184 | 64.4258
20.5 | 15.9535 | 1 | 2.856 | 184 | 64.4258
19.6 | 16.1345 | 1 | 2.856 | 184 | 64.4258
19.1 | 16.4248 | 1 | 2.856 | 184 | 64.4258
19 | 16.6281 | 1 | 2.856 | 184 | 64.4258
19.3 | 16.8527 | 1 | 2.856 | 184 | 64.4258
18.7 | 17.0124 | 1 | 2.856 | 184 | 64.4258
18.8 | 16.9842 | 1 | 2.856 | 184 | 64.4258
18.6 | 16.6063 | 1 | 2.856 | 184 | 64.4258
18.6 | 16.424 | 1 | 2.856 | 184 | 64.4258
19.5 | 16.1515 | 1 | 2.856 | 184 | 64.4258
19.7 | 16.2213 | 1 | 2.856 | 184 | 64.4258
19.5 | 16.2081 | 1 | 2.856 | 184 | 64.4258
20.3 | 17.1946 | 1 | 2.856 | 184 | 64.4258
19.6 | 17.1961 | 1 | 2.856 | 184 | 64.4258
19.3 | 17.1548 | 1 | 2.856 | 184 | 64.4258
19.7 | 16.9282 | 1 | 2.856 | 184 | 64.4258
18.3 | 16.6249 | 1 | 2.856 | 184 | 64.4258
17.9 | 16.5463 | 1 | 2.856 | 184 | 64.4258
17.7 | 16.4137 | 1 | 2.856 | 184 | 64.4258
18 | 16.8949 | 1 | 2.856 | 184 | 64.4258
18.5 | 17.1304 | 1 | 2.856 | 184 | 64.4258
18.5 | 17.5125 | 1 | 2.856 | 184 | 64.4258
18.3 | 16.9981 | 1 | 2.856 | 184 | 64.4258
18.6 | 17.5463 | 1 | 2.856 | 184 | 64.4258
18.9 | 17.5836 | 1 | 2.856 | 184 | 64.4258
18.5 | 17.3843 | 1 | 2.856 | 184 | 64.4258
18 | 17.2137 | 1 | 2.856 | 184 | 64.4258
17.8 | 17.0809 | 1 | 2.856 | 184 | 64.4258
17.2 | 16.553 | 1 | 2.856 | 184 | 64.4258
16.1 | 15.1587 | 1 | 2.856 | 184 | 64.4258
15 | 14.1404 | 1 | 2.856 | 184 | 64.4258
14.1 | 13.3755 | 1 | 2.856 | 184 | 64.4258
13.7 | 13.1586 | 1 | 2.856 | 184 | 64.4258
14 | 13.3361 | 1 | 2.856 | 184 | 64.4258
14.1 | 13.494 | 1 | 2.856 | 184 | 64.4258
13.6 | 13.1191 | 1 | 2.856 | 184 | 64.4258
13.9 | 13.297 | 1 | 2.856 | 184 | 64.4258
14.4 | 13.6712 | 1 | 2.856 | 184 | 64.4258
14.9 | 13.8652 | 1 | 2.856 | 184 | 64.4258
15.6 | 14.4297 | 1 | 2.856 | 184 | 64.4258
16.2 | 14.598 | 1 | 2.856 | 184 | 64.4258
17.3 | 14.9519 | 1 | 2.856 | 184 | 64.4258
19.6 | 15.573 | 1 | 2.856 | 184 | 64.4258
20.8 | 14.96 | 1 | 2.856 | 184 | 64.4258
21.2 | 13.9661 | 1 | 2.856 | 184 | 64.4258
20.1 | 13.5849 | 1 | 2.856 | 184 | 64.4258
16.5 | 14.7703 | 1 | 2.856 | 184 | 64.4258
17.8 | 15.196 | 1 | 2.856 | 184 | 64.4258
17.5 | 14.5732 | 1 | 2.856 | 184 | 64.4258
16.9 | 14.1219 | 1 | 2.856 | 184 | 64.4258
16.6 | 14.2888 | 1 | 2.856 | 184 | 64.4258
16.3 | 13.6696 | 1 | 2.856 | 184 | 64.4258
15.6 | 13.3397 | 1 | 2.856 | 184 | 64.4258
14.8 | 12.5812 | 1 | 2.856 | 184 | 64.4258
14.1 | 12.629 | 1 | 2.856 | 184 | 64.4258
13.8 | 12.2844 | 1 | 2.856 | 184 | 64.4258
13 | 11.8428 | 1 | 2.856 | 184 | 64.4258
13.2 | 12.0372 | 1 | 2.856 | 184 | 64.4258
12 | 11.2003 | 1 | 2.856 | 184 | 64.4258
12.1 | 11.1322 | 1 | 2.856 | 184 | 64.4258
12.6 | 11.399 | 1 | 2.856 | 184 | 64.4258
13 | 11.5678 | 1 | 2.856 | 184 | 64.4258
15 | 12.7172 | 1 | 2.856 | 184 | 64.4258
16.8 | 13.5944 | 1 | 2.856 | 184 | 64.4258
17.5 | 13.0939 | 1 | 2.856 | 184 | 64.4258
16.5 | 13.97 | 1 | 2.856 | 184 | 64.4258
17.1 | 14.2562 | 1 | 2.856 | 184 | 64.4258
18.5 | 14.8946 | 1 | 2.856 | 184 | 64.4258
19.2 | 14.5687 | 1 | 2.856 | 184 | 64.4258
18.6 | 14.6602 | 1 | 2.856 | 184 | 64.4258
19.4 | 14.3867 | 1 | 2.856 | 184 | 64.4258
19 | 13.732 | 1 | 2.856 | 184 | 64.4258
18.6 | 13.7252 | 1 | 2.856 | 184 | 64.4258
17.8 | 13.114 | 1 | 2.856 | 184 | 64.4258
17 | 12.7441 | 1 | 2.856 | 184 | 64.4258
15.9 | 12.3479 | 1 | 2.856 | 184 | 64.4258
15.5 | 12.1345 | 1 | 2.856 | 184 | 64.4258
14.1 | 12.1344 | 1 | 2.856 | 184 | 64.4258
13 | 11.1393 | 1 | 2.856 | 184 | 64.4258
12.5 | 11.1399 | 1 | 2.856 | 184 | 64.4258
11.9 | 10.7208 | 1 | 2.856 | 184 | 64.4258
11.8 | 10.8403 | 1 | 2.856 | 184 | 64.4258
11.4 | 10.5584 | 1 | 2.856 | 184 | 64.4258
10.9 | 10.3955 | 1 | 2.856 | 184 | 64.4258
11.3 | 10.5699 | 1 | 2.856 | 184 | 64.4258
11.8 | 10.8954 | 1 | 2.856 | 184 | 64.4258
13.8 | 12.3969 | 1 | 2.856 | 184 | 64.4258
16.3 | 13.4544 | 1 | 2.856 | 184 | 64.4258
17.7 | 13.7895 | 1 | 2.856 | 184 | 64.4258
18.5 | 13.7421 | 1 | 2.856 | 184 | 64.4258
19.4 | 13.7964 | 1 | 2.856 | 184 | 64.4258
19.8 | 13.8556 | 1 | 2.856 | 184 | 64.4258
20 | 13.8382 | 1 | 2.856 | 184 | 64.4258
20.1 | 13.4606 | 1 | 2.856 | 184 | 64.4258
20.8 | 12.8309 | 1 | 2.856 | 184 | 64.4258
21.4 | 13.5714 | 1 | 2.856 | 184 | 64.4258
20.5 | 13.525 | 1 | 2.856 | 184 | 64.4258
19.4 | 13.3686 | 1 | 2.856 | 184 | 64.4258
18.4 | 13.1617 | 1 | 2.856 | 184 | 64.4258
17.3 | 12.7698 | 1 | 2.856 | 184 | 64.4258
16.2 | 12.3728 | 1 | 2.856 | 184 | 64.4258
15.1 | 12.0217 | 1 | 2.856 | 184 | 64.4258
14.6 | 12.0747 | 1 | 2.856 | 184 | 64.4258
14.4 | 12.8641 | 1 | 2.856 | 184 | 64.4258
13.8 | 12.5654 | 1 | 2.856 | 184 | 64.4258
13.5 | 12.2741 | 1 | 2.856 | 184 | 64.4258
13.1 | 11.9972 | 1 | 2.856 | 184 | 64.4258
13.5 | 11.8325 | 1 | 2.856 | 184 | 64.4258
13 | 11.1929 | 1 | 2.856 | 184 | 64.4258
13.9 | 11.8375 | 1 | 2.856 | 184 | 64.4258
15.1 | 12.1245 | 1 | 2.856 | 184 | 64.4258
17.3 | 12.87 | 1 | 2.856 | 184 | 64.4258
18.7 | 12.4986 | 1 | 2.856 | 184 | 64.4258
19.7 | 13.2572 | 1 | 2.856 | 184 | 64.4258
20.2 | 13.1848 | 1 | 2.856 | 184 | 64.4258
21.2 | 13.4074 | 1 | 2.856 | 184 | 64.4258
21.1 | 12.7866 | 1 | 2.856 | 184 | 64.4258
21.7 | 13.1067 | 1 | 2.856 | 184 | 64.4258
20.9 | 12.9913 | 1 | 2.856 | 184 | 64.4258
21 | 12.6633 | 1 | 2.856 | 184 | 64.4258
19.7 | 13.6199 | 1 | 2.856 | 184 | 64.4258
17.5 | 13.1942 | 1 | 2.856 | 184 | 64.4258
16.1 | 12.787 | 1 | 2.856 | 184 | 64.4258
15.2 | 12.5286 | 1 | 2.856 | 184 | 64.4258
14.5 | 12.3508 | 1 | 2.856 | 184 | 64.4258
13.2 | 11.651 | 1 | 2.856 | 184 | 64.4258
12.9 | 11.58 | 1 | 2.856 | 184 | 64.4258
12.9 | 11.58 | 1 | 2.856 | 184 | 64.4258
12.1 | 11.187 | 1 | 2.856 | 184 | 64.4258
11.4 | 10.6668 | 1 | 2.856 | 184 | 64.4258
10.9 | 10.2847 | 1 | 2.856 | 184 | 64.4258
11 | 10.3284 | 1 | 2.856 | 184 | 64.4258
11.4 | 10.7213 | 1 | 2.856 | 184 | 64.4258
12.5 | 11.6332 | 1 | 2.856 | 184 | 64.4258
15 | 12.8769 | 1 | 2.856 | 184 | 64.4258
16 | 13.1122 | 1 | 2.856 | 184 | 64.4258
17.9 | 13.647 | 1 | 2.856 | 184 | 64.4258
19.3 | 13.9862 | 1 | 2.856 | 184 | 64.4258
20 | 13.7693 | 1 | 2.856 | 184 | 64.4258
21.3 | 14.1272 | 1 | 2.856 | 184 | 64.4258
21.4 | 13.2472 | 1 | 2.856 | 184 | 64.4258
21.3 | 13.7196 | 1 | 2.856 | 184 | 64.4258
20.2 | 14.126 | 1 | 2.856 | 184 | 64.4258
19 | 14.2159 | 1 | 2.856 | 184 | 64.4258
18.7 | 14.0482 | 1 | 2.856 | 184 | 64.4258
17.5 | 14.562 | 1 | 2.856 | 184 | 64.4258
17 | 14.4872 | 1 | 2.856 | 184 | 64.4258
16.6 | 13.9955 | 1 | 2.856 | 184 | 64.4258
15.1 | 13.6457 | 1 | 2.856 | 184 | 64.4258
14.7 | 13.6069 | 1 | 2.856 | 184 | 64.4258
14.7 | 13.5482 | 1 | 2.856 | 184 | 64.4258
14.8 | 14.3042 | 1 | 2.856 | 184 | 64.4258
15.1 | 14.7864 | 1 | 2.856 | 184 | 64.4258
14.7 | 14.0831 | 1 | 2.856 | 184 | 64.4258
14.6 | 13.6251 | 1 | 2.856 | 184 | 64.4258
14.7 | 14.0218 | 1 | 2.856 | 184 | 64.4258
15.3 | 14.4295 | 1 | 2.856 | 184 | 64.4258
15.2 | 14.5134 | 1 | 2.856 | 184 | 64.4258
15 | 14.3158 | 1 | 2.856 | 184 | 64.4258
14.8 | 14.6115 | 1 | 2.856 | 184 | 64.4258
15.5 | 14.9319 | 1 | 2.856 | 184 | 64.4258
16.3 | 15.2849 | 1 | 2.856 | 184 | 64.4258
16.5 | 15.2952 | 1 | 2.856 | 184 | 64.4258
16.3 | 15.0997 | 1 | 2.856 | 184 | 64.4258
17.4 | 15.9864 | 1 | 2.856 | 184 | 64.4258
18 | 14.0662 | 1 | 2.856 | 184 | 64.4258
17.6 | 13.6475 | 1 | 2.856 | 184 | 64.4258
17 | 12.7915 | 1 | 2.856 | 184 | 64.4258
16.3 | 12.5652 | 1 | 2.856 | 184 | 64.4258
15.5 | 12.7227 | 1 | 2.856 | 184 | 64.4258
15.2 | 12.7675 | 1 | 2.856 | 184 | 64.4258
14.4 | 12.3942 | 1 | 2.856 | 184 | 64.4258
13.7 | 12.7984 | 1 | 2.856 | 184 | 64.4258
13 | 12.1129 | 1 | 2.856 | 184 | 64.4258
12.7 | 11.8191 | 1 | 2.856 | 184 | 64.4258
13.2 | 11.5215 | 1 | 2.856 | 184 | 64.4258
13.4 | 11.1745 | 1 | 2.856 | 184 | 64.4258
13.2 | 10.8809 | 1 | 2.856 | 184 | 64.4258
13 | 10.9022 | 1 | 2.856 | 184 | 64.4258
11.7 | 11.0088 | 1 | 2.856 | 184 | 64.4258
12 | 10.9123 | 1 | 2.856 | 184 | 64.4258
12.5 | 10.5867 | 1 | 2.856 | 184 | 64.4258
13.4 | 11.0734 | 1 | 2.856 | 184 | 64.4258
14.5 | 11.1781 | 1 | 2.856 | 184 | 64.4258
15.7 | 11.2921 | 1 | 2.856 | 184 | 64.4258
16.6 | 11.6186 | 1 | 2.856 | 184 | 64.4258
12.8 | 11.3603 | 1 | 2.856 | 184 | 64.4258
15.9 | 12.6779 | 1 | 2.856 | 184 | 64.4258
17 | 12.0216 | 1 | 2.856 | 184 | 64.4258
15.1 | 12.4655 | 1 | 2.856 | 184 | 64.4258
15.5 | 12.5193 | 1 | 2.856 | 184 | 64.4258
16 | 11.1459 | 1 | 2.856 | 184 | 64.4258
15.6 | 11.1634 | 1 | 2.856 | 184 | 64.4258
14.3 | 11.1025 | 1 | 2.856 | 184 | 64.4258
14.2 | 10.7656 | 1 | 2.856 | 184 | 64.4258
13 | 10.4496 | 1 | 2.856 | 184 | 64.4258
12.6 | 10.2778 | 1 | 2.856 | 184 | 64.4258
11.7 | 9.9365 | 1 | 2.856 | 184 | 64.4258
11.4 | 9.7015 | 1 | 2.856 | 184 | 64.4258
11.3 | 9.7606 | 1 | 2.856 | 184 | 64.4258
11.5 | 9.8487 | 1 | 2.856 | 184 | 64.4258
11.4 | 9.961 | 1 | 2.856 | 184 | 64.4258
11.5 | 9.9519 | 1 | 2.856 | 184 | 64.4258
11.4 | 10.0658 | 1 | 2.856 | 184 | 64.4258
11.4 | 10.0664 | 1 | 2.856 | 184 | 64.4258
12.2 | 10.7851 | 1 | 2.856 | 184 | 64.4258
13.2 | 10.9457 | 1 | 2.856 | 184 | 64.4258
14.6 | 11.1326 | 1 | 2.856 | 184 | 64.4258
16 | 11.6684 | 1 | 2.856 | 184 | 64.4258
16.6 | 11.6333 | 1 | 2.856 | 184 | 64.4258
17.2 | 12.1156 | 1 | 2.856 | 184 | 64.4258
17.8 | 12.3126 | 1 | 2.856 | 184 | 64.4258
17.5 | 12.0082 | 1 | 2.856 | 184 | 64.4258
18.3 | 12.4707 | 1 | 2.856 | 184 | 64.4258
17.6 | 12.2359 | 1 | 2.856 | 184 | 64.4258
18.2 | 12.1607 | 1 | 2.856 | 184 | 64.4258
16.5 | 10.5447 | 1 | 2.856 | 184 | 64.4258
14.8 | 10.0647 | 1 | 2.856 | 184 | 64.4258
13.6 | 9.8534 | 1 | 2.856 | 184 | 64.4258
12.5 | 9.1804 | 1 | 2.856 | 184 | 64.4258
12 | 9.3305 | 1 | 2.856 | 184 | 64.4258
11 | 8.879 | 1 | 2.856 | 184 | 64.4258
11.1 | 9.0721 | 1 | 2.856 | 184 | 64.4258
10.3 | 8.8576 | 1 | 2.856 | 184 | 64.4258
10.1 | 8.7661 | 1 | 2.856 | 184 | 64.4258
9.5 | 8.3886 | 1 | 2.856 | 184 | 64.4258
10.7 | 9.3965 | 1 | 2.856 | 184 | 64.4258
9.7 | 8.5829 | 1 | 2.856 | 184 | 64.4258
10.2 | 8.8637 | 1 | 2.856 | 184 | 64.4258
11.1 | 9.8886 | 1 | 2.856 | 184 | 64.4258
13.1 | 10.9146 | 1 | 2.856 | 184 | 64.4258
15.7 | 11.8568 | 1 | 2.856 | 184 | 64.4258
16.9 | 11.5131 | 1 | 2.856 | 184 | 64.4258
17.2 | 11.9553 | 1 | 2.856 | 184 | 64.4258
18 | 12.1059 | 1 | 2.856 | 184 | 64.4258
18.5 | 12.4895 | 1 | 2.856 | 184 | 64.4258
19.3 | 12.5048 | 1 | 2.856 | 184 | 64.4258
19 | 12.2109 | 1 | 2.856 | 184 | 64.4258
18.8 | 12.5661 | 1 | 2.856 | 184 | 64.4258
18.6 | 12.266 | 1 | 2.856 | 184 | 64.4258
17.6 | 11.8987 | 1 | 2.856 | 184 | 64.4258
16 | 11.8414 | 1 | 2.856 | 184 | 64.4258
15.1 | 12.2758 | 1 | 2.856 | 184 | 64.4258
14.1 | 12.132 | 1 | 2.856 | 184 | 64.4258
13.6 | 12.2012 | 1 | 2.856 | 184 | 64.4258
13.4 | 12.0634 | 1 | 2.856 | 184 | 64.4258
11.8 | 11.115 | 1 | 2.856 | 184 | 64.4258
12.7 | 11.9429 | 1 | 2.856 | 184 | 64.4258
13 | 12.2371 | 1 | 2.856 | 184 | 64.4258
13.4 | 12.6296 | 1 | 2.856 | 184 | 64.4258
13.9 | 12.8883 | 1 | 2.856 | 184 | 64.4258
14 | 13.0439 | 1 | 2.856 | 184 | 64.4258
13.7 | 13.2777 | 1 | 2.856 | 184 | 64.4258
14.4 | 13.9712 | 1 | 2.856 | 184 | 64.4258
14.9 | 14.4665 | 1 | 2.856 | 184 | 64.4258
16.1 | 15.4683 | 1 | 2.856 | 184 | 64.4258
16.8 | 15.4188 | 1 | 2.856 | 184 | 64.4258
19 | 15.9808 | 1 | 2.856 | 184 | 64.4258
20.2 | 14.9957 | 1 | 2.856 | 184 | 64.4258
21.1 | 15.0282 | 1 | 2.856 | 184 | 64.4258
21.3 | 14.9054 | 1 | 2.856 | 184 | 64.4258
21.7 | 15.1056 | 1 | 2.856 | 184 | 64.4258
21.5 | 14.9825 | 1 | 2.856 | 184 | 64.4258
20.3 | 14.4351 | 1 | 2.856 | 184 | 64.4258
18.4 | 13.9591 | 1 | 2.856 | 184 | 64.4258
17.2 | 13.7027 | 1 | 2.856 | 184 | 64.4258
16.6 | 13.684 | 1 | 2.856 | 184 | 64.4258
15.9 | 13.2995 | 1 | 2.856 | 184 | 64.4258
14.6 | 12.397 | 1 | 2.856 | 184 | 64.4258
14.4 | 12.2084 | 1 | 2.856 | 184 | 64.4258
12.5 | 11.089 | 1 | 2.856 | 184 | 64.4258
12.5 | 11.749 | 1 | 2.856 | 184 | 64.4258
11.7 | 10.9087 | 1 | 2.856 | 184 | 64.4258
11.2 | 10.6377 | 1 | 2.856 | 184 | 64.4258
10.7 | 10.1449 | 1 | 2.856 | 184 | 64.4258
10.1 | 9.7694 | 1 | 2.856 | 184 | 64.4258
11 | 10.4406 | 1 | 2.856 | 184 | 64.4258
11.7 | 10.9093 | 1 | 2.856 | 184 | 64.4258
13.1 | 12 | 1 | 2.856 | 184 | 64.4258
14.4 | 12.9804 | 1 | 2.856 | 184 | 64.4258
16.7 | 13.4597 | 1 | 2.856 | 184 | 64.4258
19.5 | 14.5439 | 1 | 2.856 | 184 | 64.4258
20.7 | 14.8466 | 1 | 2.856 | 184 | 64.4258
21.9 | 16.5248 | 1 | 2.856 | 184 | 64.4258
23 | 17.1793 | 1 | 2.856 | 184 | 64.4258
23.1 | 16.4266 | 1 | 2.856 | 184 | 64.4258
24 | 17.2061 | 1 | 2.856 | 184 | 64.4258
23 | 16.3402 | 1 | 2.856 | 184 | 64.4258
21.7 | 16.7261 | 1 | 2.856 | 184 | 64.4258
20.3 | 15.6803 | 1 | 2.856 | 184 | 64.4258
18.7 | 15.1464 | 1 | 2.856 | 184 | 64.4258
17.7 | 14.6612 | 1 | 2.856 | 184 | 64.4258
17 | 13.7375 | 1 | 2.856 | 184 | 64.4258
15.5 | 13.4198 | 1 | 2.856 | 184 | 64.4258
14.9 | 13.294 | 1 | 2.856 | 184 | 64.4258
14.8 | 13.2536 | 1 | 2.856 | 184 | 64.4258
14.2 | 12.9 | 1 | 2.856 | 184 | 64.4258
13.9 | 12.7221 | 1 | 2.856 | 184 | 64.4258
13.2 | 12.3229 | 1 | 2.856 | 184 | 64.4258
13.6 | 12.4867 | 1 | 2.856 | 184 | 64.4258
13.6 | 12.6002 | 1 | 2.856 | 184 | 64.4258
14.6 | 13.3453 | 1 | 2.856 | 184 | 64.4258
17.2 | 15.2741 | 1 | 2.856 | 184 | 64.4258
19.7 | 16.7076 | 1 | 2.856 | 184 | 64.4258
21.6 | 17.5422 | 1 | 2.856 | 184 | 64.4258
23.8 | 17.0351 | 1 | 2.856 | 184 | 64.4258
24.6 | 16.9571 | 1 | 2.856 | 184 | 64.4258
25.6 | 17.9594 | 1 | 2.856 | 184 | 64.4258
26 | 17.9392 | 1 | 2.856 | 184 | 64.4258
26.2 | 18.579 | 1 | 2.856 | 184 | 64.4258
25.7 | 16.9917 | 1 | 2.856 | 184 | 64.4258
24.9 | 16.3777 | 1 | 2.856 | 184 | 64.4258
23.4 | 15.7434 | 1 | 2.856 | 184 | 64.4258
21.4 | 15.5558 | 1 | 2.856 | 184 | 64.4258
19 | 15.3089 | 1 | 2.856 | 184 | 64.4258
18.3 | 15.3876 | 1 | 2.856 | 184 | 64.4258
17.4 | 15.2281 | 1 | 2.856 | 184 | 64.4258
17.3 | 15.2488 | 1 | 2.856 | 184 | 64.4258
16 | 14.4676 | 1 | 2.856 | 184 | 64.4258
16.1 | 14.2732 | 1 | 2.856 | 184 | 64.4258
16 | 14.0618 | 1 | 2.856 | 184 | 64.4258
15.2 | 13.8094 | 1 | 2.856 | 184 | 64.4258
15.8 | 13.8704 | 1 | 2.856 | 184 | 64.4258
15.4 | 13.2079 | 1 | 2.856 | 184 | 64.4258
16.2 | 13.8008 | 1 | 2.856 | 184 | 64.4258
16.4 | 13.9891 | 1 | 2.856 | 184 | 64.4258
18.9 | 15.4351 | 1 | 2.856 | 184 | 64.4258
20.1 | 15.4358 | 1 | 2.856 | 184 | 64.4258
20.7 | 15.4947 | 1 | 2.856 | 184 | 64.4258
21.7 | 15.3997 | 1 | 2.856 | 184 | 64.4258
23.6 | 16.686 | 1 | 2.856 | 184 | 64.4258
24.5 | 17.7279 | 1 | 2.856 | 184 | 64.4258
25.5 | 17.7471 | 1 | 2.856 | 184 | 64.4258
25.1 | 17.2539 | 1 | 2.856 | 184 | 64.4258
24 | 16.7723 | 1 | 2.856 | 184 | 64.4258
22.7 | 16.3151 | 1 | 2.856 | 184 | 64.4258
21.7 | 15.7505 | 1 | 2.856 | 184 | 64.4258
21.2 | 15.9901 | 1 | 2.856 | 184 | 64.4258
19.9 | 16.2439 | 1 | 2.856 | 184 | 64.4258
19.8 | 16.5549 | 1 | 2.856 | 184 | 64.4258
18.5 | 15.7995 | 1 | 2.856 | 184 | 64.4258
18.3 | 16.383 | 1 | 2.856 | 184 | 64.4258
18 | 16.2766 | 1 | 2.856 | 184 | 64.4258
16.8 | 15.7233 | 1 | 2.856 | 184 | 64.4258
16 | 14.9415 | 1 | 2.856 | 184 | 64.4258
15.3 | 14.1979 | 1 | 2.856 | 184 | 64.4258
14.6 | 13.8092 | 1 | 2.856 | 184 | 64.4258
14.1 | 13.3181 | 1 | 2.856 | 184 | 64.4258
13.8 | 12.9076 | 1 | 2.856 | 184 | 64.4258
15 | 13.5569 | 1 | 2.856 | 184 | 64.4258
16.1 | 13.9284 | 1 | 2.856 | 184 | 64.4258
17.1 | 14.481 | 1 | 2.856 | 184 | 64.4258
18.5 | 15.0088 | 1 | 2.856 | 184 | 64.4258
20.1 | 15.6532 | 1 | 2.856 | 184 | 64.4258
20.5 | 15.2163 | 1 | 2.856 | 184 | 64.4258
21.3 | 15.4595 | 1 | 2.856 | 184 | 64.4258
21.8 | 15.6423 | 1 | 2.856 | 184 | 64.4258
22.3 | 15.8262 | 1 | 2.856 | 184 | 64.4258
22.2 | 15.94 | 1 | 2.856 | 184 | 64.4258
22 | 15.5167 | 1 | 2.856 | 184 | 64.4258
20.8 | 15.3808 | 1 | 2.856 | 184 | 64.4258
19.1 | 14.8615 | 1 | 2.856 | 184 | 64.4258
17.8 | 14.4182 | 1 | 2.856 | 184 | 64.4258
16.6 | 13.793 | 1 | 2.856 | 184 | 64.4258
15.8 | 13.6463 | 1 | 2.856 | 184 | 64.4258
15 | 12.9403 | 1 | 2.856 | 184 | 64.4258
14.3 | 12.882 | 1 | 2.856 | 184 | 64.4258
13.3 | 12.0819 | 1 | 2.856 | 184 | 64.4258
12.5 | 11.6368 | 1 | 2.856 | 184 | 64.4258
11.9 | 11.1601 | 1 | 2.856 | 184 | 64.4258
11.3 | 10.736 | 1 | 2.856 | 184 | 64.4258
11 | 10.4403 | 1 | 2.856 | 184 | 64.4258
11.3 | 10.9589 | 1 | 2.856 | 184 | 64.4258
12 | 11.4261 | 1 | 2.856 | 184 | 64.4258
13.4 | 12.4041 | 1 | 2.856 | 184 | 64.4258
15.9 | 14.1408 | 1 | 2.856 | 184 | 64.4258
18.8 | 15.1259 | 1 | 2.856 | 184 | 64.4258
19.8 | 15.7143 | 1 | 2.856 | 184 | 64.4258
21.6 | 15.7828 | 1 | 2.856 | 184 | 64.4258
22.4 | 16.382 | 1 | 2.856 | 184 | 64.4258
22.9 | 16.2998 | 1 | 2.856 | 184 | 64.4258
21.8 | 15.9566 | 1 | 2.856 | 184 | 64.4258
20.6 | 16.1672 | 1 | 2.856 | 184 | 64.4258
20 | 15.676 | 1 | 2.856 | 184 | 64.4258
19.8 | 15.1703 | 1 | 2.856 | 184 | 64.4258
17.8 | 13.9904 | 1 | 2.856 | 184 | 64.4258
17.8 | 14.639 | 1 | 2.856 | 184 | 64.4258
16.6 | 14.0135 | 1 | 2.856 | 184 | 64.4258
15.8 | 13.8719 | 1 | 2.856 | 184 | 64.4258
15 | 13.5018 | 1 | 2.856 | 184 | 64.4258
14.5 | 13.1889 | 1 | 2.856 | 184 | 64.4258
13.8 | 12.7939 | 1 | 2.856 | 184 | 64.4258
13.8 | 12.7939 | 1 | 2.856 | 184 | 64.4258
13.6 | 12.428 | 1 | 2.856 | 184 | 64.4258
13 | 12.1252 | 1 | 2.856 | 184 | 64.4258
12.6 | 11.8463 | 1 | 2.856 | 184 | 64.4258
13.5 | 12.2746 | 1 | 2.856 | 184 | 64.4258
14 | 12.8169 | 1 | 2.856 | 184 | 64.4258
14.5 | 13.1883 | 1 | 2.856 | 184 | 64.4258
14.7 | 13.2683 | 1 | 2.856 | 184 | 64.4258
15.8 | 14.2743 | 1 | 2.856 | 184 | 64.4258
16.5 | 14.6573 | 1 | 2.856 | 184 | 64.4258
15.5 | 14.3952 | 1 | 2.856 | 184 | 64.4258
17.9 | 14.7866 | 1 | 2.856 | 184 | 64.4258
18.5 | 13.3992 | 1 | 2.856 | 184 | 64.4258
19.1 | 12.6636 | 1 | 2.856 | 184 | 64.4258
18.9 | 12.1495 | 1 | 2.856 | 184 | 64.4258
18.8 | 12.1508 | 1 | 2.856 | 184 | 64.4258
17.4 | 11.9238 | 1 | 2.856 | 184 | 64.4258
16 | 11.7575 | 1 | 2.856 | 184 | 64.4258
15 | 11.385 | 1 | 2.856 | 184 | 64.4258
12 | 10.1381 | 1 | 2.856 | 184 | 64.4258
10.7 | 9.0502 | 1 | 2.856 | 184 | 64.4258
9.7 | 8.489 | 1 | 2.856 | 184 | 64.4258
9.1 | 7.9093 | 1 | 2.856 | 184 | 64.4258
8.6 | 7.4743 | 1 | 2.856 | 184 | 64.4258
8.4 | 7.4266 | 1 | 2.856 | 184 | 64.4258
8.5 | 7.5238 | 1 | 2.856 | 184 | 64.4258
9.7 | 8.9477 | 1 | 2.856 | 184 | 64.4258
9.9 | 9.4622 | 1 | 2.856 | 184 | 64.4258
10.8 | 10.025 | 1 | 2.856 | 184 | 64.4258
11.5 | 10.4935 | 1 | 2.856 | 184 | 64.4258
12.6 | 11.1819 | 1 | 2.856 | 184 | 64.4258
14.2 | 11.8006 | 1 | 2.856 | 184 | 64.4258
15 | 12.028 | 1 | 2.856 | 184 | 64.4258
16 | 12.59 | 1 | 2.856 | 184 | 64.4258
16.5 | 12.2402 | 1 | 2.856 | 184 | 64.4258
16.3 | 13.0214 | 1 | 2.856 | 184 | 64.4258
16.7 | 13.1789 | 1 | 2.856 | 184 | 64.4258
16.9 | 12.5483 | 1 | 2.856 | 184 | 64.4258
17.2 | 11.2912 | 1 | 2.856 | 184 | 64.4258
17.1 | 11.1633 | 1 | 2.856 | 184 | 64.4258
15.8 | 10.5202 | 1 | 2.856 | 184 | 64.4258
14.6 | 9.9538 | 1 | 2.856 | 184 | 64.4258
14.2 | 9.7765 | 1 | 2.856 | 184 | 64.4258
13.1 | 9.5541 | 1 | 2.856 | 184 | 64.4258
12.1 | 9.1962 | 1 | 2.856 | 184 | 64.4258
10.5 | 8.2726 | 1 | 2.856 | 184 | 64.4258
9.4 | 7.9482 | 1 | 2.856 | 184 | 64.4258
9.6 | 8.2881 | 1 | 2.856 | 184 | 64.4258
10.2 | 8.6656 | 1 | 2.856 | 184 | 64.4258
10.5 | 8.8524 | 1 | 2.856 | 184 | 64.4258
10.6 | 8.9479 | 1 | 2.856 | 184 | 64.4258
10.6 | 8.8486 | 1 | 2.856 | 184 | 64.4258
10.9 | 8.7907 | 1 | 2.856 | 184 | 64.4258
11 | 8.8849 | 1 | 2.856 | 184 | 64.4258
11.5 | 9.3069 | 1 | 2.856 | 184 | 64.4258
12 | 9.7775 | 1 | 2.856 | 184 | 64.4258
13 | 10.1223 | 1 | 2.856 | 184 | 64.4258
14.1 | 10.602 | 1 | 2.856 | 184 | 64.4258
14.9 | 10.7126 | 1 | 2.856 | 184 | 64.4258
11.4 | 10.0758 | 1 | 2.856 | 184 | 64.4258
13.6 | 11.1831 | 1 | 2.856 | 184 | 64.4258
14 | 10.7046 | 1 | 2.856 | 184 | 64.4258
13.1 | 10.563 | 1 | 2.856 | 184 | 64.4258
13.6 | 10.6307 | 1 | 2.856 | 184 | 64.4258
13.8 | 10.1926 | 1 | 2.856 | 184 | 64.4258
12.1 | 9.6783 | 1 | 2.856 | 184 | 64.4258
11.1 | 9.3287 | 1 | 2.856 | 184 | 64.4258
12.1 | 9.6794 | 1 | 2.856 | 184 | 64.4258
11.9 | 9.2532 | 1 | 2.856 | 184 | 64.4258
12.1 | 9.3438 | 1 | 2.856 | 184 | 64.4258
11.7 | 9.0688 | 1 | 2.856 | 184 | 64.4258
11.5 | 8.8364 | 1 | 2.856 | 184 | 64.4258
11.1 | 8.8893 | 1 | 2.856 | 184 | 64.4258
11.3 | 9.0772 | 1 | 2.856 | 184 | 64.4258
11.3 | 9.0772 | 1 | 2.856 | 184 | 64.4258
11.2 | 8.7934 | 1 | 2.856 | 184 | 64.4258
11.6 | 8.8371 | 1 | 2.856 | 184 | 64.4258
11.6 | 9.3125 | 1 | 2.856 | 184 | 64.4258
12 | 9.5901 | 1 | 2.856 | 184 | 64.4258
12.1 | 9.7827 | 1 | 2.856 | 184 | 64.4258
12.5 | 9.8646 | 1 | 2.856 | 184 | 64.4258
12.3 | 10.1207 | 1 | 2.856 | 184 | 64.4258
13.3 | 10.5596 | 1 | 2.856 | 184 | 64.4258
14.1 | 10.7126 | 1 | 2.856 | 184 | 64.4258
14.3 | 10.5642 | 1 | 2.856 | 184 | 64.4258
13.9 | 10.1569 | 1 | 2.856 | 184 | 64.4258
13.6 | 9.9796 | 1 | 2.856 | 184 | 64.4258
13.7 | 9.9782 | 1 | 2.856 | 184 | 64.4258
13.1 | 9.8029 | 1 | 2.856 | 184 | 64.4258
12.9 | 9.7147 | 1 | 2.856 | 184 | 64.4258
12.7 | 9.7201 | 1 | 2.856 | 184 | 64.4258
12.4 | 9.7763 | 1 | 2.856 | 184 | 64.4258
12.1 | 9.5944 | 1 | 2.856 | 184 | 64.4258
11.8 | 9.4105 | 1 | 2.856 | 184 | 64.4258
11.5 | 9.4203 | 1 | 2.856 | 184 | 64.4258
11.4 | 9.4241 | 1 | 2.856 | 184 | 64.4258
10.6 | 9.2607 | 1 | 2.856 | 184 | 64.4258
10.6 | 9.06 | 1 | 2.856 | 184 | 64.4258
10.3 | 8.9722 | 1 | 2.856 | 184 | 64.4258
10.1 | 8.88 | 1 | 2.856 | 184 | 64.4258
9.8 | 8.5901 | 1 | 2.856 | 184 | 64.4258
10.7 | 9.2569 | 1 | 2.856 | 184 | 64.4258
12.2 | 10.0331 | 1 | 2.856 | 184 | 64.4258
13.6 | 10.6498 | 1 | 2.856 | 184 | 64.4258
14.5 | 10.8016 | 1 | 2.856 | 184 | 64.4258
14.9 | 10.6518 | 1 | 2.856 | 184 | 64.4258
15.5 | 10.9123 | 1 | 2.856 | 184 | 64.4258
15.5 | 11.0482 | 1 | 2.856 | 184 | 64.4258
15 | 10.7408 | 1 | 2.856 | 184 | 64.4258
15.6 | 11.1369 | 1 | 2.856 | 184 | 64.4258
14.7 | 10.8866 | 1 | 2.856 | 184 | 64.4258
14.4 | 10.8039 | 1 | 2.856 | 184 | 64.4258
14.3 | 10.8081 | 1 | 2.856 | 184 | 64.4258
14 | 10.8224 | 1 | 2.856 | 184 | 64.4258
13.1 | 10.83 | 1 | 2.856 | 184 | 64.4258
12.9 | 10.6923 | 1 | 2.856 | 184 | 64.4258
12.6 | 10.6126 | 1 | 2.856 | 184 | 64.4258
12.3 | 10.9003 | 1 | 2.856 | 184 | 64.4258
11.8 | 10.4707 | 1 | 2.856 | 184 | 64.4258
11.5 | 10.1804 | 1 | 2.856 | 184 | 64.4258
11.5 | 9.8705 | 1 | 2.856 | 184 | 64.4258
11.1 | 9.8976 | 1 | 2.856 | 184 | 64.4258
11.2 | 9.8902 | 1 | 2.856 | 184 | 64.4258
11.3 | 9.9867 | 1 | 2.856 | 184 | 64.4258
11 | 9.9054 | 1 | 2.856 | 184 | 64.4258
11.1 | 9.8976 | 1 | 2.856 | 184 | 64.4258
12 | 10.3483 | 1 | 2.856 | 184 | 64.4258
13 | 10.9388 | 1 | 2.856 | 184 | 64.4258
14.7 | 11.7642 | 1 | 2.856 | 184 | 64.4258
15.7 | 12.231 | 1 | 2.856 | 184 | 64.4258
17.4 | 12.9738 | 1 | 2.856 | 184 | 64.4258
18.5 | 13.4112 | 1 | 2.856 | 184 | 64.4258
18.5 | 13.0756 | 1 | 2.856 | 184 | 64.4258
19 | 13.0433 | 1 | 2.856 | 184 | 64.4258
19.3 | 13.6784 | 1 | 2.856 | 184 | 64.4258
19.3 | 13.6762 | 1 | 2.856 | 184 | 64.4258
18.7 | 13.5878 | 1 | 2.856 | 184 | 64.4258
18 | 13.4599 | 1 | 2.856 | 184 | 64.4258
17 | 13.4219 | 1 | 2.856 | 184 | 64.4258
16.5 | 13.1185 | 1 | 2.856 | 184 | 64.4258
16 | 13.0772 | 1 | 2.856 | 184 | 64.4258
15.3 | 13.1207 | 1 | 2.856 | 184 | 64.4258
15 | 13.0555 | 1 | 2.856 | 184 | 64.4258
15 | 13.0555 | 1 | 2.856 | 184 | 64.4258
14.8 | 12.8646 | 1 | 2.856 | 184 | 64.4258
14.3 | 12.8849 | 1 | 2.856 | 184 | 64.4258
14 | 12.7071 | 1 | 2.856 | 184 | 64.4258
13.6 | 12.4313 | 1 | 2.856 | 184 | 64.4258
13.6 | 12.3192 | 1 | 2.856 | 184 | 64.4258
14 | 12.7076 | 1 | 2.856 | 184 | 64.4258
15.6 | 13.4056 | 1 | 2.856 | 184 | 64.4258
15.7 | 13.4452 | 1 | 2.856 | 184 | 64.4258
15.6 | 13.4065 | 1 | 2.856 | 184 | 64.4258
16.1 | 13.8256 | 1 | 2.856 | 184 | 64.4258
17.3 | 13.9643 | 1 | 2.856 | 184 | 64.4258
18 | 14.2352 | 1 | 2.856 | 184 | 64.4258
18 | 14.3419 | 1 | 2.856 | 184 | 64.4258
18.4 | 14.7098 | 1 | 2.856 | 184 | 64.4258
18 | 14.5565 | 1 | 2.856 | 184 | 64.4258
17.7 | 14.3332 | 1 | 2.856 | 184 | 64.4258
17.1 | 13.9391 | 1 | 2.856 | 184 | 64.4258
16.2 | 12.8434 | 1 | 2.856 | 184 | 64.4258
15.4 | 12.5717 | 1 | 2.856 | 184 | 64.4258
14.5 | 12.3085 | 1 | 2.856 | 184 | 64.4258
14 | 11.1661 | 1 | 2.856 | 184 | 64.4258
13.6 | 11.1974 | 1 | 2.856 | 184 | 64.4258
12.9 | 10.4898 | 1 | 2.856 | 184 | 64.4258
12.6 | 10.308 | 1 | 2.856 | 184 | 64.4258
12.4 | 10.3205 | 1 | 2.856 | 184 | 64.4258
12 | 9.9931 | 1 | 2.856 | 184 | 64.4258
12.1 | 10.1383 | 1 | 2.856 | 184 | 64.4258
12.1 | 10.1374 | 1 | 2.856 | 184 | 64.4258
12.2 | 10.2323 | 1 | 2.856 | 184 | 64.4258
12.4 | 10.2207 | 1 | 2.856 | 184 | 64.4258
13 | 10.8377 | 1 | 2.856 | 184 | 64.4258
14.1 | 11.6166 | 1 | 2.856 | 184 | 64.4258
15.3 | 12.1187 | 1 | 2.856 | 184 | 64.4258
15.8 | 12.0759 | 1 | 2.856 | 184 | 64.4258
16.5 | 12.2696 | 1 | 2.856 | 184 | 64.4258
17.3 | 12.6462 | 1 | 2.856 | 184 | 64.4258
17.2 | 12.6519 | 1 | 2.856 | 184 | 64.4258
17.8 | 12.7048 | 1 | 2.856 | 184 | 64.4258
18 | 13.2181 | 1 | 2.856 | 184 | 64.4258
17.4 | 12.8303 | 1 | 2.856 | 184 | 64.4258
16.7 | 12.6939 | 1 | 2.856 | 184 | 64.4258
15.7 | 12.2352 | 1 | 2.856 | 184 | 64.4258
14.3 | 11.9096 | 1 | 2.856 | 184 | 64.4258
13.2 | 11.2352 | 1 | 2.856 | 184 | 64.4258
12.2 | 10.911 | 1 | 2.856 | 184 | 64.4258
11 | 10.0121 | 1 | 2.856 | 184 | 64.4258
10 | 9.2457 | 1 | 2.856 | 184 | 64.4258
9.9 | 9.2528 | 1 | 2.856 | 184 | 64.4258
9.3 | 8.872 | 1 | 2.856 | 184 | 64.4258
8.7 | 8.279 | 1 | 2.856 | 184 | 64.4258
8.3 | 7.9865 | 1 | 2.856 | 184 | 64.4258
7 | 6.55 | 1 | 2.856 | 184 | 64.4258
7.1 | 6.8973 | 1 | 2.856 | 184 | 64.4258
8.3 | 7.9865 | 1 | 2.856 | 184 | 64.4258
10 | 9.3513 | 1 | 2.856 | 184 | 64.4258
11.7 | 10.3758 | 1 | 2.856 | 184 | 64.4258
12.9 | 11.0557 | 1 | 2.856 | 184 | 64.4258
13.6 | 11.6172 | 1 | 2.856 | 184 | 64.4258
14.3 | 11.9106 | 1 | 2.856 | 184 | 64.4258
15.5 | 12.5637 | 1 | 2.856 | 184 | 64.4258
16.9 | 13.4414 | 1 | 2.856 | 184 | 64.4258
17.3 | 13.5983 | 1 | 2.856 | 184 | 64.4258
17 | 13.3237 | 1 | 2.856 | 184 | 64.4258
16.3 | 12.9395 | 1 | 2.856 | 184 | 64.4258
15.2 | 12.4921 | 1 | 2.856 | 184 | 64.4258
14.1 | 11.9313 | 1 | 2.856 | 184 | 64.4258
13.2 | 11.6606 | 1 | 2.856 | 184 | 64.4258
12.3 | 11.1154 | 1 | 2.856 | 184 | 64.4258
11.5 | 10.4988 | 1 | 2.856 | 184 | 64.4258
10.5 | 9.9492 | 1 | 2.856 | 184 | 64.4258
9.9 | 9.4645 | 1 | 2.856 | 184 | 64.4258
9.4 | 8.9704 | 1 | 2.856 | 184 | 64.4258
8.5 | 8.1844 | 1 | 2.856 | 184 | 64.4258
8 | 7.7917 | 1 | 2.856 | 184 | 64.4258
7.8 | 7.5928 | 1 | 2.856 | 184 | 64.4258
7.4 | 7.1952 | 1 | 2.856 | 184 | 64.4258
7.2 | 6.9964 | 1 | 2.856 | 184 | 64.4258
7.6 | 7.2923 | 1 | 2.856 | 184 | 64.4258
9.3 | 8.7665 | 1 | 2.856 | 184 | 64.4258
10.4 | 9.7432 | 1 | 2.856 | 184 | 64.4258
11.4 | 10.2943 | 1 | 2.856 | 184 | 64.4258
12.4 | 11.1028 | 1 | 2.856 | 184 | 64.4258
12.5 | 11.092 | 1 | 2.856 | 184 | 64.4258
12.8 | 11.2732 | 1 | 2.856 | 184 | 64.4258
12.9 | 11.1555 | 1 | 2.856 | 184 | 64.4258
13.3 | 11.5381 | 1 | 2.856 | 184 | 64.4258
13.2 | 11.1257 | 1 | 2.856 | 184 | 64.4258
13 | 11.4637 | 1 | 2.856 | 184 | 64.4258
12.6 | 11.403 | 1 | 2.856 | 184 | 64.4258
12.1 | 10.9179 | 1 | 2.856 | 184 | 64.4258
11.5 | 10.3886 | 1 | 2.856 | 184 | 64.4258
11.2 | 10.4187 | 1 | 2.856 | 184 | 64.4258
11 | 10.3311 | 1 | 2.856 | 184 | 64.4258
10.1 | 9.8785 | 1 | 2.856 | 184 | 64.4258
10.5 | 10.0558 | 1 | 2.856 | 184 | 64.4258
9.6 | 9.3813 | 1 | 2.856 | 184 | 64.4258
9.5 | 9.2818 | 1 | 2.856 | 184 | 64.4258
9.7 | 9.4807 | 1 | 2.856 | 184 | 64.4258
10 | 9.7788 | 1 | 2.856 | 184 | 64.4258
10.2 | 9.9776 | 1 | 2.856 | 184 | 64.4258
10.8 | 10.3518 | 1 | 2.856 | 184 | 64.4258
11.1 | 10.6483 | 1 | 2.856 | 184 | 64.4258
11.9 | 11.0477 | 1 | 2.856 | 184 | 64.4258
12.6 | 11.5096 | 1 | 2.856 | 184 | 64.4258
13.8 | 12.3951 | 1 | 2.856 | 184 | 64.4258
15.5 | 13.637 | 1 | 2.856 | 184 | 64.4258
15.5 | 13.4116 | 1 | 2.856 | 184 | 64.4258
16.5 | 13.8015 | 1 | 2.856 | 184 | 64.4258
17.5 | 13.9161 | 1 | 2.856 | 184 | 64.4258
17.2 | 14.1793 | 1 | 2.856 | 184 | 64.4258
17 | 14.3817 | 1 | 2.856 | 184 | 64.4258
16.8 | 14.3047 | 1 | 2.856 | 184 | 64.4258
16.4 | 14.0953 | 1 | 2.856 | 184 | 64.4258
15.4 | 13.6521 | 1 | 2.856 | 184 | 64.4258
15 | 13.3814 | 1 | 2.856 | 184 | 64.4258
13.6 | 12.5949 | 1 | 2.856 | 184 | 64.4258
13.8 | 12.7898 | 1 | 2.856 | 184 | 64.4258
13.5 | 12.4969 | 1 | 2.856 | 184 | 64.4258
13.6 | 12.7092 | 1 | 2.856 | 184 | 64.4258
13.5 | 12.6112 | 1 | 2.856 | 184 | 64.4258
13.2 | 12.5477 | 1 | 2.856 | 184 | 64.4258
13.1 | 12.6826 | 1 | 2.856 | 184 | 64.4258
13.1 | 12.8601 | 1 | 2.856 | 184 | 64.4258
13 | 12.7605 | 1 | 2.856 | 184 | 64.4258
13.5 | 13.0784 | 1 | 2.856 | 184 | 64.4258
13.7 | 13.0393 | 1 | 2.856 | 184 | 64.4258
14.4 | 12.9696 | 1 | 2.856 | 184 | 64.4258
14.5 | 13.0663 | 1 | 2.856 | 184 | 64.4258
16 | 13.4873 | 1 | 2.856 | 184 | 64.4258
17.9 | 14.5452 | 1 | 2.856 | 184 | 64.4258
18.5 | 12.9328 | 1 | 2.856 | 184 | 64.4258
19.1 | 11.4102 | 1 | 2.856 | 184 | 64.4258
18 | 11.6031 | 1 | 2.856 | 184 | 64.4258
17.5 | 12.0151 | 1 | 2.856 | 184 | 64.4258
16.8 | 11.8641 | 1 | 2.856 | 184 | 64.4258
15.9 | 12.4814 | 1 | 2.856 | 184 | 64.4258
15.7 | 12.4007 | 1 | 2.856 | 184 | 64.4258
14.4 | 12.6294 | 1 | 2.856 | 184 | 64.4258
13.6 | 12.7063 | 1 | 2.856 | 184 | 64.4258
12.3 | 11.4338 | 1 | 2.856 | 184 | 64.4258
11.5 | 10.596 | 1 | 2.856 | 184 | 64.4258
11 | 10.3252 | 1 | 2.856 | 184 | 64.4258
10.8 | 9.9116 | 1 | 2.856 | 184 | 64.4258
10.3 | 9.2129 | 1 | 2.856 | 184 | 64.4258
10.4 | 9.4146 | 1 | 2.856 | 184 | 64.4258
10.9 | 9.6884 | 1 | 2.856 | 184 | 64.4258
11.5 | 10.594 | 1 | 2.856 | 184 | 64.4258
12.1 | 11.0133 | 1 | 2.856 | 184 | 64.4258
11.8 | 11.1089 | 1 | 2.856 | 184 | 64.4258
12.6 | 12.2435 | 1 | 2.856 | 184 | 64.4258
14.6 | 13.3876 | 1 | 2.856 | 184 | 64.4258
14.5 | 12.8308 | 1 | 2.856 | 184 | 64.4258
16.1 | 12.9161 | 1 | 2.856 | 184 | 64.4258
16.8 | 11.2537 | 1 | 2.856 | 184 | 64.4258
15.8 | 10.1406 | 1 | 2.856 | 184 | 64.4258
15.9 | 10.2283 | 1 | 2.856 | 184 | 64.4258
16.6 | 10.288 | 1 | 2.856 | 184 | 64.4258
16.5 | 9.9702 | 1 | 2.856 | 184 | 64.4258
16 | 9.4486 | 1 | 2.856 | 184 | 64.4258
15 | 9.3534 | 1 | 2.856 | 184 | 64.4258
14 | 8.4327 | 1 | 2.856 | 184 | 64.4258
13 | 8.6587 | 1 | 2.856 | 184 | 64.4258
11.8 | 8.1479 | 1 | 2.856 | 184 | 64.4258
11.5 | 9.1546 | 1 | 2.856 | 184 | 64.4258
11.4 | 9.0609 | 1 | 2.856 | 184 | 64.4258
10.9 | 8.7848 | 1 | 2.856 | 184 | 64.4258
10.7 | 8.7909 | 1 | 2.856 | 184 | 64.4258
11.5 | 9.5996 | 1 | 2.856 | 184 | 64.4258
11.4 | 9.5047 | 1 | 2.856 | 184 | 64.4258
12.1 | 9.7651 | 1 | 2.856 | 184 | 64.4258
12.8 | 10.3708 | 1 | 2.856 | 184 | 64.4258
13.4 | 10.8824 | 1 | 2.856 | 184 | 64.4258
13.7 | 11.6346 | 1 | 2.856 | 184 | 64.4258
14.5 | 11.9661 | 1 | 2.856 | 184 | 64.4258
15 | 12.5974 | 1 | 2.856 | 184 | 64.4258
15.5 | 12.7452 | 1 | 2.856 | 184 | 64.4258
16 | 12.84 | 1 | 2.856 | 184 | 64.4258
16.1 | 13.255 | 1 | 2.856 | 184 | 64.4258
15.9 | 13.5056 | 1 | 2.856 | 184 | 64.4258
15.9 | 13.3949 | 1 | 2.856 | 184 | 64.4258
15.4 | 13.536 | 1 | 2.856 | 184 | 64.4258
14.5 | 13.298 | 1 | 2.856 | 184 | 64.4258
14.8 | 13.2438 | 1 | 2.856 | 184 | 64.4258
14.6 | 13.0508 | 1 | 2.856 | 184 | 64.4258
15 | 13.5518 | 1 | 2.856 | 184 | 64.4258
14.4 | 13.5514 | 1 | 2.856 | 184 | 64.4258
14.4 | 13.6109 | 1 | 2.856 | 184 | 64.4258
14.5 | 13.9486 | 1 | 2.856 | 184 | 64.4258
14.6 | 13.9269 | 1 | 2.856 | 184 | 64.4258
14.6 | 14.0476 | 1 | 2.856 | 184 | 64.4258
15.1 | 14.2389 | 1 | 2.856 | 184 | 64.4258
15.1 | 14.4198 | 1 | 2.856 | 184 | 64.4258
15.1 | 14.2389 | 1 | 2.856 | 184 | 64.4258
15.3 | 14.8625 | 1 | 2.856 | 184 | 64.4258
15.5 | 14.7532 | 1 | 2.856 | 184 | 64.4258
15.5 | 14.8758 | 1 | 2.856 | 184 | 64.4258
15.5 | 14.7535 | 1 | 2.856 | 184 | 64.4258
15.5 | 14.7538 | 1 | 2.856 | 184 | 64.4258
16 | 14.8206 | 1 | 2.856 | 184 | 64.4258
16.2 | 14.8953 | 1 | 2.856 | 184 | 64.4258
16.3 | 15.4183 | 1 | 2.856 | 184 | 64.4258
17.2 | 15.3856 | 1 | 2.856 | 184 | 64.4258
18.3 | 15.9044 | 1 | 2.856 | 184 | 64.4258
19.9 | 16.3584 | 1 | 2.856 | 184 | 64.4258
19.3 | 16.2613 | 1 | 2.856 | 184 | 64.4258
19.2 | 16.6998 | 1 | 2.856 | 184 | 64.4258
19.3 | 16.6152 | 1 | 2.856 | 184 | 64.4258
19.5 | 15.9313 | 1 | 2.856 | 184 | 64.4258
18.5 | 15.0049 | 1 | 2.856 | 184 | 64.4258
17.9 | 15.1765 | 1 | 2.856 | 184 | 64.4258
16.8 | 14.9419 | 1 | 2.856 | 184 | 64.4258
16.9 | 14.9206 | 1 | 2.856 | 184 | 64.4258
16.8 | 14.8248 | 1 | 2.856 | 184 | 64.4258
16.5 | 14.6538 | 1 | 2.856 | 184 | 64.4258
16.5 | 14.5375 | 1 | 2.856 | 184 | 64.4258
16.5 | 14.3075 | 1 | 2.856 | 184 | 64.4258
16.1 | 14.0394 | 1 | 2.856 | 184 | 64.4258
15.9 | 13.9623 | 1 | 2.856 | 184 | 64.4258
16 | 14.1723 | 1 | 2.856 | 184 | 64.4258
16.2 | 14.2488 | 1 | 2.856 | 184 | 64.4258
16.4 | 14.4403 | 1 | 2.856 | 184 | 64.4258
16.6 | 14.7491 | 1 | 2.856 | 184 | 64.4258
17.1 | 15.1704 | 1 | 2.856 | 184 | 64.4258
17.4 | 15.4582 | 1 | 2.856 | 184 | 64.4258
18 | 16.0945 | 1 | 2.856 | 184 | 64.4258
18.8 | 16.084 | 1 | 2.856 | 184 | 64.4258
17.1 | 15.8941 | 1 | 2.856 | 184 | 64.4258
17.4 | 15.7589 | 1 | 2.856 | 184 | 64.4258
17.7 | 15.7476 | 1 | 2.856 | 184 | 64.4258
18 | 15.1574 | 1 | 2.856 | 184 | 64.4258
17.8 | 15.1989 | 1 | 2.856 | 184 | 64.4258
16.6 | 15.9625 | 1 | 2.856 | 184 | 64.4258
16.5 | 16.0525 | 1 | 2.856 | 184 | 64.4258
16.6 | 15.9625 | 1 | 2.856 | 184 | 64.4258
16.3 | 15.5423 | 1 | 2.856 | 184 | 64.4258
16 | 15.3703 | 1 | 2.856 | 184 | 64.4258
15.8 | 14.9278 | 1 | 2.856 | 184 | 64.4258
15.7 | 15.074 | 1 | 2.856 | 184 | 64.4258
16 | 15.1238 | 1 | 2.856 | 184 | 64.4258
15.5 | 14.9378 | 1 | 2.856 | 184 | 64.4258
15.8 | 15.0496 | 1 | 2.856 | 184 | 64.4258
15.6 | 14.9749 | 1 | 2.856 | 184 | 64.4258
15.8 | 14.8059 | 1 | 2.856 | 184 | 64.4258
15.8 | 14.8059 | 1 | 2.856 | 184 | 64.4258
16 | 15.0017 | 1 | 2.856 | 184 | 64.4258
16.5 | 15.1871 | 1 | 2.856 | 184 | 64.4258
16.3 | 15.418 | 1 | 2.856 | 184 | 64.4258
16.6 | 15.7125 | 1 | 2.856 | 184 | 64.4258
17 | 15.9185 | 1 | 2.856 | 184 | 64.4258
17 | 15.7953 | 1 | 2.856 | 184 | 64.4258
17.2 | 15.99 | 1 | 2.856 | 184 | 64.4258
16.8 | 15.9082 | 1 | 2.856 | 184 | 64.4258
16.6 | 15.7115 | 1 | 2.856 | 184 | 64.4258
16.4 | 15.639 | 1 | 2.856 | 184 | 64.4258
16.4 | 15.6388 | 1 | 2.856 | 184 | 64.4258
16.3 | 15.2328 | 1 | 2.856 | 184 | 64.4258
15.8 | 14.6234 | 1 | 2.856 | 184 | 64.4258
16.3 | 14.7513 | 1 | 2.856 | 184 | 64.4258
16 | 14.8179 | 1 | 2.856 | 184 | 64.4258
16 | 14.6975 | 1 | 2.856 | 184 | 64.4258
16.1 | 14.6753 | 1 | 2.856 | 184 | 64.4258
16.3 | 14.9882 | 1 | 2.856 | 184 | 64.4258
15.7 | 15.1334 | 1 | 2.856 | 184 | 64.4258
16 | 15.2433 | 1 | 2.856 | 184 | 64.4258
16 | 15.1199 | 1 | 2.856 | 184 | 64.4258
16.1 | 15.4655 | 1 | 2.856 | 184 | 64.4258
12.1 | 11.7492 | 1 | 2.856 | 184 | 64.4258
12.3 | 11.5464 | 1 | 2.856 | 184 | 64.4258
12 | 10.8646 | 1 | 2.856 | 184 | 64.4258
12 | 11.0293 | 1 | 2.856 | 184 | 64.4258
13.3 | 11.8489 | 1 | 2.856 | 184 | 64.4258
14.3 | 12.5328 | 1 | 2.856 | 184 | 64.4258
14.7 | 12.2576 | 1 | 2.856 | 184 | 64.4258
14.3 | 11.9339 | 1 | 2.856 | 184 | 64.4258
15.3 | 12.0819 | 1 | 2.856 | 184 | 64.4258
16.7 | 11.543 | 1 | 2.856 | 184 | 64.4258
15.9 | 11.0249 | 1 | 2.856 | 184 | 64.4258
13.2 | 11.4254 | 1 | 2.856 | 184 | 64.4258
14.1 | 11.1264 | 1 | 2.856 | 184 | 64.4258
12.4 | 10.0938 | 1 | 2.856 | 184 | 64.4258
10.6 | 9.0417 | 1 | 2.856 | 184 | 64.4258
11.3 | 9.208 | 1 | 2.856 | 184 | 64.4258
10.2 | 8.6593 | 1 | 2.856 | 184 | 64.4258
10 | 8.5674 | 1 | 2.856 | 184 | 64.4258
9.5 | 8.2868 | 1 | 2.856 | 184 | 64.4258
9.1 | 8.0004 | 1 | 2.856 | 184 | 64.4258
8.7 | 7.8123 | 1 | 2.856 | 184 | 64.4258
8.4 | 7.8233 | 1 | 2.856 | 184 | 64.4258
8.6 | 7.7152 | 1 | 2.856 | 184 | 64.4258
8.2 | 7.1782 | 1 | 2.856 | 184 | 64.4258
7.7 | 6.9364 | 1 | 2.856 | 184 | 64.4258
7.8 | 7.0345 | 1 | 2.856 | 184 | 64.4258
7.6 | 6.6933 | 1 | 2.856 | 184 | 64.4258
7.8 | 7.0353 | 1 | 2.856 | 184 | 64.4258
9.2 | 8.1004 | 1 | 2.856 | 184 | 64.4258
10.9 | 9.0367 | 1 | 2.856 | 184 | 64.4258
12.5 | 9.4249 | 1 | 2.856 | 184 | 64.4258
14.2 | 10.1367 | 1 | 2.856 | 184 | 64.4258
13.8 | 9.0475 | 1 | 2.856 | 184 | 64.4258
14.7 | 9.537 | 1 | 2.856 | 184 | 64.4258
12.8 | 8.8491 | 1 | 2.856 | 184 | 64.4258
15.5 | 9.5379 | 1 | 2.856 | 184 | 64.4258
15 | 9.3915 | 1 | 2.856 | 184 | 64.4258
13.7 | 8.408 | 1 | 2.856 | 184 | 64.4258
12.8 | 8.8491 | 1 | 2.856 | 184 | 64.4258
12 | 8.7001 | 1 | 2.856 | 184 | 64.4258
11.6 | 8.5163 | 1 | 2.856 | 184 | 64.4258
9.5 | 7.2973 | 1 | 2.856 | 184 | 64.4258
9.3 | 7.6177 | 1 | 2.856 | 184 | 64.4258
7.6 | 6.5076 | 1 | 2.856 | 184 | 64.4258
6.8 | 5.9198 | 1 | 2.856 | 184 | 64.4258
6.4 | 5.624 | 1 | 2.856 | 184 | 64.4258
4.8 | 4.3328 | 1 | 2.856 | 184 | 64.4258
5.1 | 4.8613 | 1 | 2.856 | 184 | 64.4258
5 | 4.5298 | 1 | 2.856 | 184 | 64.4258
4.7 | 4.2346 | 1 | 2.856 | 184 | 64.4258
4.7 | 4.1445 | 1 | 2.856 | 184 | 64.4258
5.1 | 4.6751 | 1 | 2.856 | 184 | 64.4258
7 | 5.8839 | 1 | 2.856 | 184 | 64.4258
9.7 | 7.7213 | 1 | 2.856 | 184 | 64.4258
11.4 | 8.082 | 1 | 2.856 | 184 | 64.4258
12.8 | 8.1671 | 1 | 2.856 | 184 | 64.4258
13 | 7.9527 | 1 | 2.856 | 184 | 64.4258
13.8 | 8.4057 | 1 | 2.856 | 184 | 64.4258
14.4 | 8.3566 | 1 | 2.856 | 184 | 64.4258
14.5 | 8.5841 | 1 | 2.856 | 184 | 64.4258
13.9 | 8.1934 | 1 | 2.856 | 184 | 64.4258
13.6 | 7.9789 | 1 | 2.856 | 184 | 64.4258
12.5 | 7.7546 | 1 | 2.856 | 184 | 64.4258
11.4 | 7.2259 | 1 | 2.856 | 184 | 64.4258
10.8 | 7.5423 | 1 | 2.856 | 184 | 64.4258
10.4 | 8.0108 | 1 | 2.856 | 184 | 64.4258
10.1 | 8.29 | 1 | 2.856 | 184 | 64.4258
9.6 | 8.6989 | 1 | 2.856 | 184 | 64.4258
10.2 | 9.4934 | 1 | 2.856 | 184 | 64.4258
11 | 10.3866 | 1 | 2.856 | 184 | 64.4258
11.6 | 11.1442 | 1 | 2.856 | 184 | 64.4258
12.3 | 12.1244 | 1 | 2.856 | 184 | 64.4258
12.9 | 12.9 | 1 | 2.856 | 184 | 64.4258
12.6 | 12.6 | 1 | 2.856 | 184 | 64.4258
12.7 | 12.7 | 1 | 2.856 | 184 | 64.4258
12.7 | 12.7 | 1 | 2.856 | 184 | 64.4258
12.7 | 12.7 | 1 | 2.856 | 184 | 64.4258
12.8 | 12.8 | 1 | 2.856 | 184 | 64.4258
13.3 | 12.9419 | 1 | 2.856 | 184 | 64.4258
13.9 | 13.3585 | 1 | 2.856 | 184 | 64.4258
14 | 13.2214 | 1 | 2.856 | 184 | 64.4258
14.7 | 13.8497 | 1 | 2.856 | 184 | 64.4258
15.3 | 13.8483 | 1 | 2.856 | 184 | 64.4258
15.7 | 14.061 | 1 | 2.856 | 184 | 64.4258
15.6 | 13.9646 | 1 | 2.856 | 184 | 64.4258
15.5 | 13.8676 | 1 | 2.856 | 184 | 64.4258
15.5 | 13.8683 | 1 | 2.856 | 184 | 64.4258
15.2 | 13.8675 | 1 | 2.856 | 184 | 64.4258
15 | 13.9068 | 1 | 2.856 | 184 | 64.4258
15.2 | 13.8675 | 1 | 2.856 | 184 | 64.4258
15.1 | 13.8865 | 1 | 2.856 | 184 | 64.4258
14.5 | 13.6531 | 1 | 2.856 | 184 | 64.4258
13 | 12.4692 | 1 | 2.856 | 184 | 64.4258
12.4 | 12.1071 | 1 | 2.856 | 184 | 64.4258
13 | 12.5856 | 1 | 2.856 | 184 | 64.4258
13.9 | 12.607 | 1 | 2.856 | 184 | 64.4258
13.6 | 11.3965 | 1 | 2.856 | 184 | 64.4258
13 | 10.8294 | 1 | 2.856 | 184 | 64.4258
12.7 | 10.8564 | 1 | 2.856 | 184 | 64.4258
12.9 | 10.9425 | 1 | 2.856 | 184 | 64.4258
13 | 11.196 | 1 | 2.856 | 184 | 64.4258
14.2 | 11.1445 | 1 | 2.856 | 184 | 64.4258
15.5 | 11.5494 | 1 | 2.856 | 184 | 64.4258
16.5 | 12.4521 | 1 | 2.856 | 184 | 64.4258
17.8 | 13.0271 | 1 | 2.856 | 184 | 64.4258
17.4 | 13.1663 | 1 | 2.856 | 184 | 64.4258
18 | 13.7573 | 1 | 2.856 | 184 | 64.4258
18.6 | 13.5897 | 1 | 2.856 | 184 | 64.4258
17.9 | 13.4636 | 1 | 2.856 | 184 | 64.4258
18.1 | 13.7468 | 1 | 2.856 | 184 | 64.4258
17.4 | 13.6275 | 1 | 2.856 | 184 | 64.4258
16.8 | 13.7645 | 1 | 2.856 | 184 | 64.4258
16.4 | 13.7729 | 1 | 2.856 | 184 | 64.4258
16.1 | 13.4907 | 1 | 2.856 | 184 | 64.4258
15.7 | 13.3324 | 1 | 2.856 | 184 | 64.4258
15.5 | 13.308 | 1 | 2.856 | 184 | 64.4258
15.2 | 13.2442 | 1 | 2.856 | 184 | 64.4258
14.6 | 12.8369 | 1 | 2.856 | 184 | 64.4258
14.1 | 12.6898 | 1 | 2.856 | 184 | 64.4258
13.5 | 12.3889 | 1 | 2.856 | 184 | 64.4258
12.2 | 11.2331 | 1 | 2.856 | 184 | 64.4258
11.7 | 10.909 | 1 | 2.856 | 184 | 64.4258
11.5 | 10.8228 | 1 | 2.856 | 184 | 64.4258
11.2 | 10.5282 | 1 | 2.856 | 184 | 64.4258
12.8 | 11.8191 | 1 | 2.856 | 184 | 64.4258
14.7 | 12.8772 | 1 | 2.856 | 184 | 64.4258
16.6 | 13.4722 | 1 | 2.856 | 184 | 64.4258
17.9 | 13.8766 | 1 | 2.856 | 184 | 64.4258
18.9 | 13.8078 | 1 | 2.856 | 184 | 64.4258
19.5 | 14.0901 | 1 | 2.856 | 184 | 64.4258
19.6 | 13.9798 | 1 | 2.856 | 184 | 64.4258
19.5 | 14.088 | 1 | 2.856 | 184 | 64.4258
18.8 | 13.8165 | 1 | 2.856 | 184 | 64.4258
17.4 | 13.1646 | 1 | 2.856 | 184 | 64.4258
15.4 | 12.1001 | 1 | 2.856 | 184 | 64.4258
14.1 | 10.955 | 1 | 2.856 | 184 | 64.4258
13.3 | 10.7588 | 1 | 2.856 | 184 | 64.4258
13.3 | 10.7588 | 1 | 2.856 | 184 | 64.4258
12.7 | 10.498 | 1 | 2.856 | 184 | 64.4258
13.1 | 10.7733 | 1 | 2.856 | 184 | 64.4258
12.7 | 10.7033 | 1 | 2.856 | 184 | 64.4258
11.5 | 10.713 | 1 | 2.856 | 184 | 64.4258
11 | 10.223 | 1 | 2.856 | 184 | 64.4258
11.1 | 10.1065 | 1 | 2.856 | 184 | 64.4258
10.7 | 9.8221 | 1 | 2.856 | 184 | 64.4258
10.6 | 9.8308 | 1 | 2.856 | 184 | 64.4258
10.3 | 9.7504 | 1 | 2.856 | 184 | 64.4258
10.8 | 10.0267 | 1 | 2.856 | 184 | 64.4258
12.9 | 11.2596 | 1 | 2.856 | 184 | 64.4258
14.5 | 12.0384 | 1 | 2.856 | 184 | 64.4258
16.4 | 12.3634 | 1 | 2.856 | 184 | 64.4258
18 | 12.8663 | 1 | 2.856 | 184 | 64.4258
18.7 | 13.1469 | 1 | 2.856 | 184 | 64.4258
18.6 | 13.6371 | 1 | 2.856 | 184 | 64.4258
18.7 | 13.7737 | 1 | 2.856 | 184 | 64.4258
18.4 | 13.1659 | 1 | 2.856 | 184 | 64.4258
17.8 | 12.6391 | 1 | 2.856 | 184 | 64.4258
16.9 | 12.0823 | 1 | 2.856 | 184 | 64.4258
15 | 12.294 | 1 | 2.856 | 184 | 64.4258
13.8 | 12.2869 | 1 | 2.856 | 184 | 64.4258
14 | 12.3688 | 1 | 2.856 | 184 | 64.4258
14 | 12.3688 | 1 | 2.856 | 184 | 64.4258
13.5 | 12.3876 | 1 | 2.856 | 184 | 64.4258
13.5 | 12.7303 | 1 | 2.856 | 184 | 64.4258
13.6 | 12.4845 | 1 | 2.856 | 184 | 64.4258
13.3 | 12.3053 | 1 | 2.856 | 184 | 64.4258
12.1 | 11.4114 | 1 | 2.856 | 184 | 64.4258
12.2 | 11.7933 | 1 | 2.856 | 184 | 64.4258
11.7 | 11.3549 | 1 | 2.856 | 184 | 64.4258
11.2 | 10.9719 | 1 | 2.856 | 184 | 64.4258
11.3 | 10.9583 | 1 | 2.856 | 184 | 64.4258
11 | 10.6609 | 1 | 2.856 | 184 | 64.4258
12.6 | 11.9029 | 1 | 2.856 | 184 | 64.4258
13.2 | 12.4354 | 1 | 2.856 | 184 | 64.4258
14.1 | 13.1444 | 1 | 2.856 | 184 | 64.4258
14 | 13.3388 | 1 | 2.856 | 184 | 64.4258
14.5 | 14.0714 | 1 | 2.856 | 184 | 64.4258
15.5 | 14.5145 | 1 | 2.856 | 184 | 64.4258
16.4 | 14.8544 | 1 | 2.856 | 184 | 64.4258
17 | 15.0201 | 1 | 2.856 | 184 | 64.4258
17.1 | 15.1746 | 1 | 2.856 | 184 | 64.4258
17 | 15.3748 | 1 | 2.856 | 184 | 64.4258
16.6 | 14.4078 | 1 | 2.856 | 184 | 64.4258
16 | 13.8366 | 1 | 2.856 | 184 | 64.4258
15.5 | 13.8695 | 1 | 2.856 | 184 | 64.4258
16 | 13.9503 | 1 | 2.856 | 184 | 64.4258
15.1 | 13.772 | 1 | 2.856 | 184 | 64.4258
13.9 | 13.1238 | 1 | 2.856 | 184 | 64.4258
12.7 | 12.0591 | 1 | 2.856 | 184 | 64.4258
12.2 | 11.8514 | 1 | 2.856 | 184 | 64.4258
11.7 | 11.2427 | 1 | 2.856 | 184 | 64.4258
11.2 | 10.8599 | 1 | 2.856 | 184 | 64.4258
11.1 | 10.8169 | 1 | 2.856 | 184 | 64.4258
12.1 | 11.6953 | 1 | 2.856 | 184 | 64.4258
12.5 | 11.8627 | 1 | 2.856 | 184 | 64.4258
12.5 | 11.9197 | 1 | 2.856 | 184 | 64.4258
13 | 12.4127 | 1 | 2.856 | 184 | 64.4258
14 | 12.9343 | 1 | 2.856 | 184 | 64.4258
16.7 | 14.002 | 1 | 2.856 | 184 | 64.4258
18 | 14.4481 | 1 | 2.856 | 184 | 64.4258
19.3 | 14.4713 | 1 | 2.856 | 184 | 64.4258
20 | 14.2381 | 1 | 2.856 | 184 | 64.4258
19.4 | 14.2044 | 1 | 2.856 | 184 | 64.4258
19.5 | 14.6483 | 1 | 2.856 | 184 | 64.4258
19.1 | 14.6525 | 1 | 2.856 | 184 | 64.4258
18.2 | 14.7402 | 1 | 2.856 | 184 | 64.4258
17.8 | 14.7546 | 1 | 2.856 | 184 | 64.4258
17.3 | 14.7918 | 1 | 2.856 | 184 | 64.4258
17 | 14.7355 | 1 | 2.856 | 184 | 64.4258
16.6 | 14.8743 | 1 | 2.856 | 184 | 64.4258
16 | 14.6475 | 1 | 2.856 | 184 | 64.4258
16 | 14.6475 | 1 | 2.856 | 184 | 64.4258
14.1 | 13.1466 | 1 | 2.856 | 184 | 64.4258
13.6 | 12.9461 | 1 | 2.856 | 184 | 64.4258
13.9 | 13.3593 | 1 | 2.856 | 184 | 64.4258
13.3 | 12.7667 | 1 | 2.856 | 184 | 64.4258
13.4 | 12.8653 | 1 | 2.856 | 184 | 64.4258
12.6 | 12.1327 | 1 | 2.856 | 184 | 64.4258
12.2 | 11.8517 | 1 | 2.856 | 184 | 64.4258
13.4 | 12.8655 | 1 | 2.856 | 184 | 64.4258
14 | 13.1066 | 1 | 2.856 | 184 | 64.4258
15.4 | 13.5484 | 1 | 2.856 | 184 | 64.4258
17.2 | 13.8144 | 1 | 2.856 | 184 | 64.4258
19.3 | 14.4677 | 1 | 2.856 | 184 | 64.4258
20.7 | 15.4056 | 1 | 2.856 | 184 | 64.4258
21.6 | 15.787 | 1 | 2.856 | 184 | 64.4258
21.2 | 15.691 | 1 | 2.856 | 184 | 64.4258
21.1 | 16.0224 | 1 | 2.856 | 184 | 64.4258
21.1 | 16.0224 | 1 | 2.856 | 184 | 64.4258
19.8 | 15.6045 | 1 | 2.856 | 184 | 64.4258
19 | 15.5892 | 1 | 2.856 | 184 | 64.4258
18 | 15.3937 | 1 | 2.856 | 184 | 64.4258
18 | 15.2217 | 1 | 2.856 | 184 | 64.4258
17.1 | 14.828 | 1 | 2.856 | 184 | 64.4258
15.9 | 14.0833 | 1 | 2.856 | 184 | 64.4258
14.7 | 13.4997 | 1 | 2.856 | 184 | 64.4258
13.4 | 12.633 | 1 | 2.856 | 184 | 64.4258
14.2 | 13.1285 | 1 | 2.856 | 184 | 64.4258
13.7 | 12.928 | 1 | 2.856 | 184 | 64.4258
13.7 | 12.9277 | 1 | 2.856 | 184 | 64.4258
13.6 | 12.8294 | 1 | 2.856 | 184 | 64.4258
13.6 | 12.9456 | 1 | 2.856 | 184 | 64.4258
13.7 | 12.928 | 1 | 2.856 | 184 | 64.4258
14 | 13.0484 | 1 | 2.856 | 184 | 64.4258
14.4 | 13.4397 | 1 | 2.856 | 184 | 64.4258
15.3 | 13.9676 | 1 | 2.856 | 184 | 64.4258
16.4 | 14.4492 | 1 | 2.856 | 184 | 64.4258
17.3 | 14.7899 | 1 | 2.856 | 184 | 64.4258
19.6 | 15.6995 | 1 | 2.856 | 184 | 64.4258
20.4 | 14.1946 | 1 | 2.856 | 184 | 64.4258
20.6 | 14.3191 | 1 | 2.856 | 184 | 64.4258
20 | 14.5779 | 1 | 2.856 | 184 | 64.4258
19.3 | 14.6189 | 1 | 2.856 | 184 | 64.4258
18.4 | 14.7572 | 1 | 2.856 | 184 | 64.4258
17.1 | 14.6556 | 1 | 2.856 | 184 | 64.4258
16 | 14.1212 | 1 | 2.856 | 184 | 64.4258
15.2 | 14.0444 | 1 | 2.856 | 184 | 64.4258
13.8 | 13.2008 | 1 | 2.856 | 184 | 64.4258
13 | 12.5277 | 1 | 2.856 | 184 | 64.4258
13.5 | 12.7306 | 1 | 2.856 | 184 | 64.4258
13.7 | 12.7539 | 1 | 2.856 | 184 | 64.4258
13.4 | 12.178 | 1 | 2.856 | 184 | 64.4258
13.5 | 12.2751 | 1 | 2.856 | 184 | 64.4258
13.2 | 12.1512 | 1 | 2.856 | 184 | 64.4258
13.5 | 12.3867 | 1 | 2.856 | 184 | 64.4258
13.8 | 12.7358 | 1 | 2.856 | 184 | 64.4258
14 | 12.9309 | 1 | 2.856 | 184 | 64.4258
13.8 | 12.7358 | 1 | 2.856 | 184 | 64.4258
14.1 | 12.7999 | 1 | 2.856 | 184 | 64.4258
15.1 | 13.0331 | 1 | 2.856 | 184 | 64.4258
16.2 | 13.6888 | 1 | 2.856 | 184 | 64.4258
17.8 | 14.1977 | 1 | 2.856 | 184 | 64.4258
19.2 | 14.8353 | 1 | 2.856 | 184 | 64.4258
20.8 | 15.2715 | 1 | 2.856 | 184 | 64.4258
21.7 | 15.7527 | 1 | 2.856 | 184 | 64.4258
20.7 | 15.5964 | 1 | 2.856 | 184 | 64.4258
19.9 | 15.1439 | 1 | 2.856 | 184 | 64.4258
17.3 | 14.3858 | 1 | 2.856 | 184 | 64.4258
15.3 | 13.4446 | 1 | 2.856 | 184 | 64.4258
14.1 | 12.8552 | 1 | 2.856 | 184 | 64.4258
13.2 | 12.206 | 1 | 2.856 | 184 | 64.4258
12.6 | 11.8447 | 1 | 2.856 | 184 | 64.4258
12.3 | 11.5502 | 1 | 2.856 | 184 | 64.4258
12.3 | 11.5499 | 1 | 2.856 | 184 | 64.4258
11 | 10.5487 | 1 | 2.856 | 184 | 64.4258
12.4 | 11.9326 | 1 | 2.856 | 184 | 64.4258
12.8 | 12.2702 | 1 | 2.856 | 184 | 64.4258
13.4 | 13.0397 | 1 | 2.856 | 184 | 64.4258
13.8 | 13.3766 | 1 | 2.856 | 184 | 64.4258
13.8 | 13.3766 | 1 | 2.856 | 184 | 64.4258
14.2 | 13.5334 | 1 | 2.856 | 184 | 64.4258
14.2 | 13.4741 | 1 | 2.856 | 184 | 64.4258
14.5 | 13.7098 | 1 | 2.856 | 184 | 64.4258
15.7 | 13.9404 | 1 | 2.856 | 184 | 64.4258
16.6 | 14.2861 | 1 | 2.856 | 184 | 64.4258
17.1 | 14.7036 | 1 | 2.856 | 184 | 64.4258
17.9 | 15.0024 | 1 | 2.856 | 184 | 64.4258
18.1 | 15.1901 | 1 | 2.856 | 184 | 64.4258
18.8 | 15.8476 | 1 | 2.856 | 184 | 64.4258
18.2 | 15.0572 | 1 | 2.856 | 184 | 64.4258
16.9 | 14.9184 | 1 | 2.856 | 184 | 64.4258
16.1 | 13.9251 | 1 | 2.856 | 184 | 64.4258
15.5 | 13.0791 | 1 | 2.856 | 184 | 64.4258
15 | 12.5543 | 1 | 2.856 | 184 | 64.4258
14.2 | 12.2289 | 1 | 2.856 | 184 | 64.4258
13.9 | 11.9438 | 1 | 2.856 | 184 | 64.4258
13.5 | 11.9409 | 1 | 2.856 | 184 | 64.4258
13.1 | 11.8853 | 1 | 2.856 | 184 | 64.4258
12 | 11.0908 | 1 | 2.856 | 184 | 64.4258
11 | 10.5499 | 1 | 2.856 | 184 | 64.4258
10.1 | 9.8783 | 1 | 2.856 | 184 | 64.4258
9.5 | 9.2819 | 1 | 2.856 | 184 | 64.4258
9.5 | 9.2819 | 1 | 2.856 | 184 | 64.4258
9.6 | 9.3814 | 1 | 2.856 | 184 | 64.4258
9.4 | 9.0754 | 1 | 2.856 | 184 | 64.4258
10 | 9.455 | 1 | 2.856 | 184 | 64.4258
11 | 9.6954 | 1 | 2.856 | 184 | 64.4258
12.1 | 10.2357 | 1 | 2.856 | 184 | 64.4258
13.6 | 10.9407 | 1 | 2.856 | 184 | 64.4258
15.3 | 11.3739 | 1 | 2.856 | 184 | 64.4258
17.1 | 12.3161 | 1 | 2.856 | 184 | 64.4258
16.9 | 11.1104 | 1 | 2.856 | 184 | 64.4258
17.1 | 11.3237 | 1 | 2.856 | 184 | 64.4258
17.2 | 11.2386 | 1 | 2.856 | 184 | 64.4258
16.7 | 11.0246 | 1 | 2.856 | 184 | 64.4258
15.9 | 10.2998 | 1 | 2.856 | 184 | 64.4258
14.4 | 10.0222 | 1 | 2.856 | 184 | 64.4258
13.3 | 9.4407 | 1 | 2.856 | 184 | 64.4258
12.5 | 9.0318 | 1 | 2.856 | 184 | 64.4258
11.3 | 8.8934 | 1 | 2.856 | 184 | 64.4258
10.4 | 8.7674 | 1 | 2.856 | 184 | 64.4258
9.5 | 8.3983 | 1 | 2.856 | 184 | 64.4258
9.4 | 8.7601 | 1 | 2.856 | 184 | 64.4258
8.8 | 8.3769 | 1 | 2.856 | 184 | 64.4258
8.3 | 7.9857 | 1 | 2.856 | 184 | 64.4258
8.4 | 7.9303 | 1 | 2.856 | 184 | 64.4258
7.8 | 7.644 | 1 | 2.856 | 184 | 64.4258
6.8 | 6.6988 | 1 | 2.856 | 184 | 64.4258
6.8 | 6.6988 | 1 | 2.856 | 184 | 64.4258
7.7 | 7.4418 | 1 | 2.856 | 184 | 64.4258
8.9 | 8.4753 | 1 | 2.856 | 184 | 64.4258
11.3 | 10.1953 | 1 | 2.856 | 184 | 64.4258
12.7 | 11.2831 | 1 | 2.856 | 184 | 64.4258
13.2 | 11.765 | 1 | 2.856 | 184 | 64.4258
14.1 | 12.4669 | 1 | 2.856 | 184 | 64.4258
15.3 | 13.3382 | 1 | 2.856 | 184 | 64.4258
16.2 | 13.6917 | 1 | 2.856 | 184 | 64.4258
16.6 | 13.9028 | 1 | 2.856 | 184 | 64.4258
16.1 | 13.7071 | 1 | 2.856 | 184 | 64.4258
15.5 | 13.5277 | 1 | 2.856 | 184 | 64.4258
14.7 | 13.2114 | 1 | 2.856 | 184 | 64.4258
13.4 | 12.7478 | 1 | 2.856 | 184 | 64.4258
12.2 | 11.9664 | 1 | 2.856 | 184 | 64.4258
12.5 | 12.2648 | 1 | 2.856 | 184 | 64.4258
11.7 | 11.4693 | 1 | 2.856 | 184 | 64.4258
11.7 | 11.4693 | 1 | 2.856 | 184 | 64.4258
11 | 10.7731 | 1 | 2.856 | 184 | 64.4258
10.8 | 10.6867 | 1 | 2.856 | 184 | 64.4258
10.1 | 10.1 | 1 | 2.856 | 184 | 64.4258
11.2 | 11.2 | 1 | 2.856 | 184 | 64.4258
11.5 | 11.5 | 1 | 2.856 | 184 | 64.4258
11.5 | 11.5 | 1 | 2.856 | 184 | 64.4258
11.7 | 11.7 | 1 | 2.856 | 184 | 64.4258
11.5 | 11.5 | 1 | 2.856 | 184 | 64.4258
11 | 11 | 1 | 2.856 | 184 | 64.4258
11.3 | 11.3 | 1 | 2.856 | 184 | 64.4258
11.8 | 11.8 | 1 | 2.856 | 184 | 64.4258
12.6 | 12.364 | 1 | 2.856 | 184 | 64.4258
13.9 | 13.0062 | 1 | 2.856 | 184 | 64.4258
16 | 13.9463 | 1 | 2.856 | 184 | 64.4258
16.5 | 14.3092 | 1 | 2.856 | 184 | 64.4258
16.8 | 14.5376 | 1 | 2.856 | 184 | 64.4258
16.8 | 14.4227 | 1 | 2.856 | 184 | 64.4258
16.1 | 14.3864 | 1 | 2.856 | 184 | 64.4258
14.5 | 13.4177 | 1 | 2.856 | 184 | 64.4258
14.6 | 13.5153 | 1 | 2.856 | 184 | 64.4258
13.4 | 12.9812 | 1 | 2.856 | 184 | 64.4258
13.1 | 12.7429 | 1 | 2.856 | 184 | 64.4258
13.1 | 12.861 | 1 | 2.856 | 184 | 64.4258
12.2 | 12.2 | 1 | 2.856 | 184 | 64.4258
12.7 | 12.7 | 1 | 2.856 | 184 | 64.4258
12.3 | 12.3 | 1 | 2.856 | 184 | 64.4258
12.4 | 12.4 | 1 | 2.856 | 184 | 64.4258
12.5 | 12.5 | 1 | 2.856 | 184 | 64.4258
12.3 | 12.3 | 1 | 2.856 | 184 | 64.4258
12.3 | 12.3 | 1 | 2.856 | 184 | 64.4258
12.2 | 12.2 | 1 | 2.856 | 184 | 64.4258
12 | 12 | 1 | 2.856 | 184 | 64.4258
12.1 | 12.1 | 1 | 2.856 | 184 | 64.4258
12.7 | 12.7 | 1 | 2.856 | 184 | 64.4258
12.7 | 12.4632 | 1 | 2.856 | 184 | 64.4258
14.7 | 13.9671 | 1 | 2.856 | 184 | 64.4258
15.8 | 14.507 | 1 | 2.856 | 184 | 64.4258
16.4 | 14.8509 | 1 | 2.856 | 184 | 64.4258
16.7 | 14.9629 | 1 | 2.856 | 184 | 64.4258
17.6 | 15.4133 | 1 | 2.856 | 184 | 64.4258
17.1 | 15.2294 | 1 | 2.856 | 184 | 64.4258
16.9 | 15.3946 | 1 | 2.856 | 184 | 64.4258
16.5 | 15.2479 | 1 | 2.856 | 184 | 64.4258
15.7 | 15.1355 | 1 | 2.856 | 184 | 64.4258
15.5 | 15.3107 | 1 | 2.856 | 184 | 64.4258
15.3 | 15.0492 | 1 | 2.856 | 184 | 64.4258
15 | 14.8749 | 1 | 2.856 | 184 | 64.4258
15 | 14.8749 | 1 | 2.856 | 184 | 64.4258
15 | 14.7507 | 1 | 2.856 | 184 | 64.4258
14.8 | 14.6135 | 1 | 2.856 | 184 | 64.4258
14.6 | 14.3529 | 1 | 2.856 | 184 | 64.4258
14.5 | 13.9503 | 1 | 2.856 | 184 | 64.4258
13.5 | 12.8455 | 1 | 2.856 | 184 | 64.4258
13.4 | 12.6315 | 1 | 2.856 | 184 | 64.4258
13.3 | 12.7072 | 1 | 2.856 | 184 | 64.4258
12.7 | 11.9445 | 1 | 2.856 | 184 | 64.4258
12.6 | 11.1843 | 1 | 2.856 | 184 | 64.4258
12.3 | 11.0028 | 1 | 2.856 | 184 | 64.4258
12.4 | 10.8329 | 1 | 2.856 | 184 | 64.4258
13.3 | 11.5359 | 1 | 2.856 | 184 | 64.4258
14.5 | 11.4228 | 1 | 2.856 | 184 | 64.4258
15 | 11.7335 | 1 | 2.856 | 184 | 64.4258
15 | 11.7335 | 1 | 2.856 | 184 | 64.4258
15.1 | 10.9555 | 1 | 2.856 | 184 | 64.4258
14.8 | 10.2372 | 1 | 2.856 | 184 | 64.4258
14 | 10.1552 | 1 | 2.856 | 184 | 64.4258
12.5 | 9.3001 | 1 | 2.856 | 184 | 64.4258
11.9 | 8.9355 | 1 | 2.856 | 184 | 64.4258
10.7 | 8.4735 | 1 | 2.856 | 184 | 64.4258
9.6 | 7.8132 | 1 | 2.856 | 184 | 64.4258
8.7 | 7.3812 | 1 | 2.856 | 184 | 64.4258
7.6 | 6.9433 | 1 | 2.856 | 184 | 64.4258
6.9 | 6.4507 | 1 | 2.856 | 184 | 64.4258
6.5 | 6.0562 | 1 | 2.856 | 184 | 64.4258
6.7 | 6.1567 | 1 | 2.856 | 184 | 64.4258
6.8 | 6.1589 | 1 | 2.856 | 184 | 64.4258
5.7 | 5.3619 | 1 | 2.856 | 184 | 64.4258
5.4 | 5.0651 | 1 | 2.856 | 184 | 64.4258
5.3 | 4.8264 | 1 | 2.856 | 184 | 64.4258
5.2 | 4.6365 | 1 | 2.856 | 184 | 64.4258
6 | 5.0996 | 1 | 2.856 | 184 | 64.4258
8.2 | 6.3537 | 1 | 2.856 | 184 | 64.4258
10.8 | 7.8448 | 1 | 2.856 | 184 | 64.4258
12.5 | 8.9936 | 1 | 2.856 | 184 | 64.4258
13.8 | 9.5429 | 1 | 2.856 | 184 | 64.4258
14.1 | 9.5906 | 1 | 2.856 | 184 | 64.4258
14.7 | 9.7342 | 1 | 2.856 | 184 | 64.4258
14.2 | 9.6357 | 1 | 2.856 | 184 | 64.4258
13.4 | 9.1023 | 1 | 2.856 | 184 | 64.4258
12.7 | 8.996 | 1 | 2.856 | 184 | 64.4258
11.5 | 8.7573 | 1 | 2.856 | 184 | 64.4258
11 | 8.571 | 1 | 2.856 | 184 | 64.4258
10 | 8.1011 | 1 | 2.856 | 184 | 64.4258
8.8 | 7.3845 | 1 | 2.856 | 184 | 64.4258
8 | 6.7575 | 1 | 2.856 | 184 | 64.4258
7.2 | 6.172 | 1 | 2.856 | 184 | 64.4258
6.7 | 5.78 | 1 | 2.856 | 184 | 64.4258
5.7 | 5.1274 | 1 | 2.856 | 184 | 64.4258
5.2 | 4.7743 | 1 | 2.856 | 184 | 64.4258
5 | 4.6693 | 1 | 2.856 | 184 | 64.4258
4.7 | 4.281 | 1 | 2.856 | 184 | 64.4258
4.7 | 4.281 | 1 | 2.856 | 184 | 64.4258
4.4 | 4.2133 | 1 | 2.856 | 184 | 64.4258
4.9 | 4.6633 | 1 | 2.856 | 184 | 64.4258
5.4 | 5.3031 | 1 | 2.856 | 184 | 64.4258
7.2 | 6.8958 | 1 | 2.856 | 184 | 64.4258
10.5 | 9.0622 | 1 | 2.856 | 184 | 64.4258
12.4 | 10.3685 | 1 | 2.856 | 184 | 64.4258
14.5 | 11.1294 | 1 | 2.856 | 184 | 64.4258
15.6 | 11.6895 | 1 | 2.856 | 184 | 64.4258
16.4 | 11.4638 | 1 | 2.856 | 184 | 64.4258
16.1 | 11.1988 | 1 | 2.856 | 184 | 64.4258
14.7 | 10.7796 | 1 | 2.856 | 184 | 64.4258
14.1 | 10.4707 | 1 | 2.856 | 184 | 64.4258
13.1 | 9.7028 | 1 | 2.856 | 184 | 64.4258
12.5 | 10.3065 | 1 | 2.856 | 184 | 64.4258
12.1 | 10.5428 | 1 | 2.856 | 184 | 64.4258
12 | 10.765 | 1 | 2.856 | 184 | 64.4258
12 | 11.0359 | 1 | 2.856 | 184 | 64.4258
11.1 | 10.5379 | 1 | 2.856 | 184 | 64.4258
11 | 10.4391 | 1 | 2.856 | 184 | 64.4258
11 | 10.4389 | 1 | 2.856 | 184 | 64.4258
11.3 | 10.6239 | 1 | 2.856 | 184 | 64.4258
11.1 | 10.5369 | 1 | 2.856 | 184 | 64.4258
11 | 10.4381 | 1 | 2.856 | 184 | 64.4258
11 | 10.5485 | 1 | 2.856 | 184 | 64.4258
10.9 | 10.673 | 1 | 2.856 | 184 | 64.4258
10.9 | 10.786 | 1 | 2.856 | 184 | 64.4258
10.9 | 10.6729 | 1 | 2.856 | 184 | 64.4258
11 | 10.7723 | 1 | 2.856 | 184 | 64.4258
12.6 | 11.73 | 1 | 2.856 | 184 | 64.4258
13.5 | 11.2908 | 1 | 2.856 | 184 | 64.4258
13.2 | 10.8001 | 1 | 2.856 | 184 | 64.4258
14.3 | 11.1162 | 1 | 2.856 | 184 | 64.4258
14.8 | 11.177 | 1 | 2.856 | 184 | 64.4258
13.9 | 10.9425 | 1 | 2.856 | 184 | 64.4258
13.3 | 11.0961 | 1 | 2.856 | 184 | 64.4258
12.7 | 12.0532 | 1 | 2.856 | 184 | 64.4258
11.7 | 10.8458 | 1 | 2.856 | 184 | 64.4258
11.5 | 10.1635 | 1 | 2.856 | 184 | 64.4258
11.2 | 9.9789 | 1 | 2.856 | 184 | 64.4258
11.1 | 9.9879 | 1 | 2.856 | 184 | 64.4258
11.2 | 9.9784 | 1 | 2.856 | 184 | 64.4258
11.1 | 9.8805 | 1 | 2.856 | 184 | 64.4258
11.3 | 9.8628 | 1 | 2.856 | 184 | 64.4258
11.4 | 9.906 | 1 | 2.856 | 184 | 64.4258
10.4 | 9.3066 | 1 | 2.856 | 184 | 64.4258
9.1 | 8.1976 | 1 | 2.856 | 184 | 64.4258
8.1 | 6.9771 | 1 | 2.856 | 184 | 64.4258
6.9 | 5.864 | 1 | 2.856 | 184 | 64.4258
6.2 | 4.8707 | 1 | 2.856 | 184 | 64.4258
6.2 | 4.6949 | 1 | 2.856 | 184 | 64.4258
6.9 | 5.0557 | 1 | 2.856 | 184 | 64.4258
8.8 | 6.3546 | 1 | 2.856 | 184 | 64.4258
10.1 | 7.2033 | 1 | 2.856 | 184 | 64.4258
11.3 | 7.2732 | 1 | 2.856 | 184 | 64.4258
11.2 | 7.1048 | 1 | 2.856 | 184 | 64.4258
12.3 | 7.7057 | 1 | 2.856 | 184 | 64.4258
10.9 | 8.1614 | 1 | 2.856 | 184 | 64.4258
10.9 | 7.3274 | 1 | 2.856 | 184 | 64.4258
9.3 | 7.2704 | 1 | 2.856 | 184 | 64.4258
8.6 | 6.7946 | 1 | 2.856 | 184 | 64.4258
8.8 | 6.9376 | 1 | 2.856 | 184 | 64.4258
8.1 | 6.3222 | 1 | 2.856 | 184 | 64.4258
8.8 | 6.9385 | 1 | 2.856 | 184 | 64.4258
8.6 | 7.0763 | 1 | 2.856 | 184 | 64.4258
8.5 | 7.1717 | 1 | 2.856 | 184 | 64.4258
8.4 | 7.0749 | 1 | 2.856 | 184 | 64.4258
8.8 | 7.1716 | 1 | 2.856 | 184 | 64.4258
8.8 | 7.6554 | 1 | 2.856 | 184 | 64.4258
8.8 | 7.6548 | 1 | 2.856 | 184 | 64.4258
8.7 | 7.7572 | 1 | 2.856 | 184 | 64.4258
8.3 | 7.8243 | 1 | 2.856 | 184 | 64.4258
8.2 | 7.9865 | 1 | 2.856 | 184 | 64.4258
9 | 8.7815 | 1 | 2.856 | 184 | 64.4258
12.2 | 11.9628 | 1 | 2.856 | 184 | 64.4258
14.7 | 13.2465 | 1 | 2.856 | 184 | 64.4258
14.9 | 13.3813 | 1 | 2.856 | 184 | 64.4258
15.8 | 12.6769 | 1 | 2.856 | 184 | 64.4258
13.5 | 9.0191 | 1 | 2.856 | 184 | 64.4258
12.9 | 8.8833 | 1 | 2.856 | 184 | 64.4258
12.2 | 8.3934 | 1 | 2.856 | 184 | 64.4258
12.8 | 8.3334 | 1 | 2.856 | 184 | 64.4258
11 | 8.2038 | 1 | 2.856 | 184 | 64.4258
11.8 | 7.7518 | 1 | 2.856 | 184 | 64.4258
11.1 | 6.3719 | 1 | 2.856 | 184 | 64.4258
10 | 6.2102 | 1 | 2.856 | 184 | 64.4258
8.2 | 5.5952 | 1 | 2.856 | 184 | 64.4258
7.7 | 5.2601 | 1 | 2.856 | 184 | 64.4258
8.2 | 5.8926 | 1 | 2.856 | 184 | 64.4258
7.9 | 5.5728 | 1 | 2.856 | 184 | 64.4258
7.2 | 5.4328 | 1 | 2.856 | 184 | 64.4258
7.3 | 5.7052 | 1 | 2.856 | 184 | 64.4258
7.1 | 5.8771 | 1 | 2.856 | 184 | 64.4258
7.4 | 5.9821 | 1 | 2.856 | 184 | 64.4258
8 | 6.3252 | 1 | 2.856 | 184 | 64.4258
8.1 | 6.5119 | 1 | 2.856 | 184 | 64.4258
9 | 7.1349 | 1 | 2.856 | 184 | 64.4258
9.7 | 7.5617 | 1 | 2.856 | 184 | 64.4258
10 | 7.7503 | 1 | 2.856 | 184 | 64.4258
11.2 | 8.5413 | 1 | 2.856 | 184 | 64.4258
11.8 | 9.2405 | 1 | 2.856 | 184 | 64.4258
12.8 | 10.2205 | 1 | 2.856 | 184 | 64.4258
13.8 | 10.8999 | 1 | 2.856 | 184 | 64.4258
12.9 | 11.2457 | 1 | 2.856 | 184 | 64.4258
12.4 | 11.4193 | 1 | 2.856 | 184 | 64.4258
11.8 | 10.8883 | 1 | 2.856 | 184 | 64.4258
11 | 10.7712 | 1 | 2.856 | 184 | 64.4258
11 | 10.771 | 1 | 2.856 | 184 | 64.4258
10.8 | 10.5721 | 1 | 2.856 | 184 | 64.4258
10.8 | 10.572 | 1 | 2.856 | 184 | 64.4258
12.5 | 12.2033 | 1 | 2.856 | 184 | 64.4258
14.3 | 13.6873 | 1 | 2.856 | 184 | 64.4258
14.9 | 14.0972 | 1 | 2.856 | 184 | 64.4258
14.8 | 14.2415 | 1 | 2.856 | 184 | 64.4258
14.9 | 14.4017 | 1 | 2.856 | 184 | 64.4258
13.5 | 12.9573 | 1 | 2.856 | 184 | 64.4258
13 | 12.6998 | 1 | 2.856 | 184 | 64.4258
12.6 | 12.3617 | 1 | 2.856 | 184 | 64.4258
12.4 | 11.9291 | 1 | 2.856 | 184 | 64.4258
11.6 | 11.0251 | 1 | 2.856 | 184 | 64.4258
11.3 | 10.6177 | 1 | 2.856 | 184 | 64.4258
11.1 | 10.4211 | 1 | 2.856 | 184 | 64.4258
10.9 | 10.4461 | 1 | 2.856 | 184 | 64.4258
11 | 10.6009 | 1 | 2.856 | 184 | 64.4258
11.5 | 10.9261 | 1 | 2.856 | 184 | 64.4258
11.8 | 11.3355 | 1 | 2.856 | 184 | 64.4258
12.4 | 11.2484 | 1 | 2.856 | 184 | 64.4258
12.6 | 11.4986 | 1 | 2.856 | 184 | 64.4258
14.4 | 11.6494 | 1 | 2.856 | 184 | 64.4258
12.9 | 10.1991 | 1 | 2.856 | 184 | 64.4258
11.2 | 9.2025 | 1 | 2.856 | 184 | 64.4258
10.8 | 8.2011 | 1 | 2.856 | 184 | 64.4258
10.2 | 7.7364 | 1 | 2.856 | 184 | 64.4258
9.1 | 6.4954 | 1 | 2.856 | 184 | 64.4258
8.8 | 6.5245 | 1 | 2.856 | 184 | 64.4258
8.7 | 6.6554 | 1 | 2.856 | 184 | 64.4258
6.1 | 5.1799 | 1 | 2.856 | 184 | 64.4258
6 | 5.2222 | 1 | 2.856 | 184 | 64.4258
5.4 | 4.41 | 1 | 2.856 | 184 | 64.4258
6 | 4.9914 | 1 | 2.856 | 184 | 64.4258
6 | 4.8554 | 1 | 2.856 | 184 | 64.4258
5.2 | 3.9539 | 1 | 2.856 | 184 | 64.4258
5 | 3.8923 | 1 | 2.856 | 184 | 64.4258
4.9 | 3.8836 | 1 | 2.856 | 184 | 64.4258
4.8 | 3.8751 | 1 | 2.856 | 184 | 64.4258
4.6 | 3.5947 | 1 | 2.856 | 184 | 64.4258
4.7 | 3.5627 | 1 | 2.856 | 184 | 64.4258
6 | 4.293 | 1 | 2.856 | 184 | 64.4258
7.5 | 5.2366 | 1 | 2.856 | 184 | 64.4258
9.2 | 6.0116 | 1 | 2.856 | 184 | 64.4258
10.4 | 6.6072 | 1 | 2.856 | 184 | 64.4258
10.5 | 6.5793 | 1 | 2.856 | 184 | 64.4258
10.3 | 6.0237 | 1 | 2.856 | 184 | 64.4258
10.9 | 6.4343 | 1 | 2.856 | 184 | 64.4258
10.7 | 6.5649 | 1 | 2.856 | 184 | 64.4258
10.4 | 6.6147 | 1 | 2.856 | 184 | 64.4258
9.5 | 5.9742 | 1 | 2.856 | 184 | 64.4258
8 | 4.9806 | 1 | 2.856 | 184 | 64.4258
7 | 4.5019 | 1 | 2.856 | 184 | 64.4258
6.9 | 4.6514 | 1 | 2.856 | 184 | 64.4258
5 | 3.6469 | 1 | 2.856 | 184 | 64.4258
5.2 | 3.8385 | 1 | 2.856 | 184 | 64.4258
5 | 3.3199 | 1 | 2.856 | 184 | 64.4258
3.9 | 2.8839 | 1 | 2.856 | 184 | 64.4258
3.6 | 3.1485 | 1 | 2.856 | 184 | 64.4258
3.1 | 2.6561 | 1 | 2.856 | 184 | 64.4258
4.2 | 3.5169 | 1 | 2.856 | 184 | 64.4258
2.8 | 2.4466 | 1 | 2.856 | 184 | 64.4258
3.9 | 3.311 | 1 | 2.856 | 184 | 64.4258
4.5 | 3.9437 | 1 | 2.856 | 184 | 64.4258
5.2 | 4.6309 | 1 | 2.856 | 184 | 64.4258
7.2 | 6.2085 | 1 | 2.856 | 184 | 64.4258
7.6 | 6.9372 | 1 | 2.856 | 184 | 64.4258
9.8 | 8.3277 | 1 | 2.856 | 184 | 64.4258
11 | 8.7833 | 1 | 2.856 | 184 | 64.4258
11.6 | 8.8194 | 1 | 2.856 | 184 | 64.4258
12 | 8.9063 | 1 | 2.856 | 184 | 64.4258
10.6 | 9.2455 | 1 | 2.856 | 184 | 64.4258
11 | 9.3216 | 1 | 2.856 | 184 | 64.4258
11 | 9.6814 | 1 | 2.856 | 184 | 64.4258
10.5 | 9.9416 | 1 | 2.856 | 184 | 64.4258
10.9 | 10.2254 | 1 | 2.856 | 184 | 64.4258
11 | 10.4337 | 1 | 2.856 | 184 | 64.4258
11.5 | 10.9827 | 1 | 2.856 | 184 | 64.4258
11.5 | 10.9827 | 1 | 2.856 | 184 | 64.4258
11.5 | 10.3749 | 1 | 2.856 | 184 | 64.4258
11 | 9.3673 | 1 | 2.856 | 184 | 64.4258
10.5 | 8.2527 | 1 | 2.856 | 184 | 64.4258
10 | 7.7841 | 1 | 2.856 | 184 | 64.4258
9.5 | 7.4537 | 1 | 2.856 | 184 | 64.4258
10 | 7.5975 | 1 | 2.856 | 184 | 64.4258
9.8 | 7.5481 | 1 | 2.856 | 184 | 64.4258
10 | 7.5963 | 1 | 2.856 | 184 | 64.4258
9.7 | 8.4726 | 1 | 2.856 | 184 | 64.4258
8.5 | 7.7122 | 1 | 2.856 | 184 | 64.4258
8.5 | 7.6109 | 1 | 2.856 | 184 | 64.4258
8.8 | 7.6025 | 1 | 2.856 | 184 | 64.4258
9.7 | 8.0237 | 1 | 2.856 | 184 | 64.4258
10.3 | 8.0631 | 1 | 2.856 | 184 | 64.4258
11 | 8.7679 | 1 | 2.856 | 184 | 64.4258
11.4 | 8.8541 | 1 | 2.856 | 184 | 64.4258
11.9 | 8.8932 | 1 | 2.856 | 184 | 64.4258
11.6 | 8.7118 | 1 | 2.856 | 184 | 64.4258
11.4 | 8.302 | 1 | 2.856 | 184 | 64.4258
11.1 | 7.5524 | 1 | 2.856 | 184 | 64.4258
10.5 | 7.2698 | 1 | 2.856 | 184 | 64.4258
9.5 | 6.5762 | 1 | 2.856 | 184 | 64.4258
8.8 | 5.7759 | 1 | 2.856 | 184 | 64.4258
8.3 | 5.5661 | 1 | 2.856 | 184 | 64.4258
7.5 | 5.2447 | 1 | 2.856 | 184 | 64.4258
7.1 | 4.9157 | 1 | 2.856 | 184 | 64.4258
6.8 | 5.0147 | 1 | 2.856 | 184 | 64.4258
6.7 | 5.007 | 1 | 2.856 | 184 | 64.4258
6 | 4.5585 | 1 | 2.856 | 184 | 64.4258
5.6 | 4.2205 | 1 | 2.856 | 184 | 64.4258
5.4 | 3.9459 | 1 | 2.856 | 184 | 64.4258
5.5 | 3.9166 | 1 | 2.856 | 184 | 64.4258
5 | 3.7759 | 1 | 2.856 | 184 | 64.4258
4.6 | 3.4769 | 1 | 2.856 | 184 | 64.4258
5.8 | 4.4587 | 1 | 2.856 | 184 | 64.4258
8.1 | 5.986 | 1 | 2.856 | 184 | 64.4258
9.9 | 7.2227 | 1 | 2.856 | 184 | 64.4258
11.6 | 7.7434 | 1 | 2.856 | 184 | 64.4258
12.5 | 8.1693 | 1 | 2.856 | 184 | 64.4258
12.7 | 8.0653 | 1 | 2.856 | 184 | 64.4258
12.1 | 8.0236 | 1 | 2.856 | 184 | 64.4258
12.4 | 8.0857 | 1 | 2.856 | 184 | 64.4258
11.5 | 8.2099 | 1 | 2.856 | 184 | 64.4258
9.6 | 7.259 | 1 | 2.856 | 184 | 64.4258
10 | 7.3651 | 1 | 2.856 | 184 | 64.4258
9.6 | 7.3049 | 1 | 2.856 | 184 | 64.4258
8.3 | 6.8545 | 1 | 2.856 | 184 | 64.4258
8.8 | 7.0989 | 1 | 2.856 | 184 | 64.4258
8.8 | 7.2387 | 1 | 2.856 | 184 | 64.4258
8.5 | 7.0929 | 1 | 2.856 | 184 | 64.4258
8.1 | 7.0408 | 1 | 2.856 | 184 | 64.4258
8.5 | 7.7742 | 1 | 2.856 | 184 | 64.4258
9 | 8.3663 | 1 | 2.856 | 184 | 64.4258
9.7 | 8.9491 | 1 | 2.856 | 184 | 64.4258
10.3 | 9.5369 | 1 | 2.856 | 184 | 64.4258
11 | 10.0086 | 1 | 2.856 | 184 | 64.4258
11.2 | 10.4183 | 1 | 2.856 | 184 | 64.4258
11.7 | 10.908 | 1 | 2.856 | 184 | 64.4258
12.1 | 11.2446 | 1 | 2.856 | 184 | 64.4258
12.4 | 11.6502 | 1 | 2.856 | 184 | 64.4258
12.6 | 11.9029 | 1 | 2.856 | 184 | 64.4258
12.5 | 11.9183 | 1 | 2.856 | 184 | 64.4258
13 | 12.3534 | 1 | 2.856 | 184 | 64.4258
13.1 | 12.5675 | 1 | 2.856 | 184 | 64.4258
13.2 | 12.0941 | 1 | 2.856 | 184 | 64.4258
13.5 | 12.8453 | 1 | 2.856 | 184 | 64.4258
13.7 | 13.0422 | 1 | 2.856 | 184 | 64.4258
14.1 | 13.4362 | 1 | 2.856 | 184 | 64.4258
14.4 | 13.8513 | 1 | 2.856 | 184 | 64.4258
14.6 | 14.2916 | 1 | 2.856 | 184 | 64.4258
15.1 | 14.482 | 1 | 2.856 | 184 | 64.4258
15.1 | 14.482 | 1 | 2.856 | 184 | 64.4258
15.1 | 14.4214 | 1 | 2.856 | 184 | 64.4258
15 | 14.444 | 1 | 2.856 | 184 | 64.4258
15 | 14.444 | 1 | 2.856 | 184 | 64.4258
15 | 14.3229 | 1 | 2.856 | 184 | 64.4258
15 | 14.3229 | 1 | 2.856 | 184 | 64.4258
15 | 14.2626 | 1 | 2.856 | 184 | 64.4258
15 | 14.3229 | 1 | 2.856 | 184 | 64.4258
14.7 | 14.2689 | 1 | 2.856 | 184 | 64.4258
14.6 | 14.1697 | 1 | 2.856 | 184 | 64.4258
14.6 | 14.1697 | 1 | 2.856 | 184 | 64.4258
15.1 | 14.5426 | 1 | 2.856 | 184 | 64.4258
15.2 | 14.6414 | 1 | 2.856 | 184 | 64.4258
15.6 | 14.8527 | 1 | 2.856 | 184 | 64.4258
15.5 | 14.8762 | 1 | 2.856 | 184 | 64.4258
15.9 | 14.9034 | 1 | 2.856 | 184 | 64.4258
15.6 | 14.4898 | 1 | 2.856 | 184 | 64.4258
15.8 | 14.3871 | 1 | 2.856 | 184 | 64.4258
15.4 | 14.3534 | 1 | 2.856 | 184 | 64.4258
15 | 14.2612 | 1 | 2.856 | 184 | 64.4258
14.7 | 14.2681 | 1 | 2.856 | 184 | 64.4258
14.8 | 14.1242 | 1 | 2.856 | 184 | 64.4258
14.8 | 14.1242 | 1 | 2.856 | 184 | 64.4258
14.2 | 13.9545 | 1 | 2.856 | 184 | 64.4258
13.3 | 12.5311 | 1 | 2.856 | 184 | 64.4258
12.4 | 11.2582 | 1 | 2.856 | 184 | 64.4258
11.6 | 10.0581 | 1 | 2.856 | 184 | 64.4258
10.5 | 8.6083 | 1 | 2.856 | 184 | 64.4258
9.5 | 6.8491 | 1 | 2.856 | 184 | 64.4258
8.2 | 6.3419 | 1 | 2.856 | 184 | 64.4258
6.5 | 5.4875 | 1 | 2.856 | 184 | 64.4258
5.7 | 4.8933 | 1 | 2.856 | 184 | 64.4258
5.4 | 4.7377 | 1 | 2.856 | 184 | 64.4258
5.7 | 4.7586 | 1 | 2.856 | 184 | 64.4258
5.4 | 4.5122 | 1 | 2.856 | 184 | 64.4258
6.3 | 5.0706 | 1 | 2.856 | 184 | 64.4258
7.6 | 6.0465 | 1 | 2.856 | 184 | 64.4258
9.6 | 7.1678 | 1 | 2.856 | 184 | 64.4258
11.1 | 7.889 | 1 | 2.856 | 184 | 64.4258
12 | 8.269 | 1 | 2.856 | 184 | 64.4258
11.8 | 8.1751 | 1 | 2.856 | 184 | 64.4258
12.2 | 8.3203 | 1 | 2.856 | 184 | 64.4258
11.2 | 7.9349 | 1 | 2.856 | 184 | 64.4258
10.8 | 7.8323 | 1 | 2.856 | 184 | 64.4258
10.7 | 7.6971 | 1 | 2.856 | 184 | 64.4258
10.8 | 7.7029 | 1 | 2.856 | 184 | 64.4258
10.2 | 7.5029 | 1 | 2.856 | 184 | 64.4258
9.8 | 7.811 | 1 | 2.856 | 184 | 64.4258
9.6 | 7.8572 | 1 | 2.856 | 184 | 64.4258
9.5 | 7.6202 | 1 | 2.856 | 184 | 64.4258
9.2 | 7.5234 | 1 | 2.856 | 184 | 64.4258
9.3 | 7.7607 | 1 | 2.856 | 184 | 64.4258
9.8 | 8.3852 | 1 | 2.856 | 184 | 64.4258
9.6 | 8.4912 | 1 | 2.856 | 184 | 64.4258
9.8 | 8.6845 | 1 | 2.856 | 184 | 64.4258
10 | 8.8778 | 1 | 2.856 | 184 | 64.4258
10.5 | 8.9551 | 1 | 2.856 | 184 | 64.4258
10.9 | 9.2359 | 1 | 2.856 | 184 | 64.4258
11.2 | 9.4719 | 1 | 2.856 | 184 | 64.4258
12 | 10.0296 | 1 | 2.856 | 184 | 64.4258
12.6 | 10.1928 | 1 | 2.856 | 184 | 64.4258
12.8 | 10.5818 | 1 | 2.856 | 184 | 64.4258
13.3 | 10.8482 | 1 | 2.856 | 184 | 64.4258
13.1 | 11.3364 | 1 | 2.856 | 184 | 64.4258
13 | 11.674 | 1 | 2.856 | 184 | 64.4258
13.1 | 12.2199 | 1 | 2.856 | 184 | 64.4258
12.5 | 11.9735 | 1 | 2.856 | 184 | 64.4258
11.5 | 10.9302 | 1 | 2.856 | 184 | 64.4258
11.3 | 9.873 | 1 | 2.856 | 184 | 64.4258
10.3 | 8.5142 | 1 | 2.856 | 184 | 64.4258
9.9 | 8.134 | 1 | 2.856 | 184 | 64.4258
9.1 | 7.7576 | 1 | 2.856 | 184 | 64.4258
8.5 | 7.3744 | 1 | 2.856 | 184 | 64.4258
7.9 | 6.8901 | 1 | 2.856 | 184 | 64.4258
6.6 | 5.9109 | 1 | 2.856 | 184 | 64.4258
6.4 | 5.7155 | 1 | 2.856 | 184 | 64.4258
6 | 5.4651 | 1 | 2.856 | 184 | 64.4258
7 | 6.3512 | 1 | 2.856 | 184 | 64.4258
7.2 | 6.5472 | 1 | 2.856 | 184 | 64.4258
8.1 | 7.1821 | 1 | 2.856 | 184 | 64.4258
7.9 | 7.0362 | 1 | 2.856 | 184 | 64.4258
8.1 | 7.1332 | 1 | 2.856 | 184 | 64.4258
8.4 | 7.1815 | 1 | 2.856 | 184 | 64.4258
8.6 | 7.5206 | 1 | 2.856 | 184 | 64.4258
9.1 | 7.5666 | 1 | 2.856 | 184 | 64.4258
10.2 | 7.9935 | 1 | 2.856 | 184 | 64.4258
10.8 | 8.0468 | 1 | 2.856 | 184 | 64.4258
11.7 | 9.064 | 1 | 2.856 | 184 | 64.4258
13 | 9.6491 | 1 | 2.856 | 184 | 64.4258
12 | 9.0125 | 1 | 2.856 | 184 | 64.4258
12.3 | 9.1937 | 1 | 2.856 | 184 | 64.4258
12.3 | 9.1923 | 1 | 2.856 | 184 | 64.4258
11 | 9.5849 | 1 | 2.856 | 184 | 64.4258
10.6 | 9.827 | 1 | 2.856 | 184 | 64.4258
10.5 | 9.8362 | 1 | 2.856 | 184 | 64.4258
10.4 | 9.7385 | 1 | 2.856 | 184 | 64.4258
10.1 | 9.2855 | 1 | 2.856 | 184 | 64.4258
10 | 9.1884 | 1 | 2.856 | 184 | 64.4258
9.8 | 8.9935 | 1 | 2.856 | 184 | 64.4258
9.1 | 8.2591 | 1 | 2.856 | 184 | 64.4258
7.1 | 6.5985 | 1 | 2.856 | 184 | 64.4258
7.2 | 6.455 | 1 | 2.856 | 184 | 64.4258
5.6 | 5.0298 | 1 | 2.856 | 184 | 64.4258
4.7 | 4.237 | 1 | 2.856 | 184 | 64.4258
5.4 | 4.6532 | 1 | 2.856 | 184 | 64.4258
5 | 4.352 | 1 | 2.856 | 184 | 64.4258
5 | 4.3523 | 1 | 2.856 | 184 | 64.4258
5.6 | 4.8944 | 1 | 2.856 | 184 | 64.4258
7.4 | 6.2762 | 1 | 2.856 | 184 | 64.4258
8.9 | 7.067 | 1 | 2.856 | 184 | 64.4258
10.6 | 8.0245 | 1 | 2.856 | 184 | 64.4258
12.2 | 8.9549 | 1 | 2.856 | 184 | 64.4258
13.2 | 9.1105 | 1 | 2.856 | 184 | 64.4258
13.8 | 9.1766 | 1 | 2.856 | 184 | 64.4258
13.4 | 8.6645 | 1 | 2.856 | 184 | 64.4258
13 | 8.807 | 1 | 2.856 | 184 | 64.4258
10.1 | 7.5163 | 1 | 2.856 | 184 | 64.4258
10.1 | 7.7403 | 1 | 2.856 | 184 | 64.4258
9.8 | 7.5968 | 1 | 2.856 | 184 | 64.4258
8.7 | 7.1536 | 1 | 2.856 | 184 | 64.4258
8 | 6.5771 | 1 | 2.856 | 184 | 64.4258
7.8 | 6.71 | 1 | 2.856 | 184 | 64.4258
7.2 | 6.2231 | 1 | 2.856 | 184 | 64.4258
6.2 | 5.4815 | 1 | 2.856 | 184 | 64.4258
6.3 | 5.6257 | 1 | 2.856 | 184 | 64.4258
5.9 | 5.3266 | 1 | 2.856 | 184 | 64.4258
5.5 | 5.0724 | 1 | 2.856 | 184 | 64.4258
4.4 | 4.1228 | 1 | 2.856 | 184 | 64.4258
4.5 | 4.0859 | 1 | 2.856 | 184 | 64.4258
5 | 4.7175 | 1 | 2.856 | 184 | 64.4258
4.5 | 4.1765 | 1 | 2.856 | 184 | 64.4258
5.5 | 4.8885 | 1 | 2.856 | 184 | 64.4258
6.8 | 6.0683 | 1 | 2.856 | 184 | 64.4258
8.7 | 7.5811 | 1 | 2.856 | 184 | 64.4258
11.1 | 9.0529 | 1 | 2.856 | 184 | 64.4258
12.6 | 9.928 | 1 | 2.856 | 184 | 64.4258
13.7 | 10.2754 | 1 | 2.856 | 184 | 64.4258
14.1 | 10.1778 | 1 | 2.856 | 184 | 64.4258
13.1 | 9.8217 | 1 | 2.856 | 184 | 64.4258
12.6 | 9.8789 | 1 | 2.856 | 184 | 64.4258
11.7 | 9.5684 | 1 | 2.856 | 184 | 64.4258
11 | 9.005 | 1 | 2.856 | 184 | 64.4258
9.9 | 8.3465 | 1 | 2.856 | 184 | 64.4258
9.4 | 7.8202 | 1 | 2.856 | 184 | 64.4258
8.7 | 7.726 | 1 | 2.856 | 184 | 64.4258
8.1 | 7.2399 | 1 | 2.856 | 184 | 64.4258
8.3 | 7.3859 | 1 | 2.856 | 184 | 64.4258
7 | 6.4539 | 1 | 2.856 | 184 | 64.4258
5.8 | 5.3675 | 1 | 2.856 | 184 | 64.4258
5.3 | 5.0142 | 1 | 2.856 | 184 | 64.4258
4.7 | 4.3735 | 1 | 2.856 | 184 | 64.4258
4.5 | 4.4062 | 1 | 2.856 | 184 | 64.4258
3.6 | 3.6 | 1 | 2.856 | 184 | 64.4258
4.4 | 4.3531 | 1 | 2.856 | 184 | 64.4258
3.6 | 3.5089 | 1 | 2.856 | 184 | 64.4258
3.6 | 3.5089 | 1 | 2.856 | 184 | 64.4258
4.7 | 4.6527 | 1 | 2.856 | 184 | 64.4258
5.9 | 5.6564 | 1 | 2.856 | 184 | 64.4258
9.1 | 8.213 | 1 | 2.856 | 184 | 64.4258
11.5 | 9.5223 | 1 | 2.856 | 184 | 64.4258
12.6 | 10.0641 | 1 | 2.856 | 184 | 64.4258
12.9 | 9.9081 | 1 | 2.856 | 184 | 64.4258
12.8 | 9.9097 | 1 | 2.856 | 184 | 64.4258
11.9 | 9.4569 | 1 | 2.856 | 184 | 64.4258
10.7 | 8.9083 | 1 | 2.856 | 184 | 64.4258
10.2 | 8.6768 | 1 | 2.856 | 184 | 64.4258
8.8 | 7.721 | 1 | 2.856 | 184 | 64.4258
8.7 | 7.8709 | 1 | 2.856 | 184 | 64.4258
7.6 | 7.0418 | 1 | 2.856 | 184 | 64.4258
6.4 | 6.0058 | 1 | 2.856 | 184 | 64.4258
7.4 | 6.944 | 1 | 2.856 | 184 | 64.4258
8 | 7.385 | 1 | 2.856 | 184 | 64.4258
8.1 | 7.6344 | 1 | 2.856 | 184 | 64.4258
8.1 | 7.6341 | 1 | 2.856 | 184 | 64.4258
8.3 | 7.8826 | 1 | 2.856 | 184 | 64.4258
8.6 | 8.0758 | 1 | 2.856 | 184 | 64.4258
8.4 | 8.2413 | 1 | 2.856 | 184 | 64.4258
8.8 | 8.481 | 1 | 2.856 | 184 | 64.4258
9.2 | 8.7193 | 1 | 2.856 | 184 | 64.4258
9.5 | 8.8578 | 1 | 2.856 | 184 | 64.4258
9.9 | 9.2508 | 1 | 2.856 | 184 | 64.4258
10.2 | 9.2304 | 1 | 2.856 | 184 | 64.4258
9.9 | 9.0415 | 1 | 2.856 | 184 | 64.4258
10.6 | 9.3087 | 1 | 2.856 | 184 | 64.4258
11.4 | 8.6549 | 1 | 2.856 | 184 | 64.4258
12.1 | 8.0666 | 1 | 2.856 | 184 | 64.4258
11.9 | 7.8064 | 1 | 2.856 | 184 | 64.4258
10.7 | 7.6104 | 1 | 2.856 | 184 | 64.4258
9.3 | 6.8893 | 1 | 2.856 | 184 | 64.4258
8.8 | 6.8674 | 1 | 2.856 | 184 | 64.4258
7.8 | 6.3746 | 1 | 2.856 | 184 | 64.4258
7.9 | 6.5165 | 1 | 2.856 | 184 | 64.4258
6.6 | 5.7256 | 1 | 2.856 | 184 | 64.4258
7.3 | 6.2185 | 1 | 2.856 | 184 | 64.4258
7.2 | 6.3098 | 1 | 2.856 | 184 | 64.4258
6.8 | 6.2057 | 1 | 2.856 | 184 | 64.4258
7 | 6.4021 | 1 | 2.856 | 184 | 64.4258
6.4 | 5.9569 | 1 | 2.856 | 184 | 64.4258
5.9 | 5.2756 | 1 | 2.856 | 184 | 64.4258
5.6 | 4.5753 | 1 | 2.856 | 184 | 64.4258
4.7 | 3.922 | 1 | 2.856 | 184 | 64.4258
4.9 | 4.1611 | 1 | 2.856 | 184 | 64.4258
4.5 | 4.0379 | 1 | 2.856 | 184 | 64.4258
4.8 | 4.1087 | 1 | 2.856 | 184 | 64.4258
5.8 | 4.6814 | 1 | 2.856 | 184 | 64.4258
7.8 | 6.0176 | 1 | 2.856 | 184 | 64.4258
9.1 | 6.0408 | 1 | 2.856 | 184 | 64.4258
10.1 | 6.305 | 1 | 2.856 | 184 | 64.4258
10.6 | 6.7057 | 1 | 2.856 | 184 | 64.4258
11 | 7.0962 | 1 | 2.856 | 184 | 64.4258
10.8 | 7.2821 | 1 | 2.856 | 184 | 64.4258
10.3 | 6.7519 | 1 | 2.856 | 184 | 64.4258
9.3 | 6.4625 | 1 | 2.856 | 184 | 64.4258
8.9 | 6.4749 | 1 | 2.856 | 184 | 64.4258
8.6 | 6.2816 | 1 | 2.856 | 184 | 64.4258
7.8 | 5.9672 | 1 | 2.856 | 184 | 64.4258
7.9 | 6.1059 | 1 | 2.856 | 184 | 64.4258
8.7 | 6.7703 | 1 | 2.856 | 184 | 64.4258
9.8 | 7.9477 | 1 | 2.856 | 184 | 64.4258
9.5 | 7.9975 | 1 | 2.856 | 184 | 64.4258
9.6 | 8.2893 | 1 | 2.856 | 184 | 64.4258
10.3 | 8.8622 | 1 | 2.856 | 184 | 64.4258
10.7 | 9.1446 | 1 | 2.856 | 184 | 64.4258
10.4 | 9.161 | 1 | 2.856 | 184 | 64.4258
10.5 | 9.5177 | 1 | 2.856 | 184 | 64.4258
10.5 | 9.57 | 1 | 2.856 | 184 | 64.4258
11 | 9.7928 | 1 | 2.856 | 184 | 64.4258
10.8 | 9.8626 | 1 | 2.856 | 184 | 64.4258
11.8 | 10.0436 | 1 | 2.856 | 184 | 64.4258
12.7 | 10.1363 | 1 | 2.856 | 184 | 64.4258
13.3 | 9.0684 | 1 | 2.856 | 184 | 64.4258
10.5 | 9.57 | 1 | 2.856 | 184 | 64.4258
13.8 | 9.3357 | 1 | 2.856 | 184 | 64.4258
13.7 | 9.0788 | 1 | 2.856 | 184 | 64.4258
13.5 | 9.3301 | 1 | 2.856 | 184 | 64.4258
12.9 | 9.5999 | 1 | 2.856 | 184 | 64.4258
12.5 | 9.7054 | 1 | 2.856 | 184 | 64.4258
12.4 | 9.9536 | 1 | 2.856 | 184 | 64.4258
11.9 | 10.4507 | 1 | 2.856 | 184 | 64.4258
11.5 | 10.6541 | 1 | 2.856 | 184 | 64.4258
11.5 | 10.6541 | 1 | 2.856 | 184 | 64.4258
11.2 | 10.5244 | 1 | 2.856 | 184 | 64.4258
11.4 | 10.7763 | 1 | 2.856 | 184 | 64.4258
11 | 10.6599 | 1 | 2.856 | 184 | 64.4258
11.5 | 10.8193 | 1 | 2.856 | 184 | 64.4258
10.2 | 9.7575 | 1 | 2.856 | 184 | 64.4258
10.4 | 9.955 | 1 | 2.856 | 184 | 64.4258
10.5 | 9.9446 | 1 | 2.856 | 184 | 64.4258
10 | 9.3449 | 1 | 2.856 | 184 | 64.4258
10.1 | 9.3368 | 1 | 2.856 | 184 | 64.4258
10.4 | 9.419 | 1 | 2.856 | 184 | 64.4258
11 | 9.9501 | 1 | 2.856 | 184 | 64.4258
11 | 10.2183 | 1 | 2.856 | 184 | 64.4258
11.7 | 10.9043 | 1 | 2.856 | 184 | 64.4258
12.8 | 11.645 | 1 | 2.856 | 184 | 64.4258
13.6 | 11.5431 | 1 | 2.856 | 184 | 64.4258
14 | 11.0903 | 1 | 2.856 | 184 | 64.4258
13.6 | 10.7182 | 1 | 2.856 | 184 | 64.4258
13 | 10.5604 | 1 | 2.856 | 184 | 64.4258
13 | 10.31 | 1 | 2.856 | 184 | 64.4258
12.1 | 9.8158 | 1 | 2.856 | 184 | 64.4258
12.2 | 9.6142 | 1 | 2.856 | 184 | 64.4258
11.3 | 10.0796 | 1 | 2.856 | 184 | 64.4258
10.9 | 10.1186 | 1 | 2.856 | 184 | 64.4258
11 | 10.1074 | 1 | 2.856 | 184 | 64.4258
11.4 | 10.5522 | 1 | 2.856 | 184 | 64.4258
11.3 | 10.6192 | 1 | 2.856 | 184 | 64.4258
11.3 | 10.6744 | 1 | 2.856 | 184 | 64.4258
11.4 | 10.6614 | 1 | 2.856 | 184 | 64.4258
11.3 | 10.618 | 1 | 2.856 | 184 | 64.4258
11.4 | 10.4951 | 1 | 2.856 | 184 | 64.4258
10.1 | 8.8085 | 1 | 2.856 | 184 | 64.4258
8.5 | 6.1585 | 1 | 2.856 | 184 | 64.4258
8.6 | 6.2079 | 1 | 2.856 | 184 | 64.4258
7.6 | 5.3648 | 1 | 2.856 | 184 | 64.4258
7.1 | 4.3375 | 1 | 2.856 | 184 | 64.4258
6.6 | 4.6025 | 1 | 2.856 | 184 | 64.4258
5.5 | 4.157 | 1 | 2.856 | 184 | 64.4258
5.2 | 3.8298 | 1 | 2.856 | 184 | 64.4258
5.7 | 3.9699 | 1 | 2.856 | 184 | 64.4258
6.4 | 4.1372 | 1 | 2.856 | 184 | 64.4258
6.2 | 3.3688 | 1 | 2.856 | 184 | 64.4258
4.4 | 2.9474 | 1 | 2.856 | 184 | 64.4258
3.8 | 2.2613 | 1 | 2.856 | 184 | 64.4258
3.7 | 2.0416 | 1 | 2.856 | 184 | 64.4258
4 | 1.2194 | 1 | 2.856 | 184 | 64.4258
3.2 | 0.68569 | 1 | 2.856 | 184 | 64.4258
2.8 | -0.12776 | 1 | 2.856 | 184 | 64.4258
2.4 | -0.32162 | 1 | 2.856 | 184 | 64.4258
2 | -0.64235 | 1 | 2.856 | 184 | 64.4258
1.6 | -0.81018 | 1 | 2.856 | 184 | 64.4258
1.9 | -0.6359 | 1 | 2.856 | 184 | 64.4258
1.4 | -0.31752 | 1 | 2.856 | 184 | 64.4258
1.3 | 0.076542 | 1 | 2.856 | 184 | 64.4258
1.2 | -0.021056 | 1 | 2.856 | 184 | 64.4258
1.6 | 0.25548 | 1 | 2.856 | 184 | 64.4258
2.1 | 1.4675 | 1 | 2.856 | 184 | 64.4258
2.5 | 1.4577 | 1 | 2.856 | 184 | 64.4258
2.3 | 1.1255 | 1 | 2.856 | 184 | 64.4258
2.8 | 1.4131 | 1 | 2.856 | 184 | 64.4258
3.3 | 1.8275 | 1 | 2.856 | 184 | 64.4258
4.2 | 2.4975 | 1 | 2.856 | 184 | 64.4258
5 | 3.0558 | 1 | 2.856 | 184 | 64.4258
5.7 | 3.5527 | 1 | 2.856 | 184 | 64.4258
6.2 | 3.7838 | 1 | 2.856 | 184 | 64.4258
6.6 | 4.0375 | 1 | 2.856 | 184 | 64.4258
6.5 | 3.872 | 1 | 2.856 | 184 | 64.4258
5.8 | 3.5706 | 1 | 2.856 | 184 | 64.4258
5.2 | 3.2842 | 1 | 2.856 | 184 | 64.4258
4.7 | 3.0112 | 1 | 2.856 | 184 | 64.4258
4.5 | 2.7851 | 1 | 2.856 | 184 | 64.4258
4.1 | 2.5249 | 1 | 2.856 | 184 | 64.4258
3.1 | 1.8066 | 1 | 2.856 | 184 | 64.4258
2.4 | 1.1894 | 1 | 2.856 | 184 | 64.4258
2.1 | 1.0154 | 1 | 2.856 | 184 | 64.4258
1.1 | 0.2158 | 1 | 2.856 | 184 | 64.4258
0.7 | -0.14088 | 1 | 2.856 | 184 | 64.4258
0.3 | -0.40903 | 1 | 2.856 | 184 | 64.4258
-0.3 | -0.79517 | 1 | 2.856 | 184 | 64.4258
0.2 | -0.38673 | 1 | 2.856 | 184 | 64.4258
0.9 | -0.066511 | 1 | 2.856 | 184 | 64.4258
1.2 | -0.012256 | 1 | 2.856 | 184 | 64.4258
1.4 | 0.18725 | 1 | 2.856 | 184 | 64.4258
1.6 | 0.42789 | 1 | 2.856 | 184 | 64.4258
2.4 | 1.1476 | 1 | 2.856 | 184 | 64.4258
4.9 | 2.6926 | 1 | 2.856 | 184 | 64.4258
6.3 | 3.8466 | 1 | 2.856 | 184 | 64.4258
7.8 | 4.9073 | 1 | 2.856 | 184 | 64.4258
8 | 5.0099 | 1 | 2.856 | 184 | 64.4258
8.1 | 5.4147 | 1 | 2.856 | 184 | 64.4258
9 | 5.7171 | 1 | 2.856 | 184 | 64.4258
7.7 | 5.0488 | 1 | 2.856 | 184 | 64.4258
7.4 | 5.1348 | 1 | 2.856 | 184 | 64.4258
7.3 | 5.1241 | 1 | 2.856 | 184 | 64.4258
7.2 | 5.2813 | 1 | 2.856 | 184 | 64.4258
6.6 | 5.8685 | 1 | 2.856 | 184 | 64.4258
7.1 | 6.0278 | 1 | 2.856 | 184 | 64.4258
6.9 | 6.1143 | 1 | 2.856 | 184 | 64.4258
6.7 | 6.1087 | 1 | 2.856 | 184 | 64.4258
6.7 | 6.3022 | 1 | 2.856 | 184 | 64.4258
6.8 | 6.3519 | 1 | 2.856 | 184 | 64.4258
6.8 | 6.4008 | 1 | 2.856 | 184 | 64.4258
7 | 6.5489 | 1 | 2.856 | 184 | 64.4258
7.5 | 6.7957 | 1 | 2.856 | 184 | 64.4258
7.8 | 7.0895 | 1 | 2.856 | 184 | 64.4258
8 | 7.3346 | 1 | 2.856 | 184 | 64.4258
7.9 | 7.2862 | 1 | 2.856 | 184 | 64.4258
8 | 7.4847 | 1 | 2.856 | 184 | 64.4258
9.1 | 8.2097 | 1 | 2.856 | 184 | 64.4258
9.9 | 8.8869 | 1 | 2.856 | 184 | 64.4258
10.9 | 9.7029 | 1 | 2.856 | 184 | 64.4258
12.2 | 10.8008 | 1 | 2.856 | 184 | 64.4258
12.6 | 10.7635 | 1 | 2.856 | 184 | 64.4258
12.8 | 10.8491 | 1 | 2.856 | 184 | 64.4258
12.7 | 10.9628 | 1 | 2.856 | 184 | 64.4258
12.8 | 11.2171 | 1 | 2.856 | 184 | 64.4258
12.6 | 11.1855 | 1 | 2.856 | 184 | 64.4258
12.2 | 11.1231 | 1 | 2.856 | 184 | 64.4258
12.1 | 11.0258 | 1 | 2.856 | 184 | 64.4258
11.8 | 10.8419 | 1 | 2.856 | 184 | 64.4258
11.5 | 10.6034 | 1 | 2.856 | 184 | 64.4258
10.9 | 10.0171 | 1 | 2.856 | 184 | 64.4258
10.5 | 9.5733 | 1 | 2.856 | 184 | 64.4258
8.9 | 8.4224 | 1 | 2.856 | 184 | 64.4258
8.5 | 8.3404 | 1 | 2.856 | 184 | 64.4258
8.6 | 8.3344 | 1 | 2.856 | 184 | 64.4258
7.7 | 7.4924 | 1 | 2.856 | 184 | 64.4258
7.8 | 7.5402 | 1 | 2.856 | 184 | 64.4258
8 | 7.687 | 1 | 2.856 | 184 | 64.4258
8.4 | 7.8766 | 1 | 2.856 | 184 | 64.4258
9.1 | 8.2568 | 1 | 2.856 | 184 | 64.4258
9.2 | 8.4566 | 1 | 2.856 | 184 | 64.4258
9.4 | 8.7045 | 1 | 2.856 | 184 | 64.4258
10.2 | 9.3833 | 1 | 2.856 | 184 | 64.4258
10.6 | 9.721 | 1 | 2.856 | 184 | 64.4258
10.4 | 10.0102 | 1 | 2.856 | 184 | 64.4258
10.4 | 10.0651 | 1 | 2.856 | 184 | 64.4258
10.7 | 10.1967 | 1 | 2.856 | 184 | 64.4258
10.9 | 10.4495 | 1 | 2.856 | 184 | 64.4258
11.3 | 10.789 | 1 | 2.856 | 184 | 64.4258
10.8 | 10.4616 | 1 | 2.856 | 184 | 64.4258
10.5 | 10.1643 | 1 | 2.856 | 184 | 64.4258
10.6 | 10.1533 | 1 | 2.856 | 184 | 64.4258
10.5 | 9.9998 | 1 | 2.856 | 184 | 64.4258
10.5 | 9.9456 | 1 | 2.856 | 184 | 64.4258
9.5 | 9.0665 | 1 | 2.856 | 184 | 64.4258
8.5 | 7.7215 | 1 | 2.856 | 184 | 64.4258
7.6 | 6.4583 | 1 | 2.856 | 184 | 64.4258
7.3 | 6.0758 | 1 | 2.856 | 184 | 64.4258
7.1 | 5.7472 | 1 | 2.856 | 184 | 64.4258
6.7 | 5.728 | 1 | 2.856 | 184 | 64.4258
6.4 | 5.3002 | 1 | 2.856 | 184 | 64.4258
6.4 | 5.0333 | 1 | 2.856 | 184 | 64.4258
6.1 | 4.6605 | 1 | 2.856 | 184 | 64.4258
5.7 | 4.3645 | 1 | 2.856 | 184 | 64.4258
5.7 | 4.2376 | 1 | 2.856 | 184 | 64.4258
5.6 | 4.018 | 1 | 2.856 | 184 | 64.4258
5.7 | 4.1971 | 1 | 2.856 | 184 | 64.4258
5.9 | 4.1375 | 1 | 2.856 | 184 | 64.4258
7 | 4.6775 | 1 | 2.856 | 184 | 64.4258
6.9 | 4.3879 | 1 | 2.856 | 184 | 64.4258
6.8 | 4.1441 | 1 | 2.856 | 184 | 64.4258
6.4 | 3.6324 | 1 | 2.856 | 184 | 64.4258
6.2 | 3.7864 | 1 | 2.856 | 184 | 64.4258
6.1 | 3.5087 | 1 | 2.856 | 184 | 64.4258
5.4 | 3.2791 | 1 | 2.856 | 184 | 64.4258
5 | 3.0228 | 1 | 2.856 | 184 | 64.4258
4.5 | 2.7466 | 1 | 2.856 | 184 | 64.4258
4 | 2.3921 | 1 | 2.856 | 184 | 64.4258
3.8 | 2.1174 | 1 | 2.856 | 184 | 64.4258
3.3 | 1.7489 | 1 | 2.856 | 184 | 64.4258
2.5 | 1.0798 | 1 | 2.856 | 184 | 64.4258
2.2 | 0.78138 | 1 | 2.856 | 184 | 64.4258
1.8 | 0.50553 | 1 | 2.856 | 184 | 64.4258
1.6 | 0.22633 | 1 | 2.856 | 184 | 64.4258
1.4 | 0.066627 | 1 | 2.856 | 184 | 64.4258
1 | -0.20062 | 1 | 2.856 | 184 | 64.4258
0.7 | -0.37231 | 1 | 2.856 | 184 | 64.4258
0.6 | -0.46769 | 1 | 2.856 | 184 | 64.4258
1.4 | 0.18866 | 1 | 2.856 | 184 | 64.4258
2.6 | 1.1395 | 1 | 2.856 | 184 | 64.4258
4.9 | 2.8961 | 1 | 2.856 | 184 | 64.4258
6.5 | 3.8444 | 1 | 2.856 | 184 | 64.4258
7.7 | 4.5952 | 1 | 2.856 | 184 | 64.4258
8.3 | 4.9855 | 1 | 2.856 | 184 | 64.4258
7.8 | 5.147 | 1 | 2.856 | 184 | 64.4258
7.8 | 5.4291 | 1 | 2.856 | 184 | 64.4258
7.1 | 5.4053 | 1 | 2.856 | 184 | 64.4258
6.3 | 4.7335 | 1 | 2.856 | 184 | 64.4258
6.1 | 4.7574 | 1 | 2.856 | 184 | 64.4258
5.2 | 4.3698 | 1 | 2.856 | 184 | 64.4258
4.7 | 4.0145 | 1 | 2.856 | 184 | 64.4258
3.9 | 3.3623 | 1 | 2.856 | 184 | 64.4258
3.5 | 3.056 | 1 | 2.856 | 184 | 64.4258
3 | 2.5212 | 1 | 2.856 | 184 | 64.4258
2.5 | 2.1132 | 1 | 2.856 | 184 | 64.4258
2.1 | 1.6364 | 1 | 2.856 | 184 | 64.4258
1.8 | 1.2608 | 1 | 2.856 | 184 | 64.4258
1.6 | 1.1851 | 1 | 2.856 | 184 | 64.4258
1.2 | 0.83108 | 1 | 2.856 | 184 | 64.4258
1 | 0.63383 | 1 | 2.856 | 184 | 64.4258
1.2 | 0.79116 | 1 | 2.856 | 184 | 64.4258
1 | 0.59392 | 1 | 2.856 | 184 | 64.4258
1.2 | 0.57914 | 1 | 2.856 | 184 | 64.4258
1.2 | 0.712 | 1 | 2.856 | 184 | 64.4258
3.3 | 2.3598 | 1 | 2.856 | 184 | 64.4258
5.3 | 3.8705 | 1 | 2.856 | 184 | 64.4258
7 | 5.0199 | 1 | 2.856 | 184 | 64.4258
7.7 | 5.2212 | 1 | 2.856 | 184 | 64.4258
8.9 | 5.7194 | 1 | 2.856 | 184 | 64.4258
9 | 5.9271 | 1 | 2.856 | 184 | 64.4258
7.3 | 5.2154 | 1 | 2.856 | 184 | 64.4258
6.6 | 4.6855 | 1 | 2.856 | 184 | 64.4258
6.6 | 4.3243 | 1 | 2.856 | 184 | 64.4258
6.5 | 4.4297 | 1 | 2.856 | 184 | 64.4258
6.1 | 4.2572 | 1 | 2.856 | 184 | 64.4258
5.7 | 4.208 | 1 | 2.856 | 184 | 64.4258
5.8 | 4.5153 | 1 | 2.856 | 184 | 64.4258
5.9 | 4.9612 | 1 | 2.856 | 184 | 64.4258
6.6 | 5.595 | 1 | 2.856 | 184 | 64.4258
7 | 6.1217 | 1 | 2.856 | 184 | 64.4258
7.7 | 6.8029 | 1 | 2.856 | 184 | 64.4258
7.8 | 6.9966 | 1 | 2.856 | 184 | 64.4258
7.8 | 7.0448 | 1 | 2.856 | 184 | 64.4258
8 | 7.2403 | 1 | 2.856 | 184 | 64.4258
8.2 | 7.4358 | 1 | 2.856 | 184 | 64.4258
8.4 | 7.6317 | 1 | 2.856 | 184 | 64.4258
8.6 | 7.8273 | 1 | 2.856 | 184 | 64.4258
8.9 | 8.0209 | 1 | 2.856 | 184 | 64.4258
9.3 | 8.4109 | 1 | 2.856 | 184 | 64.4258
9.7 | 8.6489 | 1 | 2.856 | 184 | 64.4258
10.4 | 9.0745 | 1 | 2.856 | 184 | 64.4258
10.9 | 9.5049 | 1 | 2.856 | 184 | 64.4258
11.2 | 9.4903 | 1 | 2.856 | 184 | 64.4258
11.3 | 9.1923 | 1 | 2.856 | 184 | 64.4258
10.9 | 8.9114 | 1 | 2.856 | 184 | 64.4258
10.6 | 8.7238 | 1 | 2.856 | 184 | 64.4258
10.6 | 8.5329 | 1 | 2.856 | 184 | 64.4258
10.4 | 8.4865 | 1 | 2.856 | 184 | 64.4258
10.5 | 8.0673 | 1 | 2.856 | 184 | 64.4258
10.4 | 7.9743 | 1 | 2.856 | 184 | 64.4258
10.3 | 8.0177 | 1 | 2.856 | 184 | 64.4258
10.3 | 8.0177 | 1 | 2.856 | 184 | 64.4258
10.1 | 8.1538 | 1 | 2.856 | 184 | 64.4258
10.1 | 8.2009 | 1 | 2.856 | 184 | 64.4258
10.1 | 8.2009 | 1 | 2.856 | 184 | 64.4258
9.9 | 8.1053 | 1 | 2.856 | 184 | 64.4258
9.7 | 8.1532 | 1 | 2.856 | 184 | 64.4258
9.5 | 8.2044 | 1 | 2.856 | 184 | 64.4258
8.8 | 8.2753 | 1 | 2.856 | 184 | 64.4258
8.6 | 8.1808 | 1 | 2.856 | 184 | 64.4258
8.5 | 8.1335 | 1 | 2.856 | 184 | 64.4258
8.8 | 8.2751 | 1 | 2.856 | 184 | 64.4258
8.8 | 8.4823 | 1 | 2.856 | 184 | 64.4258
9.1 | 8.5706 | 1 | 2.856 | 184 | 64.4258
9.5 | 8.7052 | 1 | 2.856 | 184 | 64.4258
9.8 | 8.9982 | 1 | 2.856 | 184 | 64.4258
9.9 | 8.8897 | 1 | 2.856 | 184 | 64.4258
10 | 8.8343 | 1 | 2.856 | 184 | 64.4258
9.6 | 8.4472 | 1 | 2.856 | 184 | 64.4258
9.6 | 8.4467 | 1 | 2.856 | 184 | 64.4258
9.2 | 8.4107 | 1 | 2.856 | 184 | 64.4258
9.2 | 8.4107 | 1 | 2.856 | 184 | 64.4258
9 | 8.2659 | 1 | 2.856 | 184 | 64.4258
9.1 | 8.1611 | 1 | 2.856 | 184 | 64.4258
8.9 | 7.9664 | 1 | 2.856 | 184 | 64.4258
8.7 | 7.7219 | 1 | 2.856 | 184 | 64.4258
8.5 | 7.5275 | 1 | 2.856 | 184 | 64.4258
8.4 | 7.3324 | 1 | 2.856 | 184 | 64.4258
8.2 | 7.2842 | 1 | 2.856 | 184 | 64.4258
8.1 | 7.1379 | 1 | 2.856 | 184 | 64.4258
7.7 | 7.1895 | 1 | 2.856 | 184 | 64.4258
7.5 | 7.1926 | 1 | 2.856 | 184 | 64.4258
7.5 | 6.9427 | 1 | 2.856 | 184 | 64.4258
7.6 | 7.041 | 1 | 2.856 | 184 | 64.4258
7.6 | 6.8445 | 1 | 2.856 | 184 | 64.4258
7.8 | 6.9912 | 1 | 2.856 | 184 | 64.4258
8.2 | 7.0895 | 1 | 2.856 | 184 | 64.4258
8.6 | 7.3797 | 1 | 2.856 | 184 | 64.4258
9.1 | 7.6674 | 1 | 2.856 | 184 | 64.4258
9.3 | 7.5261 | 1 | 2.856 | 184 | 64.4258
9 | 7.4754 | 1 | 2.856 | 184 | 64.4258
8.7 | 7.4267 | 1 | 2.856 | 184 | 64.4258
8.4 | 7.2819 | 1 | 2.856 | 184 | 64.4258
8.4 | 7.1378 | 1 | 2.856 | 184 | 64.4258
8.3 | 7.3308 | 1 | 2.856 | 184 | 64.4258
8.3 | 7.429 | 1 | 2.856 | 184 | 64.4258
8.2 | 7.4304 | 1 | 2.856 | 184 | 64.4258
8.2 | 7.5301 | 1 | 2.856 | 184 | 64.4258
8.1 | 7.2341 | 1 | 2.856 | 184 | 64.4258
7.9 | 7.1864 | 1 | 2.856 | 184 | 64.4258
7.6 | 6.9417 | 1 | 2.856 | 184 | 64.4258
7.4 | 6.7946 | 1 | 2.856 | 184 | 64.4258
7.2 | 6.7952 | 1 | 2.856 | 184 | 64.4258
7.1 | 6.5 | 1 | 2.856 | 184 | 64.4258
6.8 | 6.351 | 1 | 2.856 | 184 | 64.4258
6.8 | 6.3025 | 1 | 2.856 | 184 | 64.4258
6.8 | 6.1576 | 1 | 2.856 | 184 | 64.4258
6.9 | 6.1124 | 1 | 2.856 | 184 | 64.4258
6.9 | 6.1127 | 1 | 2.856 | 184 | 64.4258
7.6 | 6.3688 | 1 | 2.856 | 184 | 64.4258
7.5 | 6.1346 | 1 | 2.856 | 184 | 64.4258
8.4 | 6.2728 | 1 | 2.856 | 184 | 64.4258
8.8 | 6.1324 | 1 | 2.856 | 184 | 64.4258
9.1 | 6.2016 | 1 | 2.856 | 184 | 64.4258
9.2 | 6.2516 | 1 | 2.856 | 184 | 64.4258
9 | 6.3173 | 1 | 2.856 | 184 | 64.4258
8.8 | 6.051 | 1 | 2.856 | 184 | 64.4258
8.4 | 6.1026 | 1 | 2.856 | 184 | 64.4258
8.3 | 5.925 | 1 | 2.856 | 184 | 64.4258
7.9 | 5.7234 | 1 | 2.856 | 184 | 64.4258
7.9 | 5.5557 | 1 | 2.856 | 184 | 64.4258
7.2 | 5.5821 | 1 | 2.856 | 184 | 64.4258
7.2 | 5.6261 | 1 | 2.856 | 184 | 64.4258
6.9 | 5.2982 | 1 | 2.856 | 184 | 64.4258
5.9 | 5.0927 | 1 | 2.856 | 184 | 64.4258
5.9 | 4.9121 | 1 | 2.856 | 184 | 64.4258
5.1 | 4.3133 | 1 | 2.856 | 184 | 64.4258
3.8 | 3.1752 | 1 | 2.856 | 184 | 64.4258
4.2 | 3.6545 | 1 | 2.856 | 184 | 64.4258
4.6 | 4.0472 | 1 | 2.856 | 184 | 64.4258
5.3 | 4.2012 | 1 | 2.856 | 184 | 64.4258
6.3 | 4.4373 | 1 | 2.856 | 184 | 64.4258
5.8 | 4.3389 | 1 | 2.856 | 184 | 64.4258
5.8 | 4.5958 | 1 | 2.856 | 184 | 64.4258
7.1 | 5.5766 | 1 | 2.856 | 184 | 64.4258
8 | 6.3432 | 1 | 2.856 | 184 | 64.4258
9.9 | 7.8188 | 1 | 2.856 | 184 | 64.4258
9.6 | 7.5818 | 1 | 2.856 | 184 | 64.4258
9.6 | 7.3993 | 1 | 2.856 | 184 | 64.4258
9.7 | 7.4026 | 1 | 2.856 | 184 | 64.4258
9.6 | 7.2646 | 1 | 2.856 | 184 | 64.4258
8.7 | 6.9621 | 1 | 2.856 | 184 | 64.4258
8.7 | 7.0541 | 1 | 2.856 | 184 | 64.4258
8.7 | 7.1938 | 1 | 2.856 | 184 | 64.4258
8.8 | 7.2893 | 1 | 2.856 | 184 | 64.4258
8.9 | 7.291 | 1 | 2.856 | 184 | 64.4258
8.9 | 7.3849 | 1 | 2.856 | 184 | 64.4258
9 | 7.4805 | 1 | 2.856 | 184 | 64.4258
8.7 | 7.2873 | 1 | 2.856 | 184 | 64.4258
8.5 | 7.1428 | 1 | 2.856 | 184 | 64.4258
8 | 7.0421 | 1 | 2.856 | 184 | 64.4258
8.2 | 7.2851 | 1 | 2.856 | 184 | 64.4258
8.1 | 7.1874 | 1 | 2.856 | 184 | 64.4258
8 | 7.1387 | 1 | 2.856 | 184 | 64.4258
8.9 | 7.4784 | 1 | 2.856 | 184 | 64.4258
9.3 | 7.7658 | 1 | 2.856 | 184 | 64.4258
9.9 | 8.3394 | 1 | 2.856 | 184 | 64.4258
10.4 | 8.6215 | 1 | 2.856 | 184 | 64.4258
10.9 | 8.9978 | 1 | 2.856 | 184 | 64.4258
11.4 | 9.3731 | 1 | 2.856 | 184 | 64.4258
11.8 | 9.6512 | 1 | 2.856 | 184 | 64.4258
11.8 | 9.7503 | 1 | 2.856 | 184 | 64.4258
12 | 9.9887 | 1 | 2.856 | 184 | 64.4258
12 | 10.0383 | 1 | 2.856 | 184 | 64.4258
12 | 10.1908 | 1 | 2.856 | 184 | 64.4258
12 | 10.2937 | 1 | 2.856 | 184 | 64.4258
11.9 | 10.0446 | 1 | 2.856 | 184 | 64.4258
11.8 | 9.9995 | 1 | 2.856 | 184 | 64.4258
11.7 | 9.8536 | 1 | 2.856 | 184 | 64.4258
11.5 | 9.7635 | 1 | 2.856 | 184 | 64.4258
11.6 | 9.8082 | 1 | 2.856 | 184 | 64.4258
11.7 | 9.9536 | 1 | 2.856 | 184 | 64.4258
11.4 | 10.027 | 1 | 2.856 | 184 | 64.4258
11.6 | 10.2724 | 1 | 2.856 | 184 | 64.4258
11.8 | 10.4649 | 1 | 2.856 | 184 | 64.4258
11.6 | 10.7549 | 1 | 2.856 | 184 | 64.4258
11.9 | 10.7213 | 1 | 2.856 | 184 | 64.4258
12.6 | 10.7067 | 1 | 2.856 | 184 | 64.4258
11.5 | 10.6566 | 1 | 2.856 | 184 | 64.4258
11.5 | 10.6022 | 1 | 2.856 | 184 | 64.4258
9.8 | 8.7874 | 1 | 2.856 | 184 | 64.4258
9.4 | 8.1484 | 1 | 2.856 | 184 | 64.4258
9.8 | 7.5314 | 1 | 2.856 | 184 | 64.4258
10.5 | 7.1733 | 1 | 2.856 | 184 | 64.4258
11 | 7.2899 | 1 | 2.856 | 184 | 64.4258
10.8 | 7.1932 | 1 | 2.856 | 184 | 64.4258
10.8 | 7.2754 | 1 | 2.856 | 184 | 64.4258
10 | 6.3232 | 1 | 2.856 | 184 | 64.4258
9.1 | 6.0332 | 1 | 2.856 | 184 | 64.4258
8.7 | 5.4768 | 1 | 2.856 | 184 | 64.4258
8.3 | 4.2099 | 1 | 2.856 | 184 | 64.4258
7 | 3.5921 | 1 | 2.856 | 184 | 64.4258
5.5 | 3.058 | 1 | 2.856 | 184 | 64.4258
4.8 | 2.3058 | 1 | 2.856 | 184 | 64.4258
4.2 | 1.8489 | 1 | 2.856 | 184 | 64.4258
3.4 | 1.7181 | 1 | 2.856 | 184 | 64.4258
2.7 | 1.4023 | 1 | 2.856 | 184 | 64.4258
2.3 | 0.79487 | 1 | 2.856 | 184 | 64.4258
1.9 | 0.20373 | 1 | 2.856 | 184 | 64.4258
1.4 | -0.12554 | 1 | 2.856 | 184 | 64.4258
0.7 | -0.63618 | 1 | 2.856 | 184 | 64.4258
0.7 | -0.37532 | 1 | 2.856 | 184 | 64.4258
0.6 | -0.23871 | 1 | 2.856 | 184 | 64.4258
0.4 | -0.88271 | 1 | 2.856 | 184 | 64.4258
0.8 | -0.46761 | 1 | 2.856 | 184 | 64.4258
1.4 | 0.064293 | 1 | 2.856 | 184 | 64.4258
2.7 | 0.7533 | 1 | 2.856 | 184 | 64.4258
3.7 | 1.808 | 1 | 2.856 | 184 | 64.4258
5.4 | 2.8415 | 1 | 2.856 | 184 | 64.4258
5.8 | 3.0218 | 1 | 2.856 | 184 | 64.4258
6 | 3.2917 | 1 | 2.856 | 184 | 64.4258
6 | 3.4531 | 1 | 2.856 | 184 | 64.4258
6 | 3.6406 | 1 | 2.856 | 184 | 64.4258
5.8 | 4.0035 | 1 | 2.856 | 184 | 64.4258
5.9 | 4.3879 | 1 | 2.856 | 184 | 64.4258
6 | 4.6975 | 1 | 2.856 | 184 | 64.4258
6.1 | 5.014 | 1 | 2.856 | 184 | 64.4258
6.5 | 5.2646 | 1 | 2.856 | 184 | 64.4258
6.7 | 5.6383 | 1 | 2.856 | 184 | 64.4258
7.1 | 6.355 | 1 | 2.856 | 184 | 64.4258
7.6 | 7.1904 | 1 | 2.856 | 184 | 64.4258
7.8 | 7.3375 | 1 | 2.856 | 184 | 64.4258
7.3 | 6.9941 | 1 | 2.856 | 184 | 64.4258
7.1 | 6.7959 | 1 | 2.856 | 184 | 64.4258
7.1 | 6.8459 | 1 | 2.856 | 184 | 64.4258
6.3 | 6.1011 | 1 | 2.856 | 184 | 64.4258
6.6 | 6.3993 | 1 | 2.856 | 184 | 64.4258
8.2 | 7.5297 | 1 | 2.856 | 184 | 64.4258
8.3 | 7.8306 | 1 | 2.856 | 184 | 64.4258
9.2 | 8.5622 | 1 | 2.856 | 184 | 64.4258
10.2 | 9.2295 | 1 | 2.856 | 184 | 64.4258
11.2 | 9.9913 | 1 | 2.856 | 184 | 64.4258
12.5 | 10.4087 | 1 | 2.856 | 184 | 64.4258
13 | 10.2784 | 1 | 2.856 | 184 | 64.4258
13.9 | 10.9639 | 1 | 2.856 | 184 | 64.4258
13.3 | 10.6056 | 1 | 2.856 | 184 | 64.4258
12.8 | 10.5387 | 1 | 2.856 | 184 | 64.4258
12.3 | 10.3203 | 1 | 2.856 | 184 | 64.4258
12.2 | 10.4826 | 1 | 2.856 | 184 | 64.4258
12.1 | 10.5435 | 1 | 2.856 | 184 | 64.4258
12 | 10.712 | 1 | 2.856 | 184 | 64.4258
12.4 | 10.9379 | 1 | 2.856 | 184 | 64.4258
12.3 | 11.1104 | 1 | 2.856 | 184 | 64.4258
11.4 | 10.614 | 1 | 2.856 | 184 | 64.4258
10.2 | 9.7591 | 1 | 2.856 | 184 | 64.4258
10.7 | 10.1439 | 1 | 2.856 | 184 | 64.4258
11 | 10.2755 | 1 | 2.856 | 184 | 64.4258
11.4 | 10.4504 | 1 | 2.856 | 184 | 64.4258
11 | 10.1133 | 1 | 2.856 | 184 | 64.4258
10.9 | 10.0156 | 1 | 2.856 | 184 | 64.4258
10.4 | 9.7397 | 1 | 2.856 | 184 | 64.4258
10.3 | 9.6414 | 1 | 2.856 | 184 | 64.4258
10.5 | 9.6775 | 1 | 2.856 | 184 | 64.4258
11.3 | 10.4056 | 1 | 2.856 | 184 | 64.4258
11.8 | 11.2272 | 1 | 2.856 | 184 | 64.4258
12.6 | 11.7318 | 1 | 2.856 | 184 | 64.4258
13.1 | 12.0511 | 1 | 2.856 | 184 | 64.4258
13.7 | 12.4089 | 1 | 2.856 | 184 | 64.4258
14 | 12.6998 | 1 | 2.856 | 184 | 64.4258
14.1 | 12.6266 | 1 | 2.856 | 184 | 64.4258
13.4 | 12.514 | 1 | 2.856 | 184 | 64.4258
8 | 7.0351 | 1 | 2.856 | 184 | 64.4258
7.6 | 6.7916 | 1 | 2.856 | 184 | 64.4258
7.4 | 6.5005 | 1 | 2.856 | 184 | 64.4258
7 | 6.2064 | 1 | 2.856 | 184 | 64.4258
7.2 | 6.3536 | 1 | 2.856 | 184 | 64.4258
7 | 6.2547 | 1 | 2.856 | 184 | 64.4258
6.9 | 6.2049 | 1 | 2.856 | 184 | 64.4258
6.6 | 5.9112 | 1 | 2.856 | 184 | 64.4258
5.6 | 5.1658 | 1 | 2.856 | 184 | 64.4258
4.2 | 4.0132 | 1 | 2.856 | 184 | 64.4258
3.3 | 3.2089 | 1 | 2.856 | 184 | 64.4258
2.8 | 2.6218 | 1 | 2.856 | 184 | 64.4258
2.4 | 2.0523 | 1 | 2.856 | 184 | 64.4258
3 | 2.5584 | 1 | 2.856 | 184 | 64.4258
2.5 | 2.0661 | 1 | 2.856 | 184 | 64.4258
2.3 | 1.9112 | 1 | 2.856 | 184 | 64.4258
2.9 | 2.3322 | 1 | 2.856 | 184 | 64.4258
4.4 | 3.4106 | 1 | 2.856 | 184 | 64.4258
5.5 | 4.2556 | 1 | 2.856 | 184 | 64.4258
7.1 | 5.6543 | 1 | 2.856 | 184 | 64.4258
7.9 | 6.2813 | 1 | 2.856 | 184 | 64.4258
8 | 6.1504 | 1 | 2.856 | 184 | 64.4258
8.3 | 6.1242 | 1 | 2.856 | 184 | 64.4258
7.2 | 5.4827 | 1 | 2.856 | 184 | 64.4258
6.2 | 4.9258 | 1 | 2.856 | 184 | 64.4258
5.7 | 4.5775 | 1 | 2.856 | 184 | 64.4258
4.8 | 4.0149 | 1 | 2.856 | 184 | 64.4258
3.9 | 3.3117 | 1 | 2.856 | 184 | 64.4258
4 | 3.3222 | 1 | 2.856 | 184 | 64.4258
3.1 | 2.6997 | 1 | 2.856 | 184 | 64.4258
2.1 | 1.7977 | 1 | 2.856 | 184 | 64.4258
1.8 | 1.5009 | 1 | 2.856 | 184 | 64.4258
1.2 | 1.0314 | 1 | 2.856 | 184 | 64.4258
1.3 | 1.0475 | 1 | 2.856 | 184 | 64.4258
0.8 | 0.63376 | 1 | 2.856 | 184 | 64.4258
0.7 | 0.36614 | 1 | 2.856 | 184 | 64.4258
2.2 | 1.562 | 1 | 2.856 | 184 | 64.4258
2.3 | 1.7422 | 1 | 2.856 | 184 | 64.4258
3 | 2.3433 | 1 | 2.856 | 184 | 64.4258
3.8 | 3.1246 | 1 | 2.856 | 184 | 64.4258
4.9 | 4.0211 | 1 | 2.856 | 184 | 64.4258
6.4 | 5.2935 | 1 | 2.856 | 184 | 64.4258
7.3 | 6.1618 | 1 | 2.856 | 184 | 64.4258
8.6 | 6.8452 | 1 | 2.856 | 184 | 64.4258
9.9 | 7.7931 | 1 | 2.856 | 184 | 64.4258
10.5 | 8.2139 | 1 | 2.856 | 184 | 64.4258
10.6 | 8.6917 | 1 | 2.856 | 184 | 64.4258
10.2 | 8.9098 | 1 | 2.856 | 184 | 64.4258
9.3 | 8.499 | 1 | 2.856 | 184 | 64.4258
9.3 | 8.2437 | 1 | 2.856 | 184 | 64.4258
8.8 | 6.3199 | 1 | 2.856 | 184 | 64.4258
6.4 | 5.4311 | 1 | 2.856 | 184 | 64.4258
6 | 5.1353 | 1 | 2.856 | 184 | 64.4258
5.1 | 4.4403 | 1 | 2.856 | 184 | 64.4258
6.1 | 4.8708 | 1 | 2.856 | 184 | 64.4258
6 | 4.7754 | 1 | 2.856 | 184 | 64.4258
5.8 | 4.6273 | 1 | 2.856 | 184 | 64.4258
5 | 3.9444 | 1 | 2.856 | 184 | 64.4258
4.2 | 3.2998 | 1 | 2.856 | 184 | 64.4258
4.6 | 3.4739 | 1 | 2.856 | 184 | 64.4258
3.8 | 2.9547 | 1 | 2.856 | 184 | 64.4258
3.5 | 2.7059 | 1 | 2.856 | 184 | 64.4258
3.5 | 2.7063 | 1 | 2.856 | 184 | 64.4258
3 | 2.4299 | 1 | 2.856 | 184 | 64.4258
4.2 | 3.3022 | 1 | 2.856 | 184 | 64.4258
5.8 | 4.5433 | 1 | 2.856 | 184 | 64.4258
7.1 | 5.4344 | 1 | 2.856 | 184 | 64.4258
8.3 | 6.2146 | 1 | 2.856 | 184 | 64.4258
8.7 | 6.4133 | 1 | 2.856 | 184 | 64.4258
9 | 6.5628 | 1 | 2.856 | 184 | 64.4258
9 | 6.6499 | 1 | 2.856 | 184 | 64.4258
8.6 | 6.5854 | 1 | 2.856 | 184 | 64.4258
8.6 | 6.8113 | 1 | 2.856 | 184 | 64.4258
8.4 | 6.8518 | 1 | 2.856 | 184 | 64.4258
8.9 | 7.1881 | 1 | 2.856 | 184 | 64.4258
8.8 | 7.0931 | 1 | 2.856 | 184 | 64.4258
8.4 | 6.9923 | 1 | 2.856 | 184 | 64.4258
8.5 | 7.2305 | 1 | 2.856 | 184 | 64.4258
9 | 7.9087 | 1 | 2.856 | 184 | 64.4258
9.8 | 8.7344 | 1 | 2.856 | 184 | 64.4258
10.8 | 9.6008 | 1 | 2.856 | 184 | 64.4258
11.3 | 10.0317 | 1 | 2.856 | 184 | 64.4258
11 | 10.4381 | 1 | 2.856 | 184 | 64.4258
11 | 10.3832 | 1 | 2.856 | 184 | 64.4258
11.1 | 10.5364 | 1 | 2.856 | 184 | 64.4258
11.2 | 10.6903 | 1 | 2.856 | 184 | 64.4258
11.7 | 10.7945 | 1 | 2.856 | 184 | 64.4258
11.9 | 10.99 | 1 | 2.856 | 184 | 64.4258
11.9 | 11.1003 | 1 | 2.856 | 184 | 64.4258
12.3 | 11.5486 | 1 | 2.856 | 184 | 64.4258
12.6 | 11.9 | 1 | 2.856 | 184 | 64.4258
13 | 12.1783 | 1 | 2.856 | 184 | 64.4258
13.4 | 12.4556 | 1 | 2.856 | 184 | 64.4258
13.7 | 12.6336 | 1 | 2.856 | 184 | 64.4258
13.8 | 12.7311 | 1 | 2.856 | 184 | 64.4258
13.7 | 12.7486 | 1 | 2.856 | 184 | 64.4258
13.6 | 12.6508 | 1 | 2.856 | 184 | 64.4258
13.7 | 12.6336 | 1 | 2.856 | 184 | 64.4258
13.7 | 12.691 | 1 | 2.856 | 184 | 64.4258
13.3 | 12.5878 | 1 | 2.856 | 184 | 64.4258
13.1 | 12.5654 | 1 | 2.856 | 184 | 64.4258
13.2 | 12.6057 | 1 | 2.856 | 184 | 64.4258
13.1 | 12.6239 | 1 | 2.856 | 184 | 64.4258
13.1 | 12.5654 | 1 | 2.856 | 184 | 64.4258
13.2 | 12.7228 | 1 | 2.856 | 184 | 64.4258
13.3 | 12.7629 | 1 | 2.856 | 184 | 64.4258
13.2 | 12.7817 | 1 | 2.856 | 184 | 64.4258
13.1 | 12.7414 | 1 | 2.856 | 184 | 64.4258
13.2 | 12.7815 | 1 | 2.856 | 184 | 64.4258
13.2 | 12.7226 | 1 | 2.856 | 184 | 64.4258
13.5 | 12.8426 | 1 | 2.856 | 184 | 64.4258
13.5 | 12.726 | 1 | 2.856 | 184 | 64.4258
13.7 | 12.6906 | 1 | 2.856 | 184 | 64.4258
13.9 | 12.8282 | 1 | 2.856 | 184 | 64.4258
14.1 | 12.9655 | 1 | 2.856 | 184 | 64.4258
14.4 | 13.0846 | 1 | 2.856 | 184 | 64.4258
14.6 | 13.1636 | 1 | 2.856 | 184 | 64.4258
14.7 | 13.3179 | 1 | 2.856 | 184 | 64.4258
14.6 | 13.2786 | 1 | 2.856 | 184 | 64.4258
14.5 | 13.2392 | 1 | 2.856 | 184 | 64.4258
14.7 | 13.2604 | 1 | 2.856 | 184 | 64.4258
14.5 | 13.2397 | 1 | 2.856 | 184 | 64.4258
14.3 | 13.2184 | 1 | 2.856 | 184 | 64.4258
12.8 | 11.9251 | 1 | 2.856 | 184 | 64.4258
11.5 | 10.6526 | 1 | 2.856 | 184 | 64.4258
10 | 9.4511 | 1 | 2.856 | 184 | 64.4258
8.8 | 8.0625 | 1 | 2.856 | 184 | 64.4258
7.5 | 6.8388 | 1 | 2.856 | 184 | 64.4258
5.5 | 5.0654 | 1 | 2.856 | 184 | 64.4258
5.2 | 4.5382 | 1 | 2.856 | 184 | 64.4258
4.6 | 3.9063 | 1 | 2.856 | 184 | 64.4258
3.7 | 2.8982 | 1 | 2.856 | 184 | 64.4258
3.6 | 2.9292 | 1 | 2.856 | 184 | 64.4258
4.1 | 3.2013 | 1 | 2.856 | 184 | 64.4258
3 | 2.5564 | 1 | 2.856 | 184 | 64.4258
3.8 | 2.9105 | 1 | 2.856 | 184 | 64.4258
5.3 | 3.5982 | 1 | 2.856 | 184 | 64.4258
5.9 | 3.8783 | 1 | 2.856 | 184 | 64.4258
6.1 | 4.1869 | 1 | 2.856 | 184 | 64.4258
6.5 | 4.2358 | 1 | 2.856 | 184 | 64.4258
6.6 | 4.4495 | 1 | 2.856 | 184 | 64.4258
6.8 | 4.4332 | 1 | 2.856 | 184 | 64.4258
6.9 | 4.4061 | 1 | 2.856 | 184 | 64.4258
5.9 | 4.0813 | 1 | 2.856 | 184 | 64.4258
5.9 | 4.418 | 1 | 2.856 | 184 | 64.4258
5.9 | 4.5473 | 1 | 2.856 | 184 | 64.4258
5.3 | 4.1897 | 1 | 2.856 | 184 | 64.4258
4.5 | 3.5901 | 1 | 2.856 | 184 | 64.4258
4.2 | 3.2993 | 1 | 2.856 | 184 | 64.4258
3.5 | 2.8326 | 1 | 2.856 | 184 | 64.4258
3.1 | 2.5266 | 1 | 2.856 | 184 | 64.4258
2.5 | 2.0648 | 1 | 2.856 | 184 | 64.4258
2.1 | 1.6295 | 1 | 2.856 | 184 | 64.4258
1.8 | 1.4587 | 1 | 2.856 | 184 | 64.4258
2.1 | 1.755 | 1 | 2.856 | 184 | 64.4258
1.5 | 1.2875 | 1 | 2.856 | 184 | 64.4258
1.5 | 1.1624 | 1 | 2.856 | 184 | 64.4258
2.5 | 2.0648 | 1 | 2.856 | 184 | 64.4258
3.3 | 2.6375 | 1 | 2.856 | 184 | 64.4258
3.3 | 2.6375 | 1 | 2.856 | 184 | 64.4258
3.6 | 2.931 | 1 | 2.856 | 184 | 64.4258
4.3 | 3.5274 | 1 | 2.856 | 184 | 64.4258
5.5 | 4.3841 | 1 | 2.856 | 184 | 64.4258
5.8 | 4.6733 | 1 | 2.856 | 184 | 64.4258
6.3 | 5.1998 | 1 | 2.856 | 184 | 64.4258
6.5 | 5.1683 | 1 | 2.856 | 184 | 64.4258
6.7 | 5.4499 | 1 | 2.856 | 184 | 64.4258
6.1 | 5.1888 | 1 | 2.856 | 184 | 64.4258
6.2 | 5.195 | 1 | 2.856 | 184 | 64.4258
6.5 | 5.6244 | 1 | 2.856 | 184 | 64.4258
6.4 | 5.5275 | 1 | 2.856 | 184 | 64.4258
5.7 | 5.03 | 1 | 2.856 | 184 | 64.4258
5.2 | 4.5409 | 1 | 2.856 | 184 | 64.4258
4.5 | 3.9452 | 1 | 2.856 | 184 | 64.4258
4.6 | 4.0437 | 1 | 2.856 | 184 | 64.4258
3.3 | 3.0742 | 1 | 2.856 | 184 | 64.4258
2.8 | 2.6663 | 1 | 2.856 | 184 | 64.4258
2.9 | 2.7658 | 1 | 2.856 | 184 | 64.4258
2.8 | 2.6663 | 1 | 2.856 | 184 | 64.4258
2.5 | 2.5 | 1 | 2.856 | 184 | 64.4258
2.6 | 2.4672 | 1 | 2.856 | 184 | 64.4258
2.8 | 2.6664 | 1 | 2.856 | 184 | 64.4258
2.4 | 2.4 | 1 | 2.856 | 184 | 64.4258
2.5 | 2.5 | 1 | 2.856 | 184 | 64.4258
2.6 | 2.4674 | 1 | 2.856 | 184 | 64.4258
2.3 | 2.3 | 1 | 2.856 | 184 | 64.4258
2.5 | 2.5 | 1 | 2.856 | 184 | 64.4258
3.3 | 3.2093 | 1 | 2.856 | 184 | 64.4258
3.9 | 3.5799 | 1 | 2.856 | 184 | 64.4258
4.3 | 3.7509 | 1 | 2.856 | 184 | 64.4258
4.9 | 4.2497 | 1 | 2.856 | 184 | 64.4258
5.4 | 4.5136 | 1 | 2.856 | 184 | 64.4258
5.4 | 4.6031 | 1 | 2.856 | 184 | 64.4258
5.8 | 4.9025 | 1 | 2.856 | 184 | 64.4258
5.7 | 4.5833 | 1 | 2.856 | 184 | 64.4258
5.8 | 4.903 | 1 | 2.856 | 184 | 64.4258
5.6 | 4.7088 | 1 | 2.856 | 184 | 64.4258
5.4 | 4.6039 | 1 | 2.856 | 184 | 64.4258
5.6 | 4.7088 | 1 | 2.856 | 184 | 64.4258
4.7 | 4.2348 | 1 | 2.856 | 184 | 64.4258
5 | 4.6688 | 1 | 2.856 | 184 | 64.4258
5.2 | 4.7735 | 1 | 2.856 | 184 | 64.4258
5.3 | 4.8723 | 1 | 2.856 | 184 | 64.4258
5.4 | 5.0647 | 1 | 2.856 | 184 | 64.4258
5.6 | 5.1682 | 1 | 2.856 | 184 | 64.4258
4.9 | 4.6632 | 1 | 2.856 | 184 | 64.4258
5.2 | 4.9609 | 1 | 2.856 | 184 | 64.4258
5.2 | 4.961 | 1 | 2.856 | 184 | 64.4258
5.8 | 5.4606 | 1 | 2.856 | 184 | 64.4258
7.2 | 6.5514 | 1 | 2.856 | 184 | 64.4258
7.6 | 6.9436 | 1 | 2.856 | 184 | 64.4258
7.9 | 7.1393 | 1 | 2.856 | 184 | 64.4258
8.9 | 7.8179 | 1 | 2.856 | 184 | 64.4258
9.3 | 8.2055 | 1 | 2.856 | 184 | 64.4258
10 | 8.6825 | 1 | 2.856 | 184 | 64.4258
9.8 | 8.6901 | 1 | 2.856 | 184 | 64.4258
9.6 | 8.4963 | 1 | 2.856 | 184 | 64.4258
9.3 | 8.6625 | 1 | 2.856 | 184 | 64.4258
9.5 | 8.7556 | 1 | 2.856 | 184 | 64.4258
9.6 | 8.6989 | 1 | 2.856 | 184 | 64.4258
9.6 | 8.6989 | 1 | 2.856 | 184 | 64.4258
9.3 | 8.4064 | 1 | 2.856 | 184 | 64.4258
8.8 | 8.1204 | 1 | 2.856 | 184 | 64.4258
7.8 | 7.2391 | 1 | 2.856 | 184 | 64.4258
7.7 | 7.042 | 1 | 2.856 | 184 | 64.4258
8 | 7.1395 | 1 | 2.856 | 184 | 64.4258
7.5 | 6.6039 | 1 | 2.856 | 184 | 64.4258
6.6 | 6.155 | 1 | 2.856 | 184 | 64.4258
7.6 | 6.7012 | 1 | 2.856 | 184 | 64.4258
6.9 | 6.451 | 1 | 2.856 | 184 | 64.4258
8.1 | 7.2366 | 1 | 2.856 | 184 | 64.4258
8.1 | 7.3348 | 1 | 2.856 | 184 | 64.4258
8.6 | 7.8236 | 1 | 2.856 | 184 | 64.4258
8.9 | 8.0168 | 1 | 2.856 | 184 | 64.4258
9.7 | 8.7968 | 1 | 2.856 | 184 | 64.4258
9.9 | 9.0431 | 1 | 2.856 | 184 | 64.4258
10.3 | 9.5918 | 1 | 2.856 | 184 | 64.4258
10.5 | 9.7345 | 1 | 2.856 | 184 | 64.4258
10.5 | 9.8415 | 1 | 2.856 | 184 | 64.4258
10.6 | 9.7268 | 1 | 2.856 | 184 | 64.4258
10.6 | 9.7268 | 1 | 2.856 | 184 | 64.4258
10.3 | 9.5389 | 1 | 2.856 | 184 | 64.4258
10.2 | 9.4409 | 1 | 2.856 | 184 | 64.4258
10 | 9.3502 | 1 | 2.856 | 184 | 64.4258
10.1 | 9.4484 | 1 | 2.856 | 184 | 64.4258
10 | 9.245 | 1 | 2.856 | 184 | 64.4258
10.1 | 9.2384 | 1 | 2.856 | 184 | 64.4258
9.4 | 8.9702 | 1 | 2.856 | 184 | 64.4258
9.2 | 8.6679 | 1 | 2.856 | 184 | 64.4258
8.8 | 8.3771 | 1 | 2.856 | 184 | 64.4258
9 | 8.3162 | 1 | 2.856 | 184 | 64.4258
8.7 | 8.022 | 1 | 2.856 | 184 | 64.4258
9.2 | 8.41 | 1 | 2.856 | 184 | 64.4258
9.3 | 8.4056 | 1 | 2.856 | 184 | 64.4258
9.8 | 8.5884 | 1 | 2.856 | 184 | 64.4258
9.9 | 8.6856 | 1 | 2.856 | 184 | 64.4258
9.9 | 8.6856 | 1 | 2.856 | 184 | 64.4258
10.5 | 8.4292 | 1 | 2.856 | 184 | 64.4258
10.9 | 8.6149 | 1 | 2.856 | 184 | 64.4258
11.5 | 8.3035 | 1 | 2.856 | 184 | 64.4258
11.1 | 8.0256 | 1 | 2.856 | 184 | 64.4258
11 | 7.9344 | 1 | 2.856 | 184 | 64.4258
10.7 | 7.7042 | 1 | 2.856 | 184 | 64.4258
10.3 | 7.6444 | 1 | 2.856 | 184 | 64.4258
9.9 | 7.3633 | 1 | 2.856 | 184 | 64.4258
9.6 | 7.1736 | 1 | 2.856 | 184 | 64.4258
8.9 | 6.9211 | 1 | 2.856 | 184 | 64.4258
8.2 | 6.5307 | 1 | 2.856 | 184 | 64.4258
7.7 | 6.2817 | 1 | 2.856 | 184 | 64.4258
6.6 | 5.4983 | 1 | 2.856 | 184 | 64.4258
5.5 | 4.8386 | 1 | 2.856 | 184 | 64.4258
5.3 | 4.6429 | 1 | 2.856 | 184 | 64.4258
4.9 | 4.432 | 1 | 2.856 | 184 | 64.4258
3.7 | 3.4724 | 1 | 2.856 | 184 | 64.4258
3.9 | 3.5809 | 1 | 2.856 | 184 | 64.4258
3.3 | 3.2096 | 1 | 2.856 | 184 | 64.4258
3.9 | 3.671 | 1 | 2.856 | 184 | 64.4258
3.8 | 3.5717 | 1 | 2.856 | 184 | 64.4258
5.6 | 5.0286 | 1 | 2.856 | 184 | 64.4258
6.5 | 5.4926 | 1 | 2.856 | 184 | 64.4258
6.6 | 5.7282 | 1 | 2.856 | 184 | 64.4258
7.3 | 6.3148 | 1 | 2.856 | 184 | 64.4258
7.3 | 6.4093 | 1 | 2.856 | 184 | 64.4258
8.7 | 8.0223 | 1 | 2.856 | 184 | 64.4258
8.7 | 7.7219 | 1 | 2.856 | 184 | 64.4258
9 | 8.0134 | 1 | 2.856 | 184 | 64.4258
9.2 | 8.1081 | 1 | 2.856 | 184 | 64.4258
8.8 | 7.9189 | 1 | 2.856 | 184 | 64.4258
8.9 | 7.9167 | 1 | 2.856 | 184 | 64.4258
9 | 8.0139 | 1 | 2.856 | 184 | 64.4258
8.8 | 7.82 | 1 | 2.856 | 184 | 64.4258
9 | 8.1139 | 1 | 2.856 | 184 | 64.4258
9 | 8.1139 | 1 | 2.856 | 184 | 64.4258
8.9 | 8.0168 | 1 | 2.856 | 184 | 64.4258
8.8 | 8.0196 | 1 | 2.856 | 184 | 64.4258
8.7 | 8.0226 | 1 | 2.856 | 184 | 64.4258
8.6 | 7.9246 | 1 | 2.856 | 184 | 64.4258
8.4 | 7.8293 | 1 | 2.856 | 184 | 64.4258
7.5 | 7.1933 | 1 | 2.856 | 184 | 64.4258
8 | 7.6889 | 1 | 2.856 | 184 | 64.4258
8.4 | 7.9822 | 1 | 2.856 | 184 | 64.4258
8.7 | 8.0226 | 1 | 2.856 | 184 | 64.4258
8.8 | 8.1207 | 1 | 2.856 | 184 | 64.4258
9.1 | 8.112 | 1 | 2.856 | 184 | 64.4258
9.3 | 8.3064 | 1 | 2.856 | 184 | 64.4258
9.2 | 8.2092 | 1 | 2.856 | 184 | 64.4258
9.4 | 8.2041 | 1 | 2.856 | 184 | 64.4258
9.3 | 8.2065 | 1 | 2.856 | 184 | 64.4258
9.2 | 8.1091 | 1 | 2.856 | 184 | 64.4258
9.2 | 8.2088 | 1 | 2.856 | 184 | 64.4258
9.2 | 8.2083 | 1 | 2.856 | 184 | 64.4258
9.1 | 8.1111 | 1 | 2.856 | 184 | 64.4258
9.2 | 8.1091 | 1 | 2.856 | 184 | 64.4258
9.3 | 8.206 | 1 | 2.856 | 184 | 64.4258
9.2 | 8.0103 | 1 | 2.856 | 184 | 64.4258
8.6 | 7.7239 | 1 | 2.856 | 184 | 64.4258
7.1 | 6.5503 | 1 | 2.856 | 184 | 64.4258
6.9 | 6.3537 | 1 | 2.856 | 184 | 64.4258
4.9 | 4.6634 | 1 | 2.856 | 184 | 64.4258
6.1 | 6.001 | 1 | 2.856 | 184 | 64.4258
5.9 | 5.8017 | 1 | 2.856 | 184 | 64.4258
5.5 | 5.2587 | 1 | 2.856 | 184 | 64.4258
5.4 | 5.0649 | 1 | 2.856 | 184 | 64.4258
5.5 | 5.1638 | 1 | 2.856 | 184 | 64.4258
5.4 | 4.7404 | 1 | 2.856 | 184 | 64.4258
5.5 | 4.9299 | 1 | 2.856 | 184 | 64.4258
5 | 4.439 | 1 | 2.856 | 184 | 64.4258
3.9 | 3.4468 | 1 | 2.856 | 184 | 64.4258
5.2 | 4.7733 | 1 | 2.856 | 184 | 64.4258
5.1 | 4.3121 | 1 | 2.856 | 184 | 64.4258
5.1 | 4.0925 | 1 | 2.856 | 184 | 64.4258
5.7 | 4.3673 | 1 | 2.856 | 184 | 64.4258
6.4 | 4.8195 | 1 | 2.856 | 184 | 64.4258
6.9 | 5.3369 | 1 | 2.856 | 184 | 64.4258
7.2 | 5.6213 | 1 | 2.856 | 184 | 64.4258
6.7 | 5.7294 | 1 | 2.856 | 184 | 64.4258
6.4 | 5.3927 | 1 | 2.856 | 184 | 64.4258
5.3 | 4.7323 | 1 | 2.856 | 184 | 64.4258
6.2 | 5.4285 | 1 | 2.856 | 184 | 64.4258
5.5 | 4.7001 | 1 | 2.856 | 184 | 64.4258
5.3 | 4.6405 | 1 | 2.856 | 184 | 64.4258
5.1 | 4.2213 | 1 | 2.856 | 184 | 64.4258
4.7 | 3.7894 | 1 | 2.856 | 184 | 64.4258
4.8 | 3.8864 | 1 | 2.856 | 184 | 64.4258
4.2 | 3.4333 | 1 | 2.856 | 184 | 64.4258
4.4 | 3.6281 | 1 | 2.856 | 184 | 64.4258
4.7 | 3.5755 | 1 | 2.856 | 184 | 64.4258
4.5 | 3.7251 | 1 | 2.856 | 184 | 64.4258
4.5 | 3.8133 | 1 | 2.856 | 184 | 64.4258
4.7 | 3.9204 | 1 | 2.856 | 184 | 64.4258
5.2 | 4.1865 | 1 | 2.856 | 184 | 64.4258
5.1 | 4.0904 | 1 | 2.856 | 184 | 64.4258
5.7 | 4.4513 | 1 | 2.856 | 184 | 64.4258
6.2 | 4.7143 | 1 | 2.856 | 184 | 64.4258
6.5 | 4.8282 | 1 | 2.856 | 184 | 64.4258
6.6 | 4.9228 | 1 | 2.856 | 184 | 64.4258
6.7 | 4.5999 | 1 | 2.856 | 184 | 64.4258
6.6 | 4.7121 | 1 | 2.856 | 184 | 64.4258
6.5 | 4.7025 | 1 | 2.856 | 184 | 64.4258
6.5 | 4.6192 | 1 | 2.856 | 184 | 64.4258
6.2 | 4.2967 | 1 | 2.856 | 184 | 64.4258
5.5 | 4.176 | 1 | 2.856 | 184 | 64.4258
5.2 | 3.9736 | 1 | 2.856 | 184 | 64.4258
4.7 | 3.5785 | 1 | 2.856 | 184 | 64.4258
4.5 | 3.5979 | 1 | 2.856 | 184 | 64.4258
4.2 | 3.4353 | 1 | 2.856 | 184 | 64.4258
3.1 | 2.5313 | 1 | 2.856 | 184 | 64.4258
1.9 | 1.5604 | 1 | 2.856 | 184 | 64.4258
1.4 | 1.19 | 1 | 2.856 | 184 | 64.4258
1.4 | 1.0667 | 1 | 2.856 | 184 | 64.4258
0.6 | 0.47706 | 1 | 2.856 | 184 | 64.4258
0.7 | 0.45515 | 1 | 2.856 | 184 | 64.4258
0.2 | -0.058066 | 1 | 2.856 | 184 | 64.4258
0 | -0.25589 | 1 | 2.856 | 184 | 64.4258
-0.4 | -0.56872 | 1 | 2.856 | 184 | 64.4258
-0.4 | -0.56862 | 1 | 2.856 | 184 | 64.4258
0.7 | 0.45529 | 1 | 2.856 | 184 | 64.4258
2.2 | 1.7321 | 1 | 2.856 | 184 | 64.4258
3.9 | 3.1014 | 1 | 2.856 | 184 | 64.4258
5.3 | 4.2001 | 1 | 2.856 | 184 | 64.4258
6.5 | 5.1785 | 1 | 2.856 | 184 | 64.4258
7.8 | 6.1517 | 1 | 2.856 | 184 | 64.4258
7.2 | 5.8491 | 1 | 2.856 | 184 | 64.4258
6.9 | 5.4727 | 1 | 2.856 | 184 | 64.4258
6.4 | 5.3958 | 1 | 2.856 | 184 | 64.4258
6.6 | 5.7278 | 1 | 2.856 | 184 | 64.4258
6.7 | 5.9187 | 1 | 2.856 | 184 | 64.4258
6.7 | 5.9187 | 1 | 2.856 | 184 | 64.4258
6.9 | 6.1139 | 1 | 2.856 | 184 | 64.4258
7.1 | 6.3091 | 1 | 2.856 | 184 | 64.4258
7.1 | 6.453 | 1 | 2.856 | 184 | 64.4258
7.1 | 6.5501 | 1 | 2.856 | 184 | 64.4258
6.9 | 6.2569 | 1 | 2.856 | 184 | 64.4258
6.7 | 6.0132 | 1 | 2.856 | 184 | 64.4258
6.8 | 6.2548 | 1 | 2.856 | 184 | 64.4258
6.7 | 5.6858 | 1 | 2.856 | 184 | 64.4258
6.5 | 5.4921 | 1 | 2.856 | 184 | 64.4258
6.3 | 5.3896 | 1 | 2.856 | 184 | 64.4258
5.9 | 5.138 | 1 | 2.856 | 184 | 64.4258
5.7 | 4.9429 | 1 | 2.856 | 184 | 64.4258
5.7 | 5.0344 | 1 | 2.856 | 184 | 64.4258
5.9 | 5.2302 | 1 | 2.856 | 184 | 64.4258
5.8 | 4.9044 | 1 | 2.856 | 184 | 64.4258
5.7 | 5.0341 | 1 | 2.856 | 184 | 64.4258
5.8 | 5.1319 | 1 | 2.856 | 184 | 64.4258
5.8 | 5.0401 | 1 | 2.856 | 184 | 64.4258
5.8 | 4.8138 | 1 | 2.856 | 184 | 64.4258
5.5 | 4.3923 | 1 | 2.856 | 184 | 64.4258
4.8 | 3.803 | 1 | 2.856 | 184 | 64.4258
4.3 | 3.4044 | 1 | 2.856 | 184 | 64.4258
3.9 | 2.7685 | 1 | 2.856 | 184 | 64.4258
3.3 | 2.0736 | 1 | 2.856 | 184 | 64.4258
3 | 1.7476 | 1 | 2.856 | 184 | 64.4258
2.7 | 1.5764 | 1 | 2.856 | 184 | 64.4258
2.6 | 1.3455 | 1 | 2.856 | 184 | 64.4258
2.2 | 1.1578 | 1 | 2.856 | 184 | 64.4258
1.8 | 0.88215 | 1 | 2.856 | 184 | 64.4258
1.7 | 0.7805 | 1 | 2.856 | 184 | 64.4258
1.5 | 0.70693 | 1 | 2.856 | 184 | 64.4258
1.4 | 0.69215 | 1 | 2.856 | 184 | 64.4258
1.3 | 0.72214 | 1 | 2.856 | 184 | 64.4258
1.4 | 0.82525 | 1 | 2.856 | 184 | 64.4258
1.3 | 0.72214 | 1 | 2.856 | 184 | 64.4258
1.4 | 0.82525 | 1 | 2.856 | 184 | 64.4258
1.5 | 0.92365 | 1 | 2.856 | 184 | 64.4258
1.6 | 1.0218 | 1 | 2.856 | 184 | 64.4258
1.8 | 1.1378 | 1 | 2.856 | 184 | 64.4258
1.9 | 1.235 | 1 | 2.856 | 184 | 64.4258
2.1 | 1.4301 | 1 | 2.856 | 184 | 64.4258
2.2 | 1.4078 | 1 | 2.856 | 184 | 64.4258
2.4 | 1.602 | 1 | 2.856 | 184 | 64.4258
2.2 | 1.4078 | 1 | 2.856 | 184 | 64.4258
2.2 | 1.4078 | 1 | 2.856 | 184 | 64.4258
2.1 | 1.4301 | 1 | 2.856 | 184 | 64.4258
2.3 | 1.7475 | 1 | 2.856 | 184 | 64.4258
2.2 | 1.7318 | 1 | 2.856 | 184 | 64.4258
2.5 | 2.0687 | 1 | 2.856 | 184 | 64.4258
2.6 | 2.1672 | 1 | 2.856 | 184 | 64.4258
2.6 | 2.3809 | 1 | 2.856 | 184 | 64.4258
2.6 | 2.4678 | 1 | 2.856 | 184 | 64.4258
2.8 | 2.6668 | 1 | 2.856 | 184 | 64.4258
3 | 2.8659 | 1 | 2.856 | 184 | 64.4258
3.4 | 3.3092 | 1 | 2.856 | 184 | 64.4258
3.9 | 3.6706 | 1 | 2.856 | 184 | 64.4258
4 | 3.7698 | 1 | 2.856 | 184 | 64.4258
4.8 | 4.4708 | 1 | 2.856 | 184 | 64.4258
5.7 | 5.2664 | 1 | 2.856 | 184 | 64.4258
6.6 | 6.0576 | 1 | 2.856 | 184 | 64.4258
6.8 | 6.2542 | 1 | 2.856 | 184 | 64.4258
7.6 | 6.6995 | 1 | 2.856 | 184 | 64.4258
8.4 | 7.1862 | 1 | 2.856 | 184 | 64.4258
9.1 | 8.2093 | 1 | 2.856 | 184 | 64.4258
9.6 | 8.5944 | 1 | 2.856 | 184 | 64.4258
10.2 | 8.871 | 1 | 2.856 | 184 | 64.4258
10.1 | 8.5755 | 1 | 2.856 | 184 | 64.4258
9.9 | 8.4819 | 1 | 2.856 | 184 | 64.4258
9.9 | 8.4819 | 1 | 2.856 | 184 | 64.4258
9.8 | 8.3858 | 1 | 2.856 | 184 | 64.4258
9.9 | 8.3343 | 1 | 2.856 | 184 | 64.4258
10.1 | 8.5748 | 1 | 2.856 | 184 | 64.4258
10.1 | 8.5741 | 1 | 2.856 | 184 | 64.4258
9.9 | 8.5807 | 1 | 2.856 | 184 | 64.4258
10 | 8.6765 | 1 | 2.856 | 184 | 64.4258
10.1 | 8.7722 | 1 | 2.856 | 184 | 64.4258
10.1 | 8.7722 | 1 | 2.856 | 184 | 64.4258
10 | 8.7767 | 1 | 2.856 | 184 | 64.4258
9.9 | 8.6795 | 1 | 2.856 | 184 | 64.4258
10.3 | 8.6644 | 1 | 2.856 | 184 | 64.4258
10.3 | 8.7635 | 1 | 2.856 | 184 | 64.4258
10.1 | 8.8728 | 1 | 2.856 | 184 | 64.4258
10.2 | 8.9688 | 1 | 2.856 | 184 | 64.4258
10.4 | 9.3174 | 1 | 2.856 | 184 | 64.4258
10.4 | 9.4216 | 1 | 2.856 | 184 | 64.4258
11.1 | 9.7879 | 1 | 2.856 | 184 | 64.4258
11.6 | 9.9575 | 1 | 2.856 | 184 | 64.4258
11.7 | 10.0532 | 1 | 2.856 | 184 | 64.4258
11.9 | 10.0389 | 1 | 2.856 | 184 | 64.4258
11.8 | 9.9438 | 1 | 2.856 | 184 | 64.4258
11.8 | 9.9438 | 1 | 2.856 | 184 | 64.4258
11.4 | 9.6137 | 1 | 2.856 | 184 | 64.4258
11.2 | 9.524 | 1 | 2.856 | 184 | 64.4258
10.5 | 9.3109 | 1 | 2.856 | 184 | 64.4258
9.9 | 8.8832 | 1 | 2.856 | 184 | 64.4258
9.7 | 8.7914 | 1 | 2.856 | 184 | 64.4258
9.6 | 8.8488 | 1 | 2.856 | 184 | 64.4258
9.9 | 9.1426 | 1 | 2.856 | 184 | 64.4258
10 | 9.2402 | 1 | 2.856 | 184 | 64.4258
9.6 | 8.8481 | 1 | 2.856 | 184 | 64.4258
9.6 | 8.8481 | 1 | 2.856 | 184 | 64.4258
10.2 | 8.9666 | 1 | 2.856 | 184 | 64.4258
10.1 | 8.9717 | 1 | 2.856 | 184 | 64.4258
9.8 | 8.7823 | 1 | 2.856 | 184 | 64.4258
9.6 | 8.6897 | 1 | 2.856 | 184 | 64.4258
9.6 | 9.0564 | 1 | 2.856 | 184 | 64.4258
10 | 9.5583 | 1 | 2.856 | 184 | 64.4258
10.4 | 9.8441 | 1 | 2.856 | 184 | 64.4258
11.1 | 10.2047 | 1 | 2.856 | 184 | 64.4258
10.9 | 9.7951 | 1 | 2.856 | 184 | 64.4258
10.1 | 8.8637 | 1 | 2.856 | 184 | 64.4258
9.7 | 8.5783 | 1 | 2.856 | 184 | 64.4258
10.3 | 8.7515 | 1 | 2.856 | 184 | 64.4258
10.3 | 8.3079 | 1 | 2.856 | 184 | 64.4258
10 | 7.8831 | 1 | 2.856 | 184 | 64.4258
9.2 | 6.8594 | 1 | 2.856 | 184 | 64.4258
8.6 | 6.5685 | 1 | 2.856 | 184 | 64.4258
8.2 | 6.2821 | 1 | 2.856 | 184 | 64.4258
7.9 | 6.0004 | 1 | 2.856 | 184 | 64.4258
7.6 | 5.673 | 1 | 2.856 | 184 | 64.4258
7.4 | 5.4859 | 1 | 2.856 | 184 | 64.4258
7 | 5.067 | 1 | 2.856 | 184 | 64.4258
7.5 | 5.2378 | 1 | 2.856 | 184 | 64.4258
7 | 4.9831 | 1 | 2.856 | 184 | 64.4258
6.5 | 4.6828 | 1 | 2.856 | 184 | 64.4258
6.3 | 4.3683 | 1 | 2.856 | 184 | 64.4258
6.6 | 4.9045 | 1 | 2.856 | 184 | 64.4258
7.3 | 5.5219 | 1 | 2.856 | 184 | 64.4258
7.5 | 5.7099 | 1 | 2.856 | 184 | 64.4258
7.2 | 5.7381 | 1 | 2.856 | 184 | 64.4258
7.3 | 5.8321 | 1 | 2.856 | 184 | 64.4258
7.1 | 6.1041 | 1 | 2.856 | 184 | 64.4258
6.9 | 6.2453 | 1 | 2.856 | 184 | 64.4258
6.5 | 6.2965 | 1 | 2.856 | 184 | 64.4258
6.6 | 6.2448 | 1 | 2.856 | 184 | 64.4258
5.9 | 5.4552 | 1 | 2.856 | 184 | 64.4258
6.2 | 5.2751 | 1 | 2.856 | 184 | 64.4258
6.7 | 5.5745 | 1 | 2.856 | 184 | 64.4258
6.8 | 4.9998 | 1 | 2.856 | 184 | 64.4258
6.5 | 4.103 | 1 | 2.856 | 184 | 64.4258
4.9 | 3.4177 | 1 | 2.856 | 184 | 64.4258
4.9 | 3.4185 | 1 | 2.856 | 184 | 64.4258
5.9 | 2.9177 | 1 | 2.856 | 184 | 64.4258
6.1 | 3.1096 | 1 | 2.856 | 184 | 64.4258
5.3 | 2.7984 | 1 | 2.856 | 184 | 64.4258
4.8 | 2.5245 | 1 | 2.856 | 184 | 64.4258
4.1 | 2.1378 | 1 | 2.856 | 184 | 64.4258
3.7 | 1.7064 | 1 | 2.856 | 184 | 64.4258
3.2 | 1.7178 | 1 | 2.856 | 184 | 64.4258
1.2 | 0.48058 | 1 | 2.856 | 184 | 64.4258
1.9 | 0.97541 | 1 | 2.856 | 184 | 64.4258
2.6 | 1.7082 | 1 | 2.856 | 184 | 64.4258
3.2 | 2.0856 | 1 | 2.856 | 184 | 64.4258
2.9 | 1.877 | 1 | 2.856 | 184 | 64.4258
4.3 | 2.9364 | 1 | 2.856 | 184 | 64.4258
5.6 | 3.8012 | 1 | 2.856 | 184 | 64.4258
5.8 | 4.113 | 1 | 2.856 | 184 | 64.4258
6.5 | 4.6055 | 1 | 2.856 | 184 | 64.4258
7.1 | 5.0829 | 1 | 2.856 | 184 | 64.4258
7.3 | 5.3986 | 1 | 2.856 | 184 | 64.4258
7.3 | 5.5282 | 1 | 2.856 | 184 | 64.4258
7.3 | 5.7492 | 1 | 2.856 | 184 | 64.4258
7.5 | 5.805 | 1 | 2.856 | 184 | 64.4258
7.4 | 5.9343 | 1 | 2.856 | 184 | 64.4258
7 | 5.7797 | 1 | 2.856 | 184 | 64.4258
7 | 5.779 | 1 | 2.856 | 184 | 64.4258
7.2 | 5.9709 | 1 | 2.856 | 184 | 64.4258
6.9 | 5.8677 | 1 | 2.856 | 184 | 64.4258
6.4 | 5.2912 | 1 | 2.856 | 184 | 64.4258
5.8 | 5.2176 | 1 | 2.856 | 184 | 64.4258
4.9 | 3.9746 | 1 | 2.856 | 184 | 64.4258
4.5 | 3.9411 | 1 | 2.856 | 184 | 64.4258
4.4 | 3.7086 | 1 | 2.856 | 184 | 64.4258
4 | 3.101 | 1 | 2.856 | 184 | 64.4258
4.1 | 3.1979 | 1 | 2.856 | 184 | 64.4258
4.3 | 3.3918 | 1 | 2.856 | 184 | 64.4258
4.6 | 3.4678 | 1 | 2.856 | 184 | 64.4258
4.9 | 3.4201 | 1 | 2.856 | 184 | 64.4258
4.7 | 2.871 | 1 | 2.856 | 184 | 64.4258
4.5 | 1.9125 | 1 | 2.856 | 184 | 64.4258
4.3 | 1.0682 | 1 | 2.856 | 184 | 64.4258
5 | 1.7154 | 1 | 2.856 | 184 | 64.4258
5.7 | 1.9389 | 1 | 2.856 | 184 | 64.4258
4.9 | 1.592 | 1 | 2.856 | 184 | 64.4258
6.1 | 2.6248 | 1 | 2.856 | 184 | 64.4258
6.1 | 2.3758 | 1 | 2.856 | 184 | 64.4258
5.8 | 2.0717 | 1 | 2.856 | 184 | 64.4258
5 | 1.7266 | 1 | 2.856 | 184 | 64.4258
3.7 | 1.2418 | 1 | 2.856 | 184 | 64.4258
2.9 | 1.0142 | 1 | 2.856 | 184 | 64.4258
2.9 | 1.1356 | 1 | 2.856 | 184 | 64.4258
1.8 | 0.49651 | 1 | 2.856 | 184 | 64.4258
1.5 | 0.44535 | 1 | 2.856 | 184 | 64.4258
1.1 | 0.0014612 | 1 | 2.856 | 184 | 64.4258
0.9 | -0.071365 | 1 | 2.856 | 184 | 64.4258
1.3 | 0.20326 | 1 | 2.856 | 184 | 64.4258
1.3 | 0.32879 | 1 | 2.856 | 184 | 64.4258
1 | 0.15143 | 1 | 2.856 | 184 | 64.4258
0 | -0.58466 | 1 | 2.856 | 184 | 64.4258
-0.7 | -1.1103 | 1 | 2.856 | 184 | 64.4258
-1.7 | -2.0159 | 1 | 2.856 | 184 | 64.4258
-2.6 | -2.9761 | 1 | 2.856 | 184 | 64.4258
-0.4 | -1.0141 | 1 | 2.856 | 184 | 64.4258
-0.5 | -0.87369 | 1 | 2.856 | 184 | 64.4258
1.1 | -0.15196 | 1 | 2.856 | 184 | 64.4258
1.5 | 0.57362 | 1 | 2.856 | 184 | 64.4258
3.6 | 1.2657 | 1 | 2.856 | 184 | 64.4258
4.8 | 2.0237 | 1 | 2.856 | 184 | 64.4258
5.6 | 2.2128 | 1 | 2.856 | 184 | 64.4258
6.1 | 3.2528 | 1 | 2.856 | 184 | 64.4258
6.1 | 3.7597 | 1 | 2.856 | 184 | 64.4258
5.7 | 3.4675 | 1 | 2.856 | 184 | 64.4258
5.5 | 3.4745 | 1 | 2.856 | 184 | 64.4258
5.3 | 3.486 | 1 | 2.856 | 184 | 64.4258
5 | 3.5263 | 1 | 2.856 | 184 | 64.4258
5.5 | 3.8359 | 1 | 2.856 | 184 | 64.4258
5.3 | 3.9362 | 1 | 2.856 | 184 | 64.4258
4.6 | 3.4763 | 1 | 2.856 | 184 | 64.4258
4 | 2.9821 | 1 | 2.856 | 184 | 64.4258
3.1 | 2.3182 | 1 | 2.856 | 184 | 64.4258
2.3 | 1.9535 | 1 | 2.856 | 184 | 64.4258
1.8 | 1.4597 | 1 | 2.856 | 184 | 64.4258
1.7 | 1.4865 | 1 | 2.856 | 184 | 64.4258
1.9 | 1.6851 | 1 | 2.856 | 184 | 64.4258
2.2 | 2.069 | 1 | 2.856 | 184 | 64.4258
2.3 | 2.0822 | 1 | 2.856 | 184 | 64.4258
2.6 | 2.4673 | 1 | 2.856 | 184 | 64.4258
2.7 | 2.3498 | 1 | 2.856 | 184 | 64.4258
2.1 | 1.8842 | 1 | 2.856 | 184 | 64.4258
1.8 | 1.5866 | 1 | 2.856 | 184 | 64.4258
2 | 1.659 | 1 | 2.856 | 184 | 64.4258
2.6 | 2.2516 | 1 | 2.856 | 184 | 64.4258
3.3 | 2.7271 | 1 | 2.856 | 184 | 64.4258
3.8 | 3.1308 | 1 | 2.856 | 184 | 64.4258
4.2 | 3.4349 | 1 | 2.856 | 184 | 64.4258
4.1 | 3.21 | 1 | 2.856 | 184 | 64.4258
3.7 | 2.9483 | 1 | 2.856 | 184 | 64.4258
2.3 | 1.9555 | 1 | 2.856 | 184 | 64.4258
2.6 | 2.1669 | 1 | 2.856 | 184 | 64.4258
2 | 1.6591 | 1 | 2.856 | 184 | 64.4258
2.1 | 1.633 | 1 | 2.856 | 184 | 64.4258
2.2 | 1.6486 | 1 | 2.856 | 184 | 64.4258
1.9 | 1.4361 | 1 | 2.856 | 184 | 64.4258
1.7 | 1.2392 | 1 | 2.856 | 184 | 64.4258
2.2 | 1.6483 | 1 | 2.856 | 184 | 64.4258
3 | 2.3063 | 1 | 2.856 | 184 | 64.4258
4.2 | 3.5202 | 1 | 2.856 | 184 | 64.4258
4.8 | 4.3316 | 1 | 2.856 | 184 | 64.4258
5.5 | 5.0676 | 1 | 2.856 | 184 | 64.4258
6.3 | 5.6176 | 1 | 2.856 | 184 | 64.4258
6.9 | 6.2528 | 1 | 2.856 | 184 | 64.4258
7.3 | 6.6447 | 1 | 2.856 | 184 | 64.4258
7.8 | 7.0356 | 1 | 2.856 | 184 | 64.4258
8.3 | 7.5241 | 1 | 2.856 | 184 | 64.4258
8.8 | 8.013 | 1 | 2.856 | 184 | 64.4258
9.5 | 8.5939 | 1 | 2.856 | 184 | 64.4258
10.3 | 9.4263 | 1 | 2.856 | 184 | 64.4258
11 | 9.8961 | 1 | 2.856 | 184 | 64.4258
11.6 | 10.2654 | 1 | 2.856 | 184 | 64.4258
10.8 | 9.8077 | 1 | 2.856 | 184 | 64.4258
11.4 | 10.1786 | 1 | 2.856 | 184 | 64.4258
10.9 | 9.906 | 1 | 2.856 | 184 | 64.4258
11.2 | 9.9854 | 1 | 2.856 | 184 | 64.4258
11 | 10.1109 | 1 | 2.856 | 184 | 64.4258
11.8 | 10.3544 | 1 | 2.856 | 184 | 64.4258
11.5 | 10.1712 | 1 | 2.856 | 184 | 64.4258
10.8 | 9.8095 | 1 | 2.856 | 184 | 64.4258
11.1 | 9.9947 | 1 | 2.856 | 184 | 64.4258
11.2 | 9.9859 | 1 | 2.856 | 184 | 64.4258
11.4 | 10.2861 | 1 | 2.856 | 184 | 64.4258
10.6 | 9.6133 | 1 | 2.856 | 184 | 64.4258
11.3 | 9.7681 | 1 | 2.856 | 184 | 64.4258
11.4 | 8.9669 | 1 | 2.856 | 184 | 64.4258
10.8 | 8.2668 | 1 | 2.856 | 184 | 64.4258
11 | 9.0277 | 1 | 2.856 | 184 | 64.4258
10.5 | 8.5061 | 1 | 2.856 | 184 | 64.4258
10.4 | 8.4116 | 1 | 2.856 | 184 | 64.4258
11.2 | 8.9721 | 1 | 2.856 | 184 | 64.4258
12.1 | 9.5719 | 1 | 2.856 | 184 | 64.4258
12.4 | 9.7529 | 1 | 2.856 | 184 | 64.4258
12.2 | 9.6641 | 1 | 2.856 | 184 | 64.4258
12 | 9.575 | 1 | 2.856 | 184 | 64.4258
11.8 | 9.3879 | 1 | 2.856 | 184 | 64.4258
11.6 | 9.298 | 1 | 2.856 | 184 | 64.4258
11.6 | 9.0566 | 1 | 2.856 | 184 | 64.4258
11.5 | 8.8217 | 1 | 2.856 | 184 | 64.4258
11.1 | 8.4512 | 1 | 2.856 | 184 | 64.4258
11.1 | 8.2206 | 1 | 2.856 | 184 | 64.4258
11.1 | 8.2206 | 1 | 2.856 | 184 | 64.4258
10.9 | 7.7704 | 1 | 2.856 | 184 | 64.4258
10.7 | 7.5868 | 1 | 2.856 | 184 | 64.4258
10.7 | 7.6743 | 1 | 2.856 | 184 | 64.4258
10.7 | 7.4556 | 1 | 2.856 | 184 | 64.4258
10.1 | 7.9822 | 1 | 2.856 | 184 | 64.4258
9.9 | 7.6546 | 1 | 2.856 | 184 | 64.4258
9.6 | 6.797 | 1 | 2.856 | 184 | 64.4258
8.4 | 5.495 | 1 | 2.856 | 184 | 64.4258
8.1 | 5.1811 | 1 | 2.856 | 184 | 64.4258
7.8 | 5.1074 | 1 | 2.856 | 184 | 64.4258
7.8 | 5.4357 | 1 | 2.856 | 184 | 64.4258
7.9 | 5.8712 | 1 | 2.856 | 184 | 64.4258
8.2 | 5.9765 | 1 | 2.856 | 184 | 64.4258
9.1 | 6.421 | 1 | 2.856 | 184 | 64.4258
9.7 | 7.1476 | 1 | 2.856 | 184 | 64.4258
9.9 | 7.3302 | 1 | 2.856 | 184 | 64.4258
10 | 8.2157 | 1 | 2.856 | 184 | 64.4258
9.9 | 8.8725 | 1 | 2.856 | 184 | 64.4258
11 | 9.3155 | 1 | 2.856 | 184 | 64.4258
9.9 | 7.7821 | 1 | 2.856 | 184 | 64.4258
9.2 | 6.8502 | 1 | 2.856 | 184 | 64.4258
8.2 | 5.832 | 1 | 2.856 | 184 | 64.4258
7.7 | 5.4532 | 1 | 2.856 | 184 | 64.4258
7.2 | 5.5069 | 1 | 2.856 | 184 | 64.4258
6.2 | 4.6033 | 1 | 2.856 | 184 | 64.4258
5.1 | 3.7277 | 1 | 2.856 | 184 | 64.4258
4.4 | 2.9362 | 1 | 2.856 | 184 | 64.4258
3.5 | 2.1207 | 1 | 2.856 | 184 | 64.4258
3.3 | 1.9303 | 1 | 2.856 | 184 | 64.4258
3.5 | 2.3624 | 1 | 2.856 | 184 | 64.4258
3.2 | 2.1556 | 1 | 2.856 | 184 | 64.4258
2.8 | 1.7702 | 1 | 2.856 | 184 | 64.4258
2.3 | 1.4894 | 1 | 2.856 | 184 | 64.4258
2.3 | 1.3686 | 1 | 2.856 | 184 | 64.4258
1.8 | 0.86449 | 1 | 2.856 | 184 | 64.4258
1.7 | 0.89663 | 1 | 2.856 | 184 | 64.4258
2.9 | 1.7481 | 1 | 2.856 | 184 | 64.4258
4.5 | 2.4288 | 1 | 2.856 | 184 | 64.4258
4.3 | 2.3613 | 1 | 2.856 | 184 | 64.4258
4.6 | 2.6517 | 1 | 2.856 | 184 | 64.4258
4.5 | 2.4288 | 1 | 2.856 | 184 | 64.4258
3.9 | 2.3063 | 1 | 2.856 | 184 | 64.4258
3.6 | 2.1007 | 1 | 2.856 | 184 | 64.4258
2.5 | 0.68164 | 1 | 2.856 | 184 | 64.4258
1.9 | 0.33375 | 1 | 2.856 | 184 | 64.4258
0.7 | -0.43177 | 1 | 2.856 | 184 | 64.4258
-0.7 | -1.7639 | 1 | 2.856 | 184 | 64.4258
-0.2 | -1.0613 | 1 | 2.856 | 184 | 64.4258
-1 | -1.6434 | 1 | 2.856 | 184 | 64.4258
-0.6 | -1.4839 | 1 | 2.856 | 184 | 64.4258
-1.9 | -2.4805 | 1 | 2.856 | 184 | 64.4258
-1.5 | -2.0536 | 1 | 2.856 | 184 | 64.4258
-2 | -2.5775 | 1 | 2.856 | 184 | 64.4258
-2.2 | -2.7718 | 1 | 2.856 | 184 | 64.4258
-1.9 | -2.3683 | 1 | 2.856 | 184 | 64.4258
-1.5 | -2.0529 | 1 | 2.856 | 184 | 64.4258
-0.8 | -1.4476 | 1 | 2.856 | 184 | 64.4258
-1.8 | -2.2699 | 1 | 2.856 | 184 | 64.4258
-1.8 | -2.1169 | 1 | 2.856 | 184 | 64.4258
-1.3 | -1.7415 | 1 | 2.856 | 184 | 64.4258
0.1 | -0.61177 | 1 | 2.856 | 184 | 64.4258
1.5 | -0.19456 | 1 | 2.856 | 184 | 64.4258
3.7 | 1.9986 | 1 | 2.856 | 184 | 64.4258
4.3 | 1.8447 | 1 | 2.856 | 184 | 64.4258
4.5 | 2.1982 | 1 | 2.856 | 184 | 64.4258
4.1 | 2.14 | 1 | 2.856 | 184 | 64.4258
3.2 | 1.5923 | 1 | 2.856 | 184 | 64.4258
2.3 | 0.90855 | 1 | 2.856 | 184 | 64.4258
1.8 | 0.6178 | 1 | 2.856 | 184 | 64.4258
1.5 | 0.57093 | 1 | 2.856 | 184 | 64.4258
1.4 | 0.17659 | 1 | 2.856 | 184 | 64.4258
0.4 | -0.62957 | 1 | 2.856 | 184 | 64.4258
-0.4 | -1.0541 | 1 | 2.856 | 184 | 64.4258
-1.3 | -1.8151 | 1 | 2.856 | 184 | 64.4258
0 | -0.70467 | 1 | 2.856 | 184 | 64.4258
-2 | -2.3498 | 1 | 2.856 | 184 | 64.4258
-2.5 | -2.7301 | 1 | 2.856 | 184 | 64.4258
-0.7 | -1.3448 | 1 | 2.856 | 184 | 64.4258
-1.3 | -1.7384 | 1 | 2.856 | 184 | 64.4258
-0.8 | -1.3268 | 1 | 2.856 | 184 | 64.4258
-1.4 | -1.9502 | 1 | 2.856 | 184 | 64.4258
-1.1 | -1.6192 | 1 | 2.856 | 184 | 64.4258
-1.6 | -1.9173 | 1 | 2.856 | 184 | 64.4258
-1.3 | -1.7381 | 1 | 2.856 | 184 | 64.4258
0.3 | -0.41303 | 1 | 2.856 | 184 | 64.4258
2.1 | 1.1838 | 1 | 2.856 | 184 | 64.4258
4 | 2.421 | 1 | 2.856 | 184 | 64.4258
4.9 | 3.1115 | 1 | 2.856 | 184 | 64.4258
5 | 2.9716 | 1 | 2.856 | 184 | 64.4258
4.5 | 2.6955 | 1 | 2.856 | 184 | 64.4258
4.5 | 2.3275 | 1 | 2.856 | 184 | 64.4258
3.6 | 1.863 | 1 | 2.856 | 184 | 64.4258
3.5 | 2.0205 | 1 | 2.856 | 184 | 64.4258
3.9 | 2.6782 | 1 | 2.856 | 184 | 64.4258
4.5 | 3.2508 | 1 | 2.856 | 184 | 64.4258
5.5 | 4.1655 | 1 | 2.856 | 184 | 64.4258
6.4 | 5.0691 | 1 | 2.856 | 184 | 64.4258
7.2 | 6.2066 | 1 | 2.856 | 184 | 64.4258
7.5 | 6.739 | 1 | 2.856 | 184 | 64.4258
8.1 | 7.2249 | 1 | 2.856 | 184 | 64.4258
7.9 | 7.2281 | 1 | 2.856 | 184 | 64.4258
4.8 | 4.4663 | 1 | 2.856 | 184 | 64.4258
4.1 | 3.866 | 1 | 2.856 | 184 | 64.4258
3.5 | 3.2707 | 1 | 2.856 | 184 | 64.4258
4.2 | 3.1673 | 1 | 2.856 | 184 | 64.4258
3.9 | 2.5499 | 1 | 2.856 | 184 | 64.4258
3 | 1.8506 | 1 | 2.856 | 184 | 64.4258
3 | 1.6013 | 1 | 2.856 | 184 | 64.4258
4 | 2.0377 | 1 | 2.856 | 184 | 64.4258
5.1 | 2.6912 | 1 | 2.856 | 184 | 64.4258
5.9 | 3.2945 | 1 | 2.856 | 184 | 64.4258
6.3 | 3.3471 | 1 | 2.856 | 184 | 64.4258
6.9 | 3.9873 | 1 | 2.856 | 184 | 64.4258
6.5 | 3.5382 | 1 | 2.856 | 184 | 64.4258
5.3 | 3.054 | 1 | 2.856 | 184 | 64.4258
4.7 | 2.5171 | 1 | 2.856 | 184 | 64.4258
4.1 | 2.2692 | 1 | 2.856 | 184 | 64.4258
4.1 | 2.2702 | 1 | 2.856 | 184 | 64.4258
3.4 | 1.7924 | 1 | 2.856 | 184 | 64.4258
3.9 | 2.44 | 1 | 2.856 | 184 | 64.4258
4.3 | 2.6245 | 1 | 2.856 | 184 | 64.4258
3.8 | 2.465 | 1 | 2.856 | 184 | 64.4258
2.2 | 1.4037 | 1 | 2.856 | 184 | 64.4258
2.9 | 2.0026 | 1 | 2.856 | 184 | 64.4258
3.4 | 2.2839 | 1 | 2.856 | 184 | 64.4258
3.4 | 2.4058 | 1 | 2.856 | 184 | 64.4258
1.9 | 1.4353 | 1 | 2.856 | 184 | 64.4258
3.2 | 2.4184 | 1 | 2.856 | 184 | 64.4258
2.6 | 1.9164 | 1 | 2.856 | 184 | 64.4258
2.7 | 2.0144 | 1 | 2.856 | 184 | 64.4258
2.7 | 2.0147 | 1 | 2.856 | 184 | 64.4258
2.4 | 1.7221 | 1 | 2.856 | 184 | 64.4258
3.3 | 2.4343 | 1 | 2.856 | 184 | 64.4258
4.8 | 3.508 | 1 | 2.856 | 184 | 64.4258
6.5 | 4.7053 | 1 | 2.856 | 184 | 64.4258
7 | 5.0916 | 1 | 2.856 | 184 | 64.4258
7.4 | 5.51 | 1 | 2.856 | 184 | 64.4258
7.7 | 5.7049 | 1 | 2.856 | 184 | 64.4258
7.7 | 6.0551 | 1 | 2.856 | 184 | 64.4258
7.7 | 6.0551 | 1 | 2.856 | 184 | 64.4258
7.5 | 6.1816 | 1 | 2.856 | 184 | 64.4258
8.1 | 6.4349 | 1 | 2.856 | 184 | 64.4258
8.5 | 7.0466 | 1 | 2.856 | 184 | 64.4258
9.5 | 8.199 | 1 | 2.856 | 184 | 64.4258
9.3 | 8.4051 | 1 | 2.856 | 184 | 64.4258
9.4 | 8.5026 | 1 | 2.856 | 184 | 64.4258
9.3 | 8.6616 | 1 | 2.856 | 184 | 64.4258
9.4 | 8.8643 | 1 | 2.856 | 184 | 64.4258
8.5 | 8.1838 | 1 | 2.856 | 184 | 64.4258
9.3 | 8.8708 | 1 | 2.856 | 184 | 64.4258
9.5 | 9.0684 | 1 | 2.856 | 184 | 64.4258
10.1 | 9.4476 | 1 | 2.856 | 184 | 64.4258
10.3 | 9.4326 | 1 | 2.856 | 184 | 64.4258
11.1 | 9.587 | 1 | 2.856 | 184 | 64.4258
10.9 | 9.5994 | 1 | 2.856 | 184 | 64.4258
11.3 | 9.0832 | 1 | 2.856 | 184 | 64.4258
11.5 | 9.079 | 1 | 2.856 | 184 | 64.4258
11.5 | 9.3197 | 1 | 2.856 | 184 | 64.4258
11.8 | 9.0748 | 1 | 2.856 | 184 | 64.4258
11.3 | 8.6572 | 1 | 2.856 | 184 | 64.4258
12.5 | 9.5321 | 1 | 2.856 | 184 | 64.4258
12.1 | 9.1178 | 1 | 2.856 | 184 | 64.4258
11.3 | 8.8912 | 1 | 2.856 | 184 | 64.4258
10.7 | 8.5187 | 1 | 2.856 | 184 | 64.4258
9.8 | 8.0489 | 1 | 2.856 | 184 | 64.4258
9.7 | 8.0495 | 1 | 2.856 | 184 | 64.4258
9.3 | 7.9569 | 1 | 2.856 | 184 | 64.4258
9.2 | 7.8601 | 1 | 2.856 | 184 | 64.4258
9 | 7.9123 | 1 | 2.856 | 184 | 64.4258
9.2 | 8.007 | 1 | 2.856 | 184 | 64.4258
10.2 | 8.5253 | 1 | 2.856 | 184 | 64.4258
9.9 | 8.3357 | 1 | 2.856 | 184 | 64.4258
10.1 | 8.3315 | 1 | 2.856 | 184 | 64.4258
9.5 | 7.9526 | 1 | 2.856 | 184 | 64.4258
9.9 | 8.0459 | 1 | 2.856 | 184 | 64.4258
10.5 | 8.2799 | 1 | 2.856 | 184 | 64.4258
10.6 | 8.5158 | 1 | 2.856 | 184 | 64.4258
10.7 | 9.1495 | 1 | 2.856 | 184 | 64.4258
10.2 | 9.5443 | 1 | 2.856 | 184 | 64.4258
10.5 | 9.8391 | 1 | 2.856 | 184 | 64.4258
10.9 | 9.9099 | 1 | 2.856 | 184 | 64.4258
11.5 | 9.9675 | 1 | 2.856 | 184 | 64.4258
11.5 | 9.9675 | 1 | 2.856 | 184 | 64.4258
11.8 | 9.846 | 1 | 2.856 | 184 | 64.4258
12.5 | 9.7645 | 1 | 2.856 | 184 | 64.4258
12.1 | 9.4413 | 1 | 2.856 | 184 | 64.4258
10.5 | 8.6144 | 1 | 2.856 | 184 | 64.4258
9.7 | 8.0479 | 1 | 2.856 | 184 | 64.4258
9.3 | 7.8591 | 1 | 2.856 | 184 | 64.4258
7.6 | 6.0481 | 1 | 2.856 | 184 | 64.4258
7.7 | 5.6153 | 1 | 2.856 | 184 | 64.4258
5.8 | 4.2058 | 1 | 2.856 | 184 | 64.4258
6 | 4.9583 | 1 | 2.856 | 184 | 64.4258
5.1 | 4.219 | 1 | 2.856 | 184 | 64.4258
3.8 | 3.1261 | 1 | 2.856 | 184 | 64.4258
|  |  | 27957.5734 | 184 | 0.0065814