## General guidance
LONDON BOROUGH PLANNING DEVELOPMENT CONTROL
"be Seen" development energy demand and
| renewable/low carbon energy monitoring | GO TO CALCULATOR
General guidance
The Council and the GLA require all major (and usually minor) developments to undertake post-construction monitoring of energy loads and renewable/low-carbon energy equipment to demonstrate full compliance with the Mayor’s energy planning policy SI2 "be Seen" and the Council's relevant DPD policies. |  | Complete Platform/Officer time and Equipment tabs
Version 5.2 (2024)
Equipment + Data
To assist developers in this the Council has commissioned, or approved, a web-based solution in the form of an Automated Energy Monitoring Platform (AEMP). This AEMP is provided by Energence Ltd. |  | Info links
Platform & support fees
The monitoring normally involves installing GPRS smart meters that record kWh readings from PV, heat pumps, CHP, etc. These kWh readings are transmitted to the AEMP and displayed on a web-dashboard. The platform provides a remote monitoring solution for developers (as well as the Council and GLA) that enables them to track the performance of energy loads and the renewable/low-carbon systems. |  | Monitoring requirements
Data acquisition and processing
EMP Dashboard
Cost schedule
Some Councils require the developer to pay a S106 contribution that covers the cost of:
a) the AEMP and officer/consultant time spent analysing and validating application energy strategies, and
b) the monitoring equipment (PV smart meters, heat pump heat meters, data telemetry SIM cards, etc) |  | Energy Monitoring Platform ®
Part a) of the S106 contribution is payable on completion of the Legal Agreement, and Part b) on commencement of construction (excluding ground works) or on installation of the equipment. |  | www.energymonitoringplatform.co.uk
Alternatively, the Developer can pay the monitoring fees direct to Energence Ltd. |  | Powered by Energence
For transparency, all fees and equipment costs are itemised in this spreadsheet as part of the planning application process.systems. Energence will fill in the spreadsheet and forward it to the Applicant. |  | www.energence.co.uk
If applicants wish to source their own monitoring equipment then they only need to pay the basic AEMP and officer time fee. Please note that the monitoring equipment and data processing must meet Ealing Council's technical and administrative requirements and must be compatible with the AEMP. |  | © Energence Ltd Verified by
info@energence.co.uk
The monitoring equipment requirements and costs in the spreadsheet are based on the available information about the proposed renewable/low-carbon energy equipment. Please note that some equipment and consultancy services may be subject to inflation and price increases. |  | 01865 423678

## Platform + officer support
"be Seen" energy load and renewable/low-carbon energy monitoring compliance
Monitoring fees | Net | VAT | Total | Case officer(s) |  | Christopher Brady
Monitoring fees (basic + officer time) | 1860 | 372 | 2232 | Development |  | Land at Yiewsley Library, Falling Lane
Equipment + data costs | 17695 | 3539 | 21234 | Application |  | 76795/APP/2023/2503 |  | Validated | 2023-09-14 | Development Control
Monitoring fees + equipment / data | 19555 | 3911 | 23466 | Application (rev) |  |  |  | Decission | 2024-09-03 | General guidance
|  |  |  | Address 1 |  | Falling Lane |  |  |  | Energence ID
BASIC AEMP PLATFORM FEES | units or m2 | Net |  | Address 2 |  | Yiewsley |  |  | Planning ID |  | LBH-01
More than 10 Residential units | 50 | 700 |  | City / County |  | Middlesex | Post code | UB7 7BE |  | Active ID
Non-residential development - select |  | 0 |  | Energy Strategy |  | FutureServe |  | 2023-08-01 | v1 | Approved
| Basic Platform fee | 700 |  | Additional info |  | FAO: Mark Finch (Technical Director, Bugler)
| More info |  |  | Notes
Ealing/Energence officer support | p/hour | hours | Net |  |  | Installed technologies | kW(p) size | installs | kW(p) total
Monitoring implimentation follow-up | 75 | 8 | 600 |  | PV array (multi-phase meter) |  | 20 | 1 | 20
Data acquisition, configuration, and analysis | 70 | 8 | 560 |  | Photovoltaic (PV) - select |  |  |  | 0
Select | 0 |  | 0 |  | Photovoltaic (PV) - select |  |  |  | 0
Select | 0 |  | 0 |  | Photovoltaic (PV) - select |  |  |  | 0
Select | 0 |  | 0 |  | Photovoltaic (PV) - select |  |  |  | 0
Contingency (equipment and/or officer time) | 0 | [5 empty] | Total (PV systems) | 1 | 20
|  | Ealing/Energence support fees | 1160
Cost schedule |  |  |  |  | Air Source Heat Pump (air-to-water) |  | 200 | 1 | 200
[5 empty] | Heat pump(s) - select |  |  |  | 0
[5 empty] | Heat pump(s) - select |  |  |  | 0
[7 empty] | Total (heat pump) | 1 | 200
[5 empty] | ASHP MT (55/40) loop |  |  | 1
[5 empty] | Heat Network (site-wide) |  |  | Gas back-up boilers - select
[5 empty] | HIU (Heating & DHW) |  |  | Underfloor / panel mix
[5 empty] | CHP ? - select |  |  | kWe / kW/th

## Equipment + Data
Monitoring fees |  | Application |  |  | 76795/APP/2023/2503 |  |  |  | General guidance
Back to main Platform tab |  |  | Development |  | Land at Yiewsley Library, Falling Lane | 0 | 0 | 0 | 0 | Full cost schedule
Equipment + Data | 17695 |  |  | Planning ID | LBH-01 |  |  |  | Monitoring requirements
|  |  |  | Active ID | 0 |  |  |  | Telemetry info
| p/unit | units |  | Net | SIM cards and data processing |  | x units
Dwelling electric load smart meter | 130 | 50 |  | 6500 | Daily readings £28 p/yr (x5 yrs) |  | 7000
ASHP (heat meter) data-logger (M-Bus) | 455 | 1 |  | 455 | Daily readings £28 p/yr (x5 yrs) |  | 140
ASHP (parasitic load) smart meter (3-phase) | 225 | 4 |  | 900 | Daily readings £28 p/yr (x5 yrs) |  | 560
PV 3-phase smart meter (GPRS) | 225 | 1 |  | 225 | Daily readings £28 p/yr (x5 yrs) |  | 140
Smart meters / loggers - select | 0 |  |  | 0 | Select |  | 0
Domestic heat pump load meter - select | 0 |  |  | 0 | Data telemetry costs |  | 7840 |  | 56 | SIM card total
| Sub total | 56 |  | 8080 |  |  | Net |  | points
Heat meter (flow 25m3p/hr) 65mm diam | 1160 | 1 |  | 1160 | Equipment metering points: £10 p/point |  | 570 |  | 57
Heat meters - select | 0 |  |  | 0
| Sub total | 1 |  | 1160 | Data and meter point total |  | 8410
Delivery charge (per despatch) | 15 | 3 |  | 45 | Equipment and SIM cards are quoted at the current retail price - and for equipment and data processing currently available.
| Equipment total | 57 |  | 9285 | Meters should be installed at the same time as the renewable/CHP systems. This is done by the developer's contractor and not by Energence.

## Platform & support fees
Automatic Energy Monitoring Platform (AEMP) S106 (or direct) fees
Basic fees methodology
10 (or fewer) residential units
£50 per residential unit
Over 10 residential units
£500 + £5 per additional unit (over 10)
1,000 m2 (or less) Non-residential development
£0.50 per m2
More than 1,000 m2 Non-residential development
£500 + £0.05 per additional m2 (over 1,000)
Energence will respond to key issues about energy equipment monitoring and how the monitoring platform operates. Additional detailed advice and project management is chargable. A situation where this could be relevant is if Energence was asked to research the monitoring of a specific configuration of technologies, or if SIM cards have been installed incorrectly and remedial work is needed to rectify the situation.
Any additional project management or installation costs may be added to the spreadsheet or be in the form of a direct contract between Energence and the developer.
Additional time spent by Energence staff is charged at £70 p/hour and/or £80 p/hour for site visits (4 hours minimum).
Platform + officer support
General guidance

## Monitoring requirements
Key monitoring requirements
PV, heat pumps, and CHP must be monitoring using MID certified meters.
The kWh data must be automatically transmitted to the AEMP every day.
The Council and the GLA require the renewable/CHP to be monitored for a full five years from the point that the building is occupied and the systems are fully opperational. Particular attantion to this is needed with phased developments.
The energy planning policy is assessed in terms of CO2 reduction. Therefore, the parasitic electric load for heat pumps needs to be monitored as well as the energy generation. The parasitic kWh load is deducted from the kWh generation to determine the kWh and CO2 reduction.
Energence will offer general advice on the monitoring of renewable/low-carbon (or other) systems, however, they accept no liability for technical installation decisions made by the developer or their associates.
Platform + officer support
Equipment + Data
General guidance
PV monitoring
14.37 kWh
MID certified heat meter (eg. Sontex 440) with kWh integrator (M-Bus comms)
Heat pump monitoring
Single collector
Heat pump parasitic load
Smart meter (usually 3-phase)
(either Direct Connect or with CT clamps)
Elvaco (M-Bus) GPRS logger
Switchless electric supplies
Flow temp sensor
Return temp sensor
Flow rate sensor
M-Bus data lead
Heat meter integrator unit
CHP monitoring
CHP electric generation CT clamp 3-phase meter
Switchless electric supply
Elvaco (M-Bus) GPRS logger
L1
L3
L2
Gas meter (with M-Bus converter unit)
Smaller CHPs may be able to use a Direct Connect meter
District Heat Network (DHN) monitoring
Heat (and heat pump parasitic load) meter data upload via GPRS data-logger
Dwelling heat meter (6)
(post dwelling HIUs)
Heat meter (4)
Post block plate exchanger
(if not HIU direct feed)
Heat meter (5)
Post block gas boiler (if installed)
Block 3
Block 2
Block 4
Block 1
Heat meter (3)
Main network loop
Heat meter (1)
ASHP(s)
Main energy centre
M-Bus 1
M-Bus 2
M-Bus 3
Heat meter (2)
Main gas boiler(s)
All parasitic loads must be monitored – either individually or through a single supply meter

## Data acquisition & processing
| Back to general guidance | Automated alerts
| SIM cards and data acquisition | For the Council and GLA to confirm that the renewable/CHP systems are operating correctly, alert emails are automatically triggered if the systems stop sending data or if the performance drops noticeably.
Smart meter should use roaming SIM cards on the 2/3G network
kWh data must be uploaded to the Automated Energy Monitoring Platform (AEMP) every 24 hours via an ftp protocol.
The alerts are configured to trigger if there has been no data, or a performance fall, for a set level for a certain number of days.
Plug-and-play smart meters supplied by Energence are pre-loaded with SIM cards already configured to the AEMP.
The alerts are sent to Council officers and also to the Developer's consultants and/or maintenance company. Additional alert reciepients can be added. If an alert is triggered then Ealing may then inform the Developer that they not in compliance with the energy planning policy.
For performance/efficiency analysis large PV arrays, heat pumps, and CHP require half-hourly kWh data granularity.
Data processing
The kWh data is processed by the AEMP in the form of CSV files. CSV files look like Excel spreadsheets.
If the developer is using their own smart meters and data processing then the CSV data files must be configured to the AEMP. If Energence has to configure the AEMP database to process the CSV files then it is likely they will charge the developer a fee for this.
"Cloud" alternative data management option
Rather than developers automatically sending the CSV files to Energence it should be possible for them to deposit the data each night in a web-cloud (eg. Google or Amazon). Ealing/Energence should be able to automatically pull down the data from the "cloud".
The (Automated) Energy Monitoring Platform holds the renewable/low-carbon energy equipment kWh and performance data in a database. This data can be downloaded, analysed and projected in a range of graphs.
CALC. Platform & officer support
CALC. Equipment + Data
EMP Dashboard

## EMP Dashboard
Key Energy Monitoring Platform dashboard displays | Back to general guidance
Multiple properties developments are grouped together into Master projects. | Platform + officer support
Click on a row to select a specific sub-site (individual property PV etc). | Equipment + Data
Select technology for graphs and data analysis
Performance data for analysis and fault finding

## Cost schedule & DDs
COST SCHEDULE |  | Back to general guidance |  | Renewable/CHP technologies
Basic Platform fees |  |  |  |  | Equipment |  | Data acquisition
Residential development - select | p/unit | 10+ residential unit calculator cell | 40 | Photovoltaic (PV) - select | Smart meters / loggers - select |  | Select | p/yr
Less than 10 residential units | 50 | Residential development - select |  | PV array (single-phase meter) | PV single phase smart meter (GPRS) | 130 | Daily readings £28 p/yr (x5 yrs) | 28 | 140 | 140
Additional residential units (above 10) | 5 | 10 (or less) Residential units | 2500 | PV array (multi-phase meter) | PV 3-phase smart meter (GPRS) | 225 | Half-hour readings £34 p/yr (x5 yrs) | 34 | 170 | 170
|  | More than 10 Residential units | 700 |  | ASHP (heat meter) data-logger (M-Bus) | 455
Non-residential development - select | p/m2 |  |  | Heat Network configuration - select | ASHP (parasitic load) smart meter (3-phase) | 225
Less than 1,000 m2 non-residential | 0.5 | 1,000+ m2 calculator cell | -1000 | ASHP HT (75/55) loop | ASHP (parasitic) smart meter (single-phase) | 130
Additional non-residential m2 (above 1,000 m2) | 0.05 | Non-residential development - select |  | ASHP MT (55/40) loop | Dwelling WSHP pump logger (muti-channel) | 455
|  | 1,000 m2 (or less) Non-residential | 0 | ASHP LT (45/30) loop | Dwelling WSHP (parasitic) smart meter | 130
Basic fees methodology |  | More than 1,000 m2 Non-residential | 450 | ASHP LT (ambient 30/20) loop | Dwelling electric load smart meter | 130
10 (or fewer) residential units |  |  |  | Electric HT buffer tank (40>65) loop | EASHP (air-to-air system) monitoring | 3250
£60 per residential unit |  | Energence support time (per/hour) |  | Electric LT buffer tank (15>40) loop | GSHP (heat meter) data-logger (M-Bus) | 455
Over 10 residential units |  | Select |  |  | Heat Network heat meter data-logger (M-Bus) | 455
£600 + £6 per additional unit (over 10) |  | Energy Strategy assessment + DC liaison | 70 | Heat pump(s) - select
1,000 m2 (or less) non-residential development |  | Revisions and Condition discharging | 70 | Air Source Heat Pump (air-to-water)
£0.60 per m2 |  | Data acquisition, configuration, and analysis | 70 | Secondary Water Source Heat Pump
More than 1,000 m2 non-residential development |  | Monitoring implimentation follow-up | 75 | Dwelling Water Source Heat Pump | Domestic heat pump load meter - select
£600 + £0.06 per additional m2 (over 1,000) |  | Site visit (min 4 hrs) - includes multiple sites | 80 | Dwelling Air Source Heat Pump | Domestic heat pump load meter (M-Bus) | 110
|  | Contingency - select |  | Air Source Heat Pump (VFR)
Platform + officer support |  | Contingency (equipment and/or officer time) |  | Air Source Heat Pump (air-to-air) | Heat meters - select
Equipment + Data |  |  |  | Air Source Heat Pump (exhaust) | Domestic heat pump heat meter (15mm) | 405
|  | Validated / Decision ? |  | Ground Source Heat Pump | Heat meter (flow 1m3p/hr) 15mm diam | 475
|  | Validated |  |  | Heat meter (flow 1.5m3p/hr) 15mm diam | 475
|  | Decision |  | CHP ? - select | Heat meter (flow 1m3p/hr) 20mm diam | 478
|  |  |  | CHP (grid gas) | Heat meter (flow 1.5m3p/hr) 20mm diam | 478
|  |  |  | CHP (biofuel) | Heat meter (flow 2.5m3p/hr) 20mm diam | 478
[5 empty] | Heat meter (flow 3.5m3p/hr) 25mm diam | 550
|  |  |  | Gas back-up boilers - select | Heat meter (flow 6m3p/hr) 25mm diam | 604
|  |  |  | Yes - gas back-up boilers used | Heat meter (flow 10m3p/hr) 40mm diam | 794
|  |  |  | No gas back-up boilers | Heat meter (flow 15m3p/hr) 50mm diam | 912
[5 empty] | Heat meter (flow 25m3p/hr) 65mm diam | 1160
|  |  |  | Network reach - select | Heat meter (flow 40m3p/hr) 80mm diam | 1431
|  |  |  | Heat Network (site-wide) | Heat meter (flow 60m3p/hr) 100mm diam | 1670
|  |  |  | District Heat Network (external) | Heat meter (flow 100m3p/hr) 125mm diam | 2967
|  |  |  | Heat transfer / DHW - select | Gas meters (inc M-Bus converter)
|  |  |  | HIU (Heating & DHW) | Gas meter (domestic 20mm diam) | 150
|  |  |  | HIU (DHW supply only) | Gas meter (25-150mm diam) | 975
|  |  |  | HIU (with dwelling WSHP) | Gas meter (50-150mm diam) | 1120
HIU (with dwelling ASHP)
|  |  |  | HIU (with immersion tank) | Delivery charge - select
|  |  |  | HIU (with direct electric DHW) | Delivery charge (per despatch) | 15
HIU (with hydro-boxes)
|  |  |  | Internal heating infrastructure ? | Total metering points (£10 p/point) | 10
Underfloor
Oversized panel radiators
|  |  |  | Underfloor / panel mix | Energence installation service (smart meters) | 520
|  |  |  | Conventional panel radiators | One off installation fee (type in) | ???
Air Handling Units / Fan Coil
AHU / panel mix