## Cover
Damage Costs Appraisal Toolkit
Original Version: January 2019
Last Updated: March 2021
Queries and comments on this toolkit should be referred to:
Department for Environment Food & Rural Affairs
Ground Floor
Seacole Building
2 Marsham Street
London
SW1P 4DF
Produced by:
Naval Narkar
Christian Mortlock
Email: | igcb@defra.gov.uk

## LBH Calculations
GEN SETS OPERATION SCHEDULE |  |  |  |  | NON ABATED | ABATED
Generator Testing Schedule | Load Profile | Individual Test Duration (min) | Frequency | Total time (hours)
Off load testing | 10% | 20 mins | 12 | 4 h (12*20 min) | 4 h (12*20 min) | 0
Mains failure test (initial period - maximum load) | 100% | 20 mins | 2 | 0.666667 h (2*20 min) | 0.666667 h (2*20 min) | 0
Mains failure test (stable period - normal load) | 75% | 40 mins | 2 | 1.333333 h (2*40 min) | 0 | 1.333333 h (2*40 min)
Generator Maintenance Schedule
Maintenance (minor) | 50% | 30 mins | 22 | 11 h | 7.333333 h (22*20 min) | 3.666667 h (22*10 min)
Maintenance (major) | 50% | 120 mins | 5 | 10 h | 1.666667 h (5*20 min) | 8.333333 h (5*100 min)
Emergency Backup
Estimated emergency operation (initial period – maximum load) | 100% | 20 mins | 1 | 0.333333 h | 0.333333 h | 0
Estimated emergency operation (subsequent stable operation) | 75% | 100 mins | 1 | 1.666667 h | 0 | 1.666667 h
TOTAL OPERATION TIME |  |  |  | 29 | 14 | 15
Virtus Emissions Calculation | Emission rates (g/h)
Loading % | NOx (g/hr) RAW | NOx (g/hr) SCR | PM2.5 (g/hr)
10% | 5238 | 5238 | 18
100% | 13600 | 1904 | 190.9
75% | 8583 | 1201.62 | 176.9
50% | 7213 | 1009.82 | 146.8
ANNUAL TOTAL EMISSIONS PER POLLUTANT
ABATED OPERATION
NOx | 15722.7 |  | g.Nox/h per gen (abated)
4 units | 62890.8 |  | g.Nox/h all generators (abated)
tonnes | 0.062891 |  | tonnes Nox/ hour (abated 86%) all generators
NOx
0.062891 | tonnes/year |  | tonnes of Nox per year
NON ABATED OPERATION
NOx | 99468.9955 |  | g.Nox/h per gen (unabated)
4 units | 397875.982 |  | g.Nox/h all generators (unabated)
tonnes | 0.39788 |  | tonnes Nox/ hour (unabated ) all generators
0.39788 | tonnes/year |  | tonnes of NOx (unabated) per year
TOTAL NOx emissions | 0.46077
PM2.5 | 3876.4001 |  | g.PM/ per generator
4 units | 15505.6003 |  | g.PM/ all generators
tonnes | 0.015506 |  | tonnes PM
0.015506 | tonnes/year |  | Total PM per year (diesel emissions)
Total PM2.5 emissions |  |  | 0.015506
All PM |  |  | 0.015506
emissions have been assumed to be PM2.5
Note on I19: Roberts, Barry: 10% load data from CAT datasheet
Note on J19: Roberts, Barry: No reduction in NOx emissions considered due to SCR, as likely below operating temp
Note on I20: Roberts, Barry: 100% load data from CAT datasheet
Note on I21: Roberts, Barry: 75% load data from CAT datasheet
Note on I22: Froggatt, Patrick: 50% load data from CAT datasheet
Note on K22: Froggatt, Patrick: 50% load data from CAT datasheet

## Guidance
This toolkit allows appraisers to calculate the economic impact of policies which affect air quality, using the damage cost approach.
This tool is designed to be used in conjunction with the Air Quality Damage Costs Guidance: |  | https://www.gov.uk/government/publications/assess-the-impact-of-air-quality
It is only appropriate for small air quality impacts (below £50 million).
Proposals with impacts over £50 million should be assessed using the impact pathway approach. In these cases Defra should be contacted for advice.
Proposals that affect compliance should use the damage cost (small air quality impacts) or the impact pathway approach (large air quality impacts) and ensure any breech of legal limits is mitigated against within the scheme design
The tool calculates a central present value along with high and low sensitivity values for up to 5 pollutants (NOx, SO2, PM2.5, VOC and NH3).
All adjustments are automated in this tool - no extra calculations are necessary unless PM is being used - in which case please use the conversion factors provided in the Assumptions sheet
The appraisal is calculated with the following steps:
1) Complete the input boxes (Start Year, End Year, Price Base Year and Number of Pollutants) in the Control Panel tab
2) Select the pollutants to be assessed in the Damage Costs User Interface tab and then fill in the change in emissions expected for each appraisal year
3) View outputs in Outputs tab
Cell Type Key:
For user input
Automated values
Automated output
Does proposal affect compliance with legal air pollution limits?
Is air quality impact found using tool greater than £50 million?
Use detailed impact pathway approach with consideration for mitigation measures to avoid breaching legal limits
Use damage costs with consideration for mitigation measures to avoid breaching legal limits
Is air quality impact found using tool greater than £50 million?
Use the impact pathway approach
Use damage cost approach
N
Y
Y
N
Y
N

## Control_Panel
Control Panel
Start Year | 2022 | Please type the year at which the policy will start from, the start year is also the discount year
End Year | 2051 | Please type the year at which the appraisal will end
Appraisal Period | 30 | Autofills the number of years for which the policy is reviewed for
Price Base Year | 2022 | Please type the price base year for your appraisal
Number of pollutants | 2 | Please type the number of pollutants to be assessed
Note: if you are assessing PM10 impacts, please convert these to PM2.5 using conversion factors found in the Assumptions sheet
Key assumptions: | Discount rate | 3.5% from appraisal year 0 to 30
3% from appraisal year 31 to 75
2.5% from appraisal year 76 to 125
| Health uplift factor | 2%

## Damage_Costs_User_Interface
Damage Cost User Interface
| Pollutant | NOx | Part A Category 3 |  |  |  | Pollutant |  | PM2.5 | Part A Category 3
Note: If you are assessing PM10 impacts, please convert these to PM2.5 using conversion factors found in the Assumptions sheet
NOx Part A Category 3
|  | Year | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051
| Reduction in emissions (tonnes) |  | 0.46077 | 0.46077 | 0.46077 | 0.46077 | 0.46077 | 0.46077 | 0.46077 | 0.46077 | 0.46077 | 0.46077 | 0.46077 | 0.46077 | 0.46077 | 0.46077 | 0.46077 | 0.46077 | 0.46077 | 0.46077 | 0.46077 | 0.46077 | 0.46077 | 0.46077 | 0.46077 | 0.46077 | 0.46077 | 0.46077 | 0.46077 | 0.46077 | 0.46077 | 0.46077
| Central Damage Costs (£) |  | 6843.5054 | 6980.3755 | 7119.983 | 7262.3827 | 7407.6303 | 7555.7829 | 7706.8986 | 7861.0365 | 8018.2573 | 8178.6224 | 8342.1949 | 8509.0388 | 8679.2195 | 8852.8039 | 9029.86 | 9210.4572 | 9394.6664 | 9582.5597 | 9774.2109 | 9969.6951 | 10169.089 | 10372.4708 | 10579.9202 | 10791.5186 | 11007.349 | 11227.4959 | 11452.0459 | 11681.0868 | 11914.7085 | 12153.0027
| Central Benefit (£) |  | 3153.26 | 3216.3251 | 3280.6517 | 3346.2647 | 3413.19 | 3481.4538 | 3551.0829 | 3622.1045 | 3694.5466 | 3768.4375 | 3843.8063 | 3920.6824 | 3999.0961 | 4079.078 | 4160.6595 | 4243.8727 | 4328.7502 | 4415.3252 | 4503.6317 | 4593.7043 | 4685.5784 | 4779.29 | 4874.8758 | 4972.3733 | 5071.8208 | 5173.2572 | 5276.7223 | 5382.2568 | 5489.9019 | 5599.6999
| Discounted Central Benefit (£) |  | 3153.26 | 3107.5605 | 3062.5234 | 3018.139 | 2974.3979 | 2931.2907 | 2888.8082 | 2846.9414 | 2805.6814 | 2765.0193 | 2724.9466 | 2685.4546 | 2646.535 | 2608.1794 | 2570.3797 | 2533.1278 | 2496.4158 | 2460.2359 | 2424.5803 | 2389.4414 | 2354.8119 | 2320.6842 | 2287.051 | 2253.9054 | 2221.2401 | 2189.0482 | 2157.3229 | 2126.0573 | 2095.2449 | 2064.879
| Central Present Value |  | 77163.1631
| Low Sensitivity Damage Costs (£) |  | 672.1951 | 685.639 | 699.3518 | 713.3388 | 727.6056 | 742.1577 | 757.0009 | 772.1409 | 787.5837 | 803.3354 | 819.4021 | 835.7901 | 852.5059 | 869.5561 | 886.9472 | 904.6861 | 922.7798 | 941.2354 | 960.0601 | 979.2613 | 998.8466 | 1018.8235 | 1039.2 | 1059.984 | 1081.1837 | 1102.8073 | 1124.8635 | 1147.3607 | 1170.308 | 1193.7141
| Low Sensitivity Benefit (£) |  | 309.7252 | 315.9197 | 322.2381 | 328.6828 | 335.2565 | 341.9616 | 348.8009 | 355.7769 | 362.8924 | 370.1503 | 377.5533 | 385.1043 | 392.8064 | 400.6625 | 408.6758 | 416.8493 | 425.1863 | 433.69 | 442.3638 | 451.2111 | 460.2353 | 469.44 | 478.8288 | 488.4054 | 498.1735 | 508.137 | 518.2997 | 528.6657 | 539.239 | 550.0238
| Discounted Low Sensitivity Benefit (£) |  | 309.7252 | 305.2364 | 300.8127 | 296.4531 | 292.1567 | 287.9225 | 283.7497 | 279.6374 | 275.5847 | 271.5907 | 267.6546 | 263.7756 | 259.9527 | 256.1853 | 252.4725 | 248.8134 | 245.2075 | 241.6537 | 238.1515 | 234.7 | 231.2986 | 227.9464 | 224.6428 | 221.3872 | 218.1786 | 215.0166 | 211.9005 | 208.8294 | 205.8029 | 202.8203
| Low Sensitivity Present Value |  | 7579.2592
| High Sensitivity Damage Costs (£) |  | 25764.643 | 26279.9358 | 26805.5346 | 27341.6452 | 27888.4782 | 28446.2477 | 29015.1727 | 29595.4761 | 30187.3856 | 30791.1334 | 31406.956 | 32035.0951 | 32675.797 | 33329.313 | 33995.8992 | 34675.8172 | 35369.3336 | 36076.7202 | 36798.2547 | 37534.2197 | 38284.9041 | 39050.6022 | 39831.6143 | 40628.2466 | 41440.8115 | 42269.6277 | 43115.0203 | 43977.3207 | 44856.8671 | 45754.0044
| High Sensitivity Benefit (£) |  | 11871.4916 | 12108.9215 | 12351.0999 | 12598.1219 | 12850.0843 | 13107.086 | 13369.2277 | 13636.6123 | 13909.3445 | 14187.5314 | 14471.2821 | 14760.7077 | 15055.9219 | 15357.0403 | 15664.1811 | 15977.4647 | 16297.014 | 16622.9543 | 16955.4134 | 17294.5216 | 17640.4121 | 17993.2203 | 18353.0847 | 18720.1464 | 19094.5494 | 19476.4403 | 19865.9691 | 20263.2885 | 20668.5543 | 21081.9254
| Discounted High Sensitivity Benefit (£) |  | 11871.4916 | 11699.441 | 11529.8839 | 11362.7841 | 11198.1061 | 11035.8147 | 10875.8754 | 10718.254 | 10562.917 | 10409.8312 | 10258.9641 | 10110.2835 | 9963.7576 | 9819.3553 | 9677.0458 | 9536.7988 | 9398.5843 | 9262.373 | 9128.1357 | 8995.8438 | 8865.4693 | 8736.9842 | 8610.3613 | 8485.5734 | 8362.5941 | 8241.3971 | 8121.9566 | 8004.247 | 7888.2435 | 7773.9211
| High Sensitivity Present Value |  | 290506.2888
PM2.5 Part A Category 3
|  | Year | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051
| Reduction in emissions (tonnes) |  | 0.015506 | 0.015506 | 0.015506 | 0.015506 | 0.015506 | 0.015506 | 0.015506 | 0.015506 | 0.015506 | 0.015506 | 0.015506 | 0.015506 | 0.015506 | 0.015506 | 0.015506 | 0.015506 | 0.015506 | 0.015506 | 0.015506 | 0.015506 | 0.015506 | 0.015506 | 0.015506 | 0.015506 | 0.015506 | 0.015506 | 0.015506 | 0.015506 | 0.015506 | 0.015506
| Central Damage Costs (£) |  | 108619.6797 | 110792.0733 | 113007.9148 | 115268.0731 | 117573.4346 | 119924.9033 | 122323.4013 | 124769.8693 | 127265.2667 | 129810.5721 | 132406.7835 | 135054.9192 | 137756.0176 | 140511.1379 | 143321.3607 | 146187.7879 | 149111.5436 | 152093.7745 | 155135.65 | 158238.363 | 161403.1303 | 164631.1929 | 167923.8167 | 171282.2931 | 174707.9389 | 178202.0977 | 181766.1397 | 185401.4625 | 189109.4917 | 192891.6815
| Central Benefit (£) |  | 1684.2133 | 1717.8976 | 1752.2556 | 1787.3007 | 1823.0467 | 1859.5076 | 1896.6978 | 1934.6317 | 1973.3244 | 2012.7908 | 2053.0467 | 2094.1076 | 2135.9897 | 2178.7095 | 2222.2837 | 2266.7294 | 2312.064 | 2358.3053 | 2405.4714 | 2453.5808 | 2502.6524 | 2552.7055 | 2603.7596 | 2655.8348 | 2708.9515 | 2763.1305 | 2818.3931 | 2874.761 | 2932.2562 | 2990.9013
| Discounted Central Benefit (£) |  | 1684.2133 | 1659.8044 | 1635.7493 | 1612.0428 | 1588.6799 | 1565.6555 | 1542.9649 | 1520.603 | 1498.5653 | 1476.847 | 1455.4434 | 1434.35 | 1413.5623 | 1393.0759 | 1372.8864 | 1352.9895 | 1333.381 | 1314.0566 | 1295.0123 | 1276.244 | 1257.7477 | 1239.5195 | 1221.5554 | 1203.8517 | 1186.4046 | 1169.2103 | 1152.2653 | 1135.5658 | 1119.1083 | 1102.8893
| Central Present Value |  | 41214.245
| Low Sensitivity Damage Costs (£) |  | 23074.647 | 23536.1399 | 24006.8627 | 24487 | 24976.74 | 25476.2748 | 25985.8003 | 26505.5163 | 27035.6266 | 27576.3391 | 28127.8659 | 28690.4232 | 29264.2317 | 29849.5163 | 30446.5067 | 31055.4368 | 31676.5455 | 32310.0765 | 32956.278 | 33615.4035 | 34287.7116 | 34973.4658 | 35672.9352 | 36386.3939 | 37114.1217 | 37856.4042 | 38613.5323 | 39385.8029 | 40173.519 | 40976.9893
| Low Sensitivity Benefit (£) |  | 357.7863 | 364.942 | 372.2408 | 379.6856 | 387.2793 | 395.0249 | 402.9254 | 410.9839 | 419.2036 | 427.5877 | 436.1394 | 444.8622 | 453.7595 | 462.8347 | 472.0914 | 481.5332 | 491.1639 | 500.9871 | 511.0069 | 521.227 | 531.6516 | 542.2846 | 553.1303 | 564.1929 | 575.4767 | 586.9863 | 598.726 | 610.7005 | 622.9145 | 635.3728
| Discounted Low Sensitivity Benefit (£) |  | 357.7863 | 352.6009 | 347.4908 | 342.4547 | 337.4916 | 332.6004 | 327.7801 | 323.0297 | 318.3481 | 313.7343 | 309.1875 | 304.7065 | 300.2904 | 295.9384 | 291.6494 | 287.4226 | 283.2571 | 279.1519 | 275.1062 | 271.1192 | 267.1899 | 263.3176 | 259.5014 | 255.7405 | 252.0341 | 248.3815 | 244.7817 | 241.2342 | 237.738 | 234.2926
| Low Sensitivity Present Value |  | 8755.3578
| High Sensitivity Damage Costs (£) |  | 319380.1967 | 325767.8006 | 332283.1566 | 338928.8198 | 345707.3961 | 352621.5441 | 359673.9749 | 366867.4544 | 374204.8035 | 381688.8996 | 389322.6776 | 397109.1312 | 405051.3138 | 413152.3401 | 421415.3869 | 429843.6946 | 438440.5685 | 447209.3799 | 456153.5674 | 465276.6388 | 474582.1716 | 484073.815 | 493755.2913 | 503630.3971 | 513703.0051 | 523977.0652 | 534456.6065 | 545145.7386 | 556048.6534 | 567169.6264
| High Sensitivity Benefit (£) |  | 4952.1817 | 5051.2253 | 5152.2498 | 5255.2948 | 5360.4007 | 5467.6087 | 5576.9609 | 5688.5001 | 5802.2701 | 5918.3155 | 6036.6818 | 6157.4154 | 6280.5638 | 6406.175 | 6534.2985 | 6664.9845 | 6798.2842 | 6934.2499 | 7072.9349 | 7214.3936 | 7358.6814 | 7505.8551 | 7655.9722 | 7809.0916 | 7965.2734 | 8124.5789 | 8287.0705 | 8452.8119 | 8621.8681 | 8794.3055
| Discounted High Sensitivity Benefit (£) |  | 4952.1817 | 4880.4109 | 4809.6803 | 4739.9748 | 4671.2795 | 4603.5798 | 4536.8613 | 4471.1097 | 4406.311 | 4342.4514 | 4279.5173 | 4217.4953 | 4156.3722 | 4096.1349 | 4036.7706 | 3978.2667 | 3920.6107 | 3863.7902 | 3807.7933 | 3752.6079 | 3698.2222 | 3644.6248 | 3591.8042 | 3539.749 | 3488.4483 | 3437.8911 | 3388.0666 | 3338.9642 | 3290.5734 | 3242.8839
| High Sensitivity Present Value |  | 121184.4273
|  | Year | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051
| Reduction in emissions (tonnes) |  | 3 | 4 | 5 | 6 | 7 | 4 | 5 | 6 | 7 | 6
Central Damage Costs (£)
Central Benefit (£)
Discounted Central Benefit (£)
| Central Present Value |  | 3: 0
Low Sensitivity Damage Costs (£)
Low Sensitivity Benefit (£)
Discounted Low Sensitivity Benefit (£)
| Low Sensitivity Present Value |  | 3: 0
High Sensitivity Damage Costs (£)
High Sensitivity Benefit (£)
Discounted High Sensitivity Benefit (£)
| High Sensitivity Present Value |  | 3: 0
|  | Year | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051
| Reduction in emissions (tonnes) |  | 12 | 12 | 12 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Central Damage Costs (£)
Central Benefit (£)
Discounted Central Benefit (£)
| Central Present Value |  | 3: 0
Low Sensitivity Damage Costs (£)
Low Sensitivity Benefit (£)
Discounted Low Sensitivity Benefit (£)
| Low Sensitivity Present Value |  | 3: 0
High Sensitivity Damage Costs (£)
High Sensitivity Benefit (£)
Discounted High Sensitivity Benefit (£)
| High Sensitivity Present Value |  | 3: 0
|  | Year | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051
| Reduction in emissions (tonnes) |  | 14 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Central Damage Costs (£)
Central Benefit (£)
Discounted Central Benefit (£)
| Central Present Value |  | 3: 0
Low Sensitivity Damage Costs (£)
Low Sensitivity Benefit (£)
Discounted Low Sensitivity Benefit (£)
| Low Sensitivity Present Value |  | 3: 0
High Sensitivity Damage Costs (£)
High Sensitivity Benefit (£)
Discounted High Sensitivity Benefit (£)
| High Sensitivity Present Value |  | 3: 0

## Outputs
Outputs
| Pollutant | Low Sensitivity Present Value | Central Present Value | High Sensitivity Present Value
| NOx Part A Category 3 | 7579.2592 | 77163.1631 | 290506.2888
| PM2.5 Part A Category 3 | 8755.3578 | 41214.245 | 121184.4273
118377.4082
|  |  | 118377.4082 | 411690.7161

## Damage_Costs_and_Assumptions
Damage Costs & Assumptions
| Damage Cost Valuations (£/tonne, 2017 Prices) |  |  |  |  | PM2.5/PM10 Conversion Factors |  |  | Pollutants by Sector
| Number | Pollutant Sector | Low Scenario | Central Scenario | High Scenario |  |  |  | NOx |  | PM2.5 |  | SO2 |  | VOC |  | NH3
| 1 | NOx National | 611 | 6385 | 24174 | - |  |  | National |  | National |  | National |  | National |  | National
| 2 | NOx Industry (area) | 573 | 5891 | 22225 | - |  |  | Industry (area) |  | Industry (area)
| 3 | NOx Commercial | 1440 | 17171 | 66697 | - |  |  | Commercial |  | Commercial
| 4 | NOx Domestic | 1077 | 12448 | 48078 | - |  |  | Domestic |  | Domestic
| 5 | NOx Solvents | 1197 | 14099 | 54231 |  |  |  | Solvents |  | Solvents
| 6 | NOx Road Transport | 817 | 9066 | 34742 | - |  |  | Road Transport |  | Road Transport
| 7 | NOx Aircraft | 856 | 9575 | 36752 | - |  |  | Aircraft |  | Aircraft
| 8 | NOx Offroad | 667 | 7106 | 27017 | - |  |  | Offroad |  | Offroad
| 9 | NOx Rail | 694 | 7466 | 28437 | - |  |  | Rail |  | Rail
| 10 | NOx Ships | 309 | 2451 | 8664 | - |  |  | Ships |  | Ships
| 11 | NOx Waste | 663 | 7060 | 26837 | - |  |  | Waste |  | Waste
| 12 | NOx Agriculture | 305 | 2393 | 8436 |  |  |  | Agriculture |  | Agriculture
| 13 | NOx Other | 295 | 2267 | 7938 | - |  |  | Other |  | Other
| 14 | NOx Road Transport Central London | 4053 | 51178 | 200767 | - |  |  | Road Transport Central London |  | Road Transport Central London
| 15 | NOx Road Transport Inner London | 4161 | 52587 | 206323 | - |  |  | Road Transport Inner London |  | Road Transport Inner London
| 16 | NOx Road Transport Outer London | 2252 | 27741 | 108367 | - |  |  | Road Transport Outer London |  | Road Transport Outer London
| 17 | NOx Road Transport Inner Conurbation | 1574 | 18913 | 73565 | - |  |  | Road Transport Inner Conurbation |  | Road Transport Inner Conurbation
| 18 | NOx Road Transport Outer Conurbation | 979 | 11170 | 43037 | - |  |  | Road Transport Outer Conurbation |  | Road Transport Outer Conurbation
| 19 | NOx Road Transport Urban Big | 1007 | 11529 | 44455 | - |  |  | Road Transport Urban Big |  | Road Transport Urban Big
| 20 | NOx Road Transport Urban Large | 850 | 9493 | 36427 | - |  |  | Road Transport Urban Large |  | Road Transport Urban Large
| 21 | NOx Road Transport Urban Medium | 706 | 7614 | 29021 | - |  |  | Road Transport Urban Medium |  | Road Transport Urban Medium
| 22 | NOx Road Transport Urban Small | 601 | 6251 | 23646 | - |  |  | Road Transport Urban Small |  | Road Transport Urban Small
| 23 | NOx Road Transport Rural | 364 | 3166 | 11483 | - |  |  | Road Transport Rural |  | Road Transport Rural
| 24 | NOx Part A Category 1 | 237 | 1512 | 4963 | - |  |  | Part A Category 1 |  | Part A Category 1
| 25 | NOx Part A Category 2 | 316 | 2547 | 9045 | - |  |  | Part A Category 2 |  | Part A Category 2
| 26 | NOx Part A Category 3 | 553 | 5630 | 21196 | - |  |  | Part A Category 3 |  | Part A Category 3
| 27 | NOx Part A Category 4 | 227 | 1378 | 4435 | - |  |  | Part A Category 4 |  | Part A Category 4
| 28 | NOx Part A Category 5 | 252 | 1707 | 5732 | - |  |  | Part A Category 5 |  | Part A Category 5
| 29 | NOx Part A Category 6 | 310 | 2464 | 8715 | - |  |  | Part A Category 6 |  | Part A Category 6
| 30 | NOx Part A Category 7 | 222 | 1320 | 4205 | - |  |  | Part A Category 7 |  | Part A Category 7
| 31 | NOx Part A Category 8 | 232 | 1453 | 4730 | - |  |  | Part A Category 8 |  | Part A Category 8
| 32 | NOx Part A Category 9 | 247 | 1641 | 5473 | - |  |  | Part A Category 9 |  | Part A Category 9
-
| 31 | PM2.5 National | 15888 | 73403 | 227323 | 0.635
| 32 | PM2.5 Industry (area) | 16141 | 71455 | 257605 | 0.342
| 33 | PM2.5 Commercial | 16674 | 78458 | 226997 | 0.958
| 34 | PM2.5 Domestic | 18936 | 89456 | 258239 | 0.978
| 35 | PM2.5 Solvents | 3494 | 110070 | 343630 | 0.619
| 36 | PM2.5 Road Transport | 17567 | 81518 | 252695 | 0.635
| 37 | PM2.5 Aircraft | 15648 | 73070 | 216359 | 0.819
| 38 | PM2.5 Offroad | 12503 | 58367 | 167598 | 1
| 39 | PM2.5 Rail | 12373 | 57550 | 166998 | 0.926
| 40 | PM2.5 Ships | 5484 | 24255 | 69497 | 0.947
| 41 | PM2.5 Waste | 15799 | 74029 | 216443 | 0.889
| 42 | PM2.5 Agriculture | 7936 | 25141 | 109571 | 0.167
| 43 | PM2.5 Other | 19472 | 91826 | 268508 | 0.895
| 44 | PM2.5 Road Transport Central London | 83689 | 401540 | 1234992 | 0.681
| 45 | PM2.5 Road Transport Inner London | 85544 | 410293 | 1273099 | 0.651
| 46 | PM2.5 Road Transport Outer London | 46656 | 222205 | 690525 | 0.642
| 47 | PM2.5 Road Transport Inner Conurbation | 32693 | 154672 | 480614 | 0.639
| 48 | PM2.5 Road Transport Outer Conurbation | 20374 | 95108 | 294812 | 0.639
| 49 | PM2.5 Road Transport Urban Big | 21067 | 98465 | 305206 | 0.639
| 50 | PM2.5 Road Transport Urban Large | 17712 | 82253 | 254531 | 0.641
| 51 | PM2.5 Road Transport Urban Medium | 14512 | 66797 | 206169 | 0.644
| 52 | PM2.5 Road Transport Urban Small | 12231 | 55777 | 171775 | 0.645
| 53 | PM2.5 Road Transport Rural | 7048 | 30697 | 93795 | 0.642
| 54 | PM2.5 Part A Category 1 | 2634 | 10189 | 28879 | 0.848
| 55 | PM2.5 Part A Category 2 | 5816 | 25684 | 74386 | 0.881
| 56 | PM2.5 Part A Category 3 | 18983 | 89359 | 262747 | 0.862
| 57 | PM2.5 Part A Category 4 | 2216 | 7414 | 21189 | 0.657
| 58 | PM2.5 Part A Category 5 | 1896 | 6210 | 17293 | 0.733
| 59 | PM2.5 Part A Category 6 | 1990 | 7250 | 20040 | 0.912
| 60 | PM2.5 Part A Category 7 | 1553 | 4167 | 11118 | 0.649
| 61 | PM2.5 Part A Category 8 | 1277 | 3289 | 8423 | 0.752
| 62 | PM2.5 Part A Category 9 | 1502 | 3421 | 8749 | 0.565
| 63 | SO2 National | 2893 | 13026 | 37611 | -
| 64 | NH3 National | 1521 | 7923 | 24467 | -
| 65 | VOC National | 55.1627 | 101.943 | 205.1442 | -
Pollutant list
| 1 | NOx
| 2 | SO2
| 3 | PM2.5
| 4 | VOC
| 5 | NH3
|  | GDP Deflator |  | 1990 | 1991 | 1992 | 1993 | 1994 | 1995 | 1996 | 1997 | 1998 | 1999 | 2000 | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100
|  | 2010 = 100 |  | 62.925 | 67.0964 | 69.2055 | 71.0884 | 72.0447 | 73.7977 | 76.8359 | 77.6641 | 78.3942 | 79.1156 | 80.584 | 81.3858 | 83.103 | 84.9778 | 87.1459 | 89.3267 | 91.8045 | 94.174 | 96.9018 | 98.4912 | 100 | 102.0409 | 103.733 | 105.6978 | 107.632 | 108.2576 | 110.5717 | 112.6644 | 115.0709 | 117.2095 | 119.3663 | 121.6624 | 124.0383 | 126.5016 | 129.4111 | 132.3876 | 135.4325 | 138.5474 | 141.734 | 144.9939 | 148.3288 | 151.7403 | 155.2303 | 158.8006 | 162.4531 | 166.1895 | 170.0118 | 173.9221 | 177.9223 | 182.0145 | 186.2009 | 190.4835 | 194.8646 | 199.3465 | 203.9315 | 208.6219 | 213.4202 | 218.3288 | 223.3504 | 228.4875 | 233.7427 | 239.1188 | 244.6185 | 250.2447 | 256.0003 | 261.8884 | 267.9118 | 274.0738 | 280.3775 | 286.8261 | 293.4231 | 300.1719 | 307.0758 | 314.1386 | 321.3638 | 328.7551 | 336.3165 | 344.0518 | 351.965 | 360.0601 | 368.3415 | 376.8134 | 385.4801 | 394.3461 | 403.4161 | 412.6947 | 422.1866 | 431.8969 | 441.8306 | 451.9927 | 462.3885 | 473.0234 | 483.903 | 495.0327 | 506.4185 | 518.0661 | 529.9816 | 542.1712 | 554.6412 | 567.3979 | 580.4481 | 593.7984 | 607.4557 | 621.4272 | 635.72 | 650.3416 | 665.2995 | 680.6013 | 696.2552 | 712.269 | 728.6512
Source: | TAG Data Book, July 2020 v1.13.1
|  | Discount Factor | Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 103 | 104 | 105 | 106 | 107 | 108 | 109 | 110 | 111 | 112 | 113 | 114 | 115 | 116 | 117 | 118 | 119 | 120 | 121 | 122 | 123 | 124 | 125
|  |  | Discount Rate | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5%
|  |  |  | 1 | 0.96618 | 0.93351 | 0.90194 | 0.87144 | 0.84197 | 0.8135 | 0.78599 | 0.75941 | 0.73373 | 0.70892 | 0.68495 | 0.66178 | 0.6394 | 0.61778 | 0.59689 | 0.57671 | 0.5572 | 0.53836 | 0.52016 | 0.50257 | 0.48557 | 0.46915 | 0.45329 | 0.43796 | 0.42315 | 0.40884 | 0.39501 | 0.38165 | 0.36875 | 0.35628 | 0.3459 | 0.33583 | 0.32605 | 0.31655 | 0.30733 | 0.29838 | 0.28969 | 0.28125 | 0.27306 | 0.2651 | 0.25738 | 0.24989 | 0.24261 | 0.23554 | 0.22868 | 0.22202 | 0.21555 | 0.20928 | 0.20318 | 0.19726 | 0.19152 | 0.18594 | 0.18052 | 0.17527 | 0.17016 | 0.1652 | 0.16039 | 0.15572 | 0.15119 | 0.14678 | 0.14251 | 0.13836 | 0.13433 | 0.13041 | 0.12662 | 0.12293 | 0.11935 | 0.11587 | 0.1125 | 0.10922 | 0.10604 | 0.10295 | 0.099951 | 0.09704 | 0.094214 | 0.091916 | 0.089674 | 0.087487 | 0.085353 | 0.083271 | 0.08124 | 0.079259 | 0.077326 | 0.07544 | 0.0736 | 0.071805 | 0.070053 | 0.068345 | 0.066678 | 0.065051 | 0.063465 | 0.061917 | 0.060407 | 0.058933 | 0.057496 | 0.056094 | 0.054725 | 0.053391 | 0.052088 | 0.050818 | 0.049579 | 0.048369 | 0.04719 | 0.046039 | 0.044916 | 0.04382 | 0.042751 | 0.041709 | 0.040691 | 0.039699 | 0.038731 | 0.037786 | 0.036864 | 0.035965 | 0.035088 | 0.034232 | 0.033397 | 0.032583 | 0.031788 | 0.031013 | 0.030256 | 0.029518 | 0.028798 | 0.028096 | 0.027411
Source: | HM Treasury Green Book
|  | Uplift Factor (2% annual) |  | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101 | 2102 | 2103 | 2104 | 2105 | 2106 | 2107 | 2108 | 2109 | 2110 | 2111 | 2112 | 2113 | 2114 | 2115 | 2116 | 2117 | 2118 | 2119 | 2120 | 2121 | 2122 | 2123 | 2124 | 2125 | 2126 | 2127 | 2128 | 2129 | 2130 | 2131 | 2132 | 2133 | 2134 | 2135 | 2136 | 2137 | 2138 | 2139 | 2140 | 2141 | 2142
|  | 1.02 |  | 1 | 1.02 | 1.0404 | 1.0612 | 1.0824 | 1.1041 | 1.1262 | 1.1487 | 1.1717 | 1.1951 | 1.219 | 1.2434 | 1.2682 | 1.2936 | 1.3195 | 1.3459 | 1.3728 | 1.4002 | 1.4282 | 1.4568 | 1.4859 | 1.5157 | 1.546 | 1.5769 | 1.6084 | 1.6406 | 1.6734 | 1.7069 | 1.741 | 1.7758 | 1.8114 | 1.8476 | 1.8845 | 1.9222 | 1.9607 | 1.9999 | 2.0399 | 2.0807 | 2.1223 | 2.1647 | 2.208 | 2.2522 | 2.2972 | 2.3432 | 2.3901 | 2.4379 | 2.4866 | 2.5363 | 2.5871 | 2.6388 | 2.6916 | 2.7454 | 2.8003 | 2.8563 | 2.9135 | 2.9717 | 3.0312 | 3.0918 | 3.1536 | 3.2167 | 3.281 | 3.3467 | 3.4136 | 3.4819 | 3.5515 | 3.6225 | 3.695 | 3.7689 | 3.8443 | 3.9211 | 3.9996 | 4.0795 | 4.1611 | 4.2444 | 4.3293 | 4.4158 | 4.5042 | 4.5942 | 4.6861 | 4.7798 | 4.8754 | 4.9729 | 5.0724 | 5.1739 | 5.2773 | 5.3829 | 5.4905 | 5.6003 | 5.7124 | 5.8266 | 5.9431 | 6.062 | 6.1832 | 6.3069 | 6.433 | 6.5617 | 6.6929 | 6.8268 | 6.9633 | 7.1026 | 7.2446 | 7.3895 | 7.5373 | 7.6881 | 7.8418 | 7.9987 | 8.1586 | 8.3218 | 8.4883 | 8.658 | 8.8312 | 9.0078 | 9.188 | 9.3717 | 9.5592 | 9.7503 | 9.9453 | 10.1443 | 10.3471 | 10.5541 | 10.7652 | 10.9805 | 11.2001 | 11.4241 | 11.6526 | 11.8856