## GLA - Power
HDP Planning Consultation Tracker
Consultees | Response Date | Response Summary | Comments | Design Team Actions | Applicant Response
GLA - Power | 2025-07-26 | Further detail is required | · The site is within the area of west London served by the Distribution Network Operator SSEN, which is currently subject to on-going electricity capacity constraints.
|  |  | · The applicant states an agreement has been made with National Grid and SSE to provide power to the site. |  | Correct.
|  |  | · In the Utility Statement the applicant states the campus will be served by two 150MW connections however in the Infrastructure Statement the applicant states the development requires 250MW of power, secured through two independent National Grid connections with phased delivery between 2027 and 2029: (i) 100MW from Uxbridge Moor/Iver B and Bullsbrook Road Substation and (ii) 150MW from North Hyde. We would advise that the case officer seek clarification on this point. |  | LON4,5 power was included in the statement of 250MW. However, only 150MW is applicable to LON6,7,8 . Approved application ref: 38421/APP/2021/4045 is 100MW (from Iver), current application ref: 78343/APP/2025/719 is 150MW (from North Hyde)
|  |  | · In the Utility Statement the applicant states an SSEN 1000kVA supply will be located at the north of the site to provided 720kVA to Hayes Digital Park including the Innovation hub. |  | Correct. This is to supply the Innovation Hub.
|  |  | · The applicant states enquiries have been made with the necessary statutory undertakers regarding the power requirements and other utilities necessary. The applicant states enquiries will be made with the utility service providers. |  | The 150MW North Hyde and 100MW Iver are confirmed contracted supplies with National Grid
|  |  | The North Hyde Nation Grid connection made by the applicant to power the site is a connection to one of the known constrained grid supply points within the West London area. |  | Point noted. We understand National Grid is upgrading Iver primary substation to account for our data centre and other data centre campuses around the area.
|  |  | The Uxbridge Moor/Iver B National Grid connection made by the applicant to power the site is outside of the outside of the development borough and outside of London. Uxbridge Moor GSP is a new GSP that is currently under development by National Grid. The current timeline for energisation is 2029: Uxbridge Moor substation ¦ National Grid. |  | Point noted. Refer to response above.
|  |  | We are aware of several instances of new data centres coming forward in the affected west London area are having to rely on the use of a significant 'stretch connection', sourcing power across boroughs and outside of London. These 'stretch connections' are an emerging phenomenon in west London as major energy users seek faster connection times in response to the on-going capacity constraints. Stretch connections generate significant environmental impacts in construction in terms of emission of pollutants, noise, vibration, the creation of nuisances, and in the disposal of waste associated with the works. To allow for a fuller assessment of the environmental impacts of this connection, we would advise that the applicant provides details as to: |  | Point noted. Refer to responses below. Emission of pollutants - airborne dust created by cuttings / breaking of road surfaces is controlled through the application of water during construction process. Noise & vibration is controlled through the use of carefully selected equipment to minimise impact where possible. Noise intensive activites are contained within daytime working hours to minimise disruption particularly in residential areas. Nuisance - where possible, out of hours working is deployed to minimise impact on busy roads and traffic in the locality.Skilled contractors are deployed with expertise to minimise programme and impacts. Waste disposal - the majority of excavated material is reused for backfilling of trenches , reducing the waste material to landfill
|  |  | · The proposed electricity connection, including the proposed point or points of connection, the routing or routings (if confirmed), capacity, timeframe for connection, and expected duration of construction works. | Ridge (Andrew Hinkins) to provide cable routes details, programme for the works. What is the planning process for taking the cable routing - is this under permitted development ? | Uxbridge Moor - Cable Route Plan attached. 80% of this cable route has already been constructed. The work on the cable route is expected to complete by October 20206. All cable route works are below ground. Works within the highways are conducted under a S50 Licence. North Hyde - Cable Route Plan attached. Works to commence in Q4 2025 and complete by Q1 - 2027.
|  |  | · The alternative points of connections considered. | Ridge (Andrew Hinkins) to provide cable routes details, programme for the works. | Connections contracts with NESO dictate the point of connection. Feasibility studies have been undertaken by a specialist contractor to establish the routes to the Data Centre site.
|  |  | · Assessment of environmental impacts of this construction. | JSM / Ridge | The feasibility studies, consider environmental impacts and environmental asssesmenta are consider at various points of the route e..g green spaces, river crosssings etc. Environment Agency approvals have been sought and obtained where necessary.
|  |  | · Outline of the steps taking to mitigate these impacts. | JSM / Ridge
|  |  | It should be noted that there are significant opportunities to mitigate the impacts of any streetworks through existing collaborative mechanisms. Collaborative works that are carried out concurrently by two or more works promoters at the same location on the Transport for London Road Network (TLRN) can apply to have the lane rental charges waivered for the period of collaboration. Further information on collaborative streetworks is available here: https://www.london.gov.uk/programmes-strategies/better-infrastructure/infrastructure-coordination/streets-service | JSM / Ridge | Point noted.
|  |  | Given the scale and extent of potential 'stretch connections' there is likely to be opportunities for collaboration, and subsequent cost saving to the applicant, given the broad programme of regular utility works undertaken by networks across London. We would advise that if proceeding with a stretch the applicant ensure that they engage at the earliest possible opportunity with utilities, boroughs, and other known work promoters during the planning and testing of a potential routing to assess any opportunities for collaboration. Doing this will increase the feasibility of aligning other works programmes and bringing about collaborative delivery. This would help reduce disruption to Londoners and the environmental impact of any connection works. |  | Point noted.
GLA - Power (Heat Network Integration) | 2025-07-26 | Further detail is required | In relation to heat network integration, and the opportunities for waste heat off-take, we would raise the following queries:
|  |  | o Has the developer contacted/liaised with any heat network providers or large energy demands in the vicinity to better understand the opportunity for heat export? |  | Yes. Berkeley Homes have been approached and we are in active discussions to provide waste heat that will be used to heat the residential units (8000 aprox) housed in their Green Quarter development on the Old Gas Works site Ealing under the approved app ref: 38421/APP/2021/4045. Under the current application, the pipework is taken to the site boundary for future extension . Heat load supply from LON6: 13.5MW
|  |  | o The application mentions that the design has allowed for provision of heat export and future connection to a heat network, but what are these infrastructure provisions? Provision has been made within planning documentation for heat export to innovation hub and admin buildings but what about futureproofing the development for heat export to local heat demands. |  | At present, there is no known demand for the heat export and on that basis it has been agreed to cap off the supply at the edge of the site for future provisions. It is worth noting that the district heating network in the masterplan will heat the data centre communal areas such as the office block, amenity areas and Innovation Hub. The data centre building design includes plate heat exchangers located on the roofs that form the basis of the heat export infrastructure. Warm return water from the data halls is distributed to the primary side of the plate heat exchangers. Pipework is distributed from the secondary side of the plate heat exchangers to below ground chambers or kiosks located near the site boundary. These chambers will serve as connection points to any future external heat network.
|  |  | o Documentation mentions: Low grade heat (~30°C water) is pumped to a connection point housed within a kiosk or energy centre on the site boundary, for extension by others – is this within the site boundary or would an ESCo have to purchase land adjacent? A connection point that could house a kiosk for additional plant room such as a plate heat exchanger at the site boundary is preferred in order to futureproof the site for heat export. |  | As above, kiosks or below ground chambers are provided near the site boundary (within the site boundary) to facilitate any future heat network connection. The plate heat exchangers are located on the data centre building roofs.
|  |  | We would request data that will help the assessment for potential heat availability and export, such as: Peak IT load, Expected DC type (Enterprise, Colocation, Hyperscale etc), Expected cooling system types(s), Expected PUE |  | Peak IT Load: • LON6: 30MW • LON7: 60MW • LON8: 22MW Expected DC type: Enterprise Cooling system: Chilled water system with heat rejected by air-cooled chillers located on the roof gantry. Expected annualised PUE: 1.22
|  |  | We would also want to confirm whether the applicant has included unregulated carbon emissions in their carbon offset calculations. |  | According to GLA energy statement guidance unregulated carbon emission is not accounted in the carbon offset calculations.