## Case details
Energy Memo: GLA Consultation
Case details
Date of first review: | 2024-05-29
Case Name: | 148-154 High Street Uxbridge
Case Number: | 2024/0265
Case Officer: | Valeria Cabrera
London Borough: | Hillingdon
Application Type (Outline/Hybrid/Detailed): | Detailed
Applicant: | DNA Uxbridge Ltd.
Energy Consultant: | Ridge and Partners
Document Title: | Energy Strategy Report
Document Date: | 2024-03-27
Development proposals
Use | Floorspace/Number of units
Hotel (C1) | TBC
Residential co-living accom (Sui Generis) | TBC
commercial floorspace € | TBC

## Pre-application advice (hidden)
Useful References/Links
1 | London Plan: The Mayor has published his London Plan 2021 which includes new carbon, energy and heat risk policies (See Policies SI 2, SI 3 and SI 4) which applicants are expected to follow. This can be found here: https://www.london.gov.uk/what-we-do/planning/london-plan/new-london-plan/london-plan-2021 | https://www.london.gov.uk/what-we-do/planning/london-plan/new-london-plan/london-plan-2021
2 | As of 1 January 2023 all planning applications submitted on or after this date will be required to follow the 2022 guidance and spreadsheet. If you have any questions about the guidance or the spreadsheet, please contact: ZeroCarbonPlanning@london.gov.uk | https://www.london.gov.uk/what-we-do/planning/planning-applications-and-decisions/pre-planning-application-meeting-service-0
3 | The following comments summarise key points for you to be aware of in progressing your energy strategy, but you should refer to the guidance for full details. A Technical FAQ has been developed which applicants should refer to. This will be updated regularly.
Net zero carbon target
4 | The Mayor’s London Plan 2021 requires all major developments (residential and non-residential) to meet his net-zero carbon target. This should be met with a minimum on-site 35% reduction in carbon emissions beyond Part L of 2021 Building Regulations with any carbon shortfall to net zero being paid into the relevant borough’s carbon offset fund using the GLA’s recommended carbon offset price (£95/tonne) or, where a local price has been set, the borough’s carbon offset price .
5 | Applicants should submit a completed Carbon Emissions Reporting spreadsheet (https://www.london.gov.uk/what-we-do/planning/planning-applications-and-decisions/pre-planning-application-meeting-service-0) alongside their Stage 1 application to confirm the anticipated carbon performance of the development. | https://www.london.gov.uk/what-we-do/planning/planning-applications-and-decisions/pre-planning-application-meeting-service-0
6 | The carbon emission figures should be reported against a Part L 2021 baseline. Sample SAP full calculation worksheets (both DER and TER sheets) and BRUKL sheets for all stages of the energy hierarchy should be provided to support the savings claimed.
Be Lean Demand Reduction
7 | Applicants are expected to meet the London Plan 2021 energy efficiency targets: • Residential – at least a 10% improvement on 2021 Building Regulations from energy efficiency • Non-residential – at least a 15% improvement on 2021 Building Regulations from energy efficiency
8 | Applicants are expected to design buildings to be able to meet all energy policy areas. They should consider how building form is contributing to the meeting of energy policy targets. Applicant are required to consider the suitability of other design areas which may be negatively impacting the energy consumption and overheating risk of the proposed development.
9 | Applicants will be expected to consider and minimise the estimated energy costs to occupants and outline how they are committed to protecting the consumer from high prices. See the guidance for further detail.
Energy flexibility
10 | Applicants will be expected to investigate the potential for energy flexibility in new developments, include proposals to reduce the amount of capacity required for each site and to reduce peak demand. The measures followed to achieve this should be set out in their energy assessment. See the Energy Assessment Guidance for further details.
Cooling and Overheating
11 | The Good Homes Alliance (GHA) Early Stage Overheating Risk Tool (https://goodhomes.org.uk/wp-content/uploads/2019/07/GHA-Overheating-in-New-Homes-Tool-and-Guidance-Tool-only.pdf) should be submitted to the GLA alongside the Stage 1 application, if this was not submitted at pre-application stage, to identify potential overheating risk and passive responses early in the design process. | https://goodhomes.org.uk/wp-content/uploads/2019/07/GHA-Overheating-in-New-Homes-Tool-and-Guidance-Tool-only.pdf
12 | Evidence should be provided on how the demand for cooling and the overheating risk will be minimised through passive design in line with the cooling hierarchy. Dynamic overheating modelling in line with CIBSE Guidance should be carried out (TM59 for residential taking into account the associated Approved Document O requirements and TM52 for non-residential) for all TM49 weather scenarios. It is expected that external shading will form part of major proposals. All applications are expected to comply with the DSY1 and maximise compliance with DSY2 & DSY3 by enhancing passive measures.
13 | The area weighted average (MJ/m2) and total (MJ/year) cooling demand for the actual and notional building should be provided and the applicant should demonstrate that the actual building’s cooling demand is lower than the notional.
Be Clean Heating Infrastructure
14 | The applicant should investigate opportunities for connection to nearby existing or planned district heating networks (DHNs) using the London Heat Map (https://www.london.gov.uk/what-we-do/environment/energy/london-heat-map). Where such opportunities exist, this should be the priority for supplying heat to the site in line with the London Plan 2021 heating hierarchy. Evidence of this investigation should be provided including evidence of active two-way communication with the network operator, the local authority and other relevant parties. This should include information on connection timescales and confirmation that the network has available capacity. See the guidance for full details on the information that should be provided. | https://www.london.gov.uk/what-we-do/environment/energy/london-heat-map
15 | The site should be provided with a single point of connection and a communal heating network where all buildings/uses on site will be connected. The heat loads that are connected to the site-wide heat network should be maximised. Relevant drawings/schematics demonstrating the above should be provided.
16 | The applicant should provide evidence confirming that the development is future proofed for connection to wider district networks now or in the future, where an immediate connection is not available.
17 | Where a DHN connection is not available, either now or in the future, applicants should follow the London Plan 2021 heating hierarchy to identify a suitable communal heating system for the site.
18 | The London Plan 2021 limits the role of CHP to low-emission CHP and only in instances where it can support the delivery of an area-wide heat network at large, strategic sites. Applicants proposing to use low-emission CHP will be asked to provide sufficient information to justify its use and strategic role while ensuring that the carbon and air quality impact is minimised.
Be Green Renewable Energy
19 | All major development proposals should maximise opportunities for renewable energy generation by producing, using and storing renewable energy on-site. This is regardless of whether the 35% on-site target has already been met through earlier stages of the energy hierarchy.
20 | Solar PV should be maximised. Applicants should submit the total PV system output (kWp) and a detailed roof plan showing that the proposed installation has been maximised for the available roof area and clearly outlining any constraints to further PV. The applicant is expected to situate PVs on green/brown roofs and explore integration with amenity areas.
21 | Should heat pumps be proposed, applicants will be expected to demonstrate a high specification of energy efficiency measures under be lean, a thorough performance analysis of the heat pump system and, where there are opportunities for DHN connection, that the system is compatible. The detail submitted on heat pumps should include: a. An estimate of the heating and/or cooling energy (MWh/annum) the heat pumps would provide to the development and the percentage of contribution to the site’s heat loads. The applicant will be required to demonstrate how the heat fraction from heat pump technologies will be maximised. b. Details of how the Seasonal Coefficient of Performance (SCOP) and Seasonal Energy Efficiency ratio (SEER) has been calculated for the energy modelling. This should be based on a dynamic calculation of the system boundaries over the course of a year i.e. incorporating variations in source temperatures and the design sink temperatures (for space heat and hot water). c. The expected heat source temperature and the heat distribution system temperature with an explanation of how the difference will be minimised to ensure the system runs efficiently. The distribution loss factor should be calculated based on the above information and used for calculation purposes.
22 | Should an ambient loop heat network be proposed, the applicant will be required to engage with local DHN stakeholders and demonstrate that proposals will be compatible and commercially viable for future connection to district heating.
Carbon Offsetting
23 | Applicants should maximise carbon emission reductions on-site. Where it is clearly demonstrated that no further carbon savings can be achieved, but the site falls short of the net-zero carbon reduction targets, applicants are required to make a cash-in-lieu contribution to the relevant borough's carbon offset fund using the GLA’s recommended carbon offset price (£95/tonne) or, where a local price has been set, the borough’s carbon offset price.
24 | Energy strategies should provide a calculation of the shortfall in carbon emissions and the offset payment that will be made to the borough.
Whole Life-Cycle Carbon Assessment
25 | Applicants will be expected to calculate and reduce whole life-cycle carbon emissions to fully capture the development’s carbon footprint. Applicants should submit a whole life-cycle carbon assessment to the GLA at pre-application stage, as part of the Stage 1 application submission and post-construction, following the Whole Life-Cycle Carbon Assessment Guidance and using the GLA’s reporting template (https://www.london.gov.uk/what-we-do/planning/implementing-london-plan/london-plan-guidance/whole-life-cycle-carbon-assessments-guidance). Applicants will be conditioned to submit a post-construction assessment to report on the development’s actual WLC emissions. | https://www.london.gov.uk/what-we-do/planning/implementing-london-plan/london-plan-guidance/whole-life-cycle-carbon-assessments-guidance
Be Seen Energy Monitoring
26 | Applicants will be expected to monitor their development’s energy performance and report on it through the GLA's online monitoring portal. Applicants should review the ‘Be Seen’ energy monitoring guidance to ensure that they are fully aware of the relevant requirements to comply with the ‘be seen’ policy (https://www.london.gov.uk/sites/default/files/be_seen_energy_monitoring_london_plan_guidance_2021.pdft). A commitment should be provided that the development will be designed to enable post construction monitoring and that the information set out in the ‘be seen’ guidance is submitted to the GLA’s portal at the appropriate reporting stages. This will be secured through suitable legal wording. The first submission of the planning stage data should be provided to the GLA through the 'Be Seen' planning stage webform (https://www.london.gov.uk/what-we-do/planning/implementing-london-plan/london-plan-guidance/be-seen-energy-monitoring-guidance/be-seen-planning-stage-webform) at the planning submission stage, alongside the energy statement. The 'Be Seen' reporting spreadsheet has been developed to enable development teams to capture all data offline before this is submitted via the webform. Should there be any issues with the webform, the reporting spreadsheet can also be submitted directly over email. | https://www.london.gov.uk/what-we-do/planning/implementing-london-plan/london-plan-guidance/be-seen-energy-monitoring-guidance
https://www.london.gov.uk/what-we-do/planning/implementing-london-plan/london-plan-guidance/be-seen-energy-monitoring-guidance/be-seen-planning-stage-webform
Energy Use Intensity and Space Heating Demand Reporting
27 | Applicants should report the EUI and space heating demand of the development. Applicants are encouraged to improve performance where possible against the demand values reported in Table 4 of the Energy Assessment Guidance. Applicants can use the ‘be seen’ methodology or an alternative predictive energy modelling methodology. Reported values should exclude any renewable energy contribution.

## Energy Comments
Compliance Schedule - To be completed by the GLA Energy Officer
| Policy | Policy Sub-Area | Required Data (In line with EAG) | Status | Policy Compliance | GLA Comment Reference
| SI 1 - Improving Air Quality (relating only to air quality impacts of energy systems; separate air quality officer consultation required) | Measures/design features to reduce exposure to air pollution | Measures to minimise NOx emissions from energy systems | N/A | Compliant | 18
| SI 2 - Minimising Greenhouse Gas Emissions (excluding SI-2-F- WLC; separate WLC consultation required) | Be Lean emissions reduction | Details of energy efficiency measures | Not yet received - applicant to submit and provide reference ---> | Potential Compliance-Pending Information | 4,5
|  |  | Alignment with Cooling and Overheating | Not yet received - applicant to submit and provide reference ---> |  | 7,8
|  |  | Be Lean 10% and/or 15% reduction achieved | Not yet received - applicant to submit and provide reference ---> |  | 4,5
|  |  | EUI and space heating demands provided | Received but items still outstanding |  | 15
|  | Be Clean | SI 3 - Energy Infrastructure data provided (see below) | Not yet received - applicant to submit and provide reference ---> |  | 9,10
|  | Be Green Renewable generation maximisation | Roof Layout detailing maximised PV proposal | Not yet received - applicant to submit and provide reference ---> |  | 11
|  |  | PV array metrics provided | Not yet received - applicant to submit and provide reference ---> |  | 11
|  |  | Heat Pump arrangement confirmed | Not yet received - applicant to submit and provide reference ---> |  | 12
|  | Total carbon reduction on-site | Confirmation of carbon emission factors used | Received; SAP 10.2 proposed and nothing further required
|  |  | GLA carbon emission reporting spreadsheet v2.0 | Not yet received - applicant to submit and provide reference ---> |  | 3
|  |  | Supporting Modelling Outputs (BRUKLs/DER Worksheets) | Received but items still outstanding |  | 17
|  |  | On-site minimum met | Received but items still outstanding |  | 0
|  | Carbon offset payment confirmed | Draft S106 wording of carbon offset (from borough) | Not yet received - applicant to submit and provide reference ---> |  | 16
|  | Be Seen commitment provided | Written confirmation/understanding of data requirements | Not yet received - applicant to submit and provide reference ---> |  | 14
|  |  | Confirmation of Planning Stage 1 submission | Not yet received - applicant to submit and provide reference ---> |  | 14
| SI 3 - Energy Infrastructure | Aligned with heating hierarchy | Applicant/Heat Network Stakeholder correspondence | Not yet received - applicant to submit and provide reference ---> | Potential Compliance-Pending Information | 9
|  |  | Heating system details provided | Received but items still outstanding |  | 10
|  | Acceptable Design | Futureproofed DHN connection drawings | Not yet received - applicant to submit and provide reference ---> |  | 10
|  |  | Site heat network drawings | Not yet received - applicant to submit and provide reference ---> |  | 10
|  |  | Details of management measures proposed | Not yet received - applicant to submit and provide reference ---> |  | 6
| SI 4 - Managing Heat Risk | Aligned with cooling hierarchy | Completed GHA overheating tool | Not yet received - applicant to submit and provide reference ---> | Potential Compliance-Pending Information | 0
|  |  | CIBSE dynamic overheating analysis | Not yet received - applicant to submit and provide reference ---> |  | 7,8
|  |  | Confirmation that cooling criteria have been met | Not yet received - applicant to submit and provide reference ---> |  | 8
| Application Metrics | Outline Value (if applicable) | Detailed Stage 1 Value | Detailed Final Value
| Domestic carbon emissions |  | TBC
| Non-domestic carbon emissions |  | TBC
| Carbon offset payment amount |  | TBC
| kWp renewable generation capacity |  | TBC
| kWh annual renewable energy generation |  | TBC
| Sqm of proposed PV array |  | TBC
| Calculated SCOP of heat pumps |  | TBC
| Heat fraction provided by heat pumps |  | TBC
| Flow/Return temperatures proposed |  | TBC
| Distribution loss assumption |  | TBC
| Energy Use Intensity |  | TBC
| Space Heating Demand |  | TBC
| Whole Life Carbon Assessment |  | Received and Under Separate Consultation
Innovative Features
Detailed Comments - Applicant MUST provide detailed responses to the below items
Comment No. | GLA Stage I | Applicant's Stage I response | GLA Post Stage I response | Applicant's Post Stage I response
| Date: 29/05/24 | Date: 01/11/2024 | Date: | Date:
Documents to be secured
Energy Strategy Report (27/03/2024)
General compliance comments
1 | The energy strategy could be compliant with the London Plan 2021 policies however, the applicant is required to submit the additional information to demonstrate policy compliance which has been requested below. The applicant's response to GLA's energy comments should be provided directly within this Energy Memo. Any wider supporting material submitted should be referenced within the applicant's memo response. | Completed
2 | The applicant appears to have completely miscalculated the carbon savings. They should re-visit the GLA policy guidance provided online to understand how the energy statement should be carried out. The submission is unacceptable in this state. Firstly, the co-living block is considered by the GLA to be a non-domestic space so should be modelled in SBEM. Secondly, the be lean saving appears to be showing a -78% saving. This cannot be correct. Furthermore, the applicant should show the heat pump and PV saving under the be green scenario not be clean. The be clean is reserved for district heating. The be clean for this submission will be exactly the same as the be lean. As per GLA guidance section 7.9, the applicant should use a heat pump with an efficiency of 2.64 for space heating and 2.86 for hot water for the be lean scenario in all non-domestic spaces. The applicant should read this guidance to understand it properly. The applicant should update their tables in the report to show the actual carbon emissions rather than just savings. The applicant should also provide the floor areas and use classes of all areas to make sure that all space is accounted for on the carbon reporting spreadsheet. | Please refer to the Energy Strategy Report as well as the CO2 performance sheet on this document. The Co-Living has been assessed as a non-domestic space and has been modelled in SBEM. All scenarios (Be lean, clean, and green) have been re-calculated. Additionally, the heat pump assessment and the PV assessment have been included under the Be Green scenario, while the Be Clean has been assessed exactly as the Be Lean. All tables containing the results have been updated to show both, the actual carbon emissions and the savings. Floor areas and use classes of all areas have been included.
3 | The applicant should submit the GLA’s Carbon Emission Reporting spreadsheet in excel format. The applicant should ensure that all tabs are completed as per methodology on Introduction tab. [The link to the spreadsheet can be found here: https://www.london.gov.uk/programmes-strategies/planning/planning-applications-and-decisions/pre-planning-application-meeting-service/energy-planning-guidance] | Please refer to the GLA's Carbon Emission Reporting spreadsheet.
Be Lean
4 | There should be no domestic element to this scheme. Co living is considered as non-domestic and therefore should be modelled in SBEM and not SAP. The applicant will need to re-do this modelling within the correct software and update the findings under the non-domestic savings alongside the hotel, amenity areas and retail. | Co-Living assessed as non-domestic and modelled in SBEM.
5 | Based on the information provided, the non-domestic element of the proposed development is estimated to achieve a reduction of -184.3 tonnes per annum (-78%) in regulated CO2 emissions compared to a 2021 Building Regulations compliant development. Secondly, the be lean saving appears to be showing a -78% saving. This cannot be correct. The applicant must have miscalculated this. Furthermore, the applicant should show the heat pump and PV saving under the be green scenario not be clean. The be clean is reserved for district heating. The be clean for this submission will be exactly the same as the be lean. As per GLA guidance section 7.9, the applicant should use a heat pump with an efficiency of 2.64 for space heating and 2.86 for hot water for the be lean scenario in all non-domestic spaces. The applicant should read this guidance to understand it properly. The applicant should note that the London Plan includes a target of a minimum 15% improvement on 2021 Building Regulations from energy efficiency which applicants should target. The applicant should therefore consider modelling additional energy efficiency measures to meet the EE target. | All scenarios (Be lean, clean, and green) have been re-calculated to provide a reasonable result. Additionally, the heat pump assessment and the PV assessment have been included under the Be Green scenario, while the Be Clean has been assessed exactly as the Be Lean. Results can be found withing the Energy Strategy Report and the CO2 Performance sheet of this document
6 | The applicant should consider and minimise the estimated energy costs to occupants and outline how they are committed to protecting the consumer from high prices. This should cover the parameters set out in the guidance and include a confirmation of the quality assurance mechanisms that will be considered as part of the strategy. See GLA Energy Assessment Guidance June 2022 paragraphs 7.16-7.19 for further details. | The estimated energy costs to occupants and how they are committed to protect the consumer from high prices has been included as part of the Energy Strategy Report.
Overheating
7 | The applicant should undertake a Dynamic Overheating Analysis to assess the overheating risk. This should follow the CIBSE TM59 methodology for the London Design Summer Year 1 (DSY1) weather file: 2020s, High emission, 50% percentile scenario. The applicant should also investigate the risk of overheating using the DSY 2 & 3 weather files. | The Dynamic Overheating Analysis has been carried on. It followed the CIBSE TM59 methodology for London DSY1 weather file as well as for the future weather files, London DSY2 and 3 2020s, High Emissions, 50th percentile. Please refer to the TM59 Overheating Report.
8 | The area weighted average (MJ/m2) and total (MJ/year) cooling demand for the actual and notional building should be provided and the applicant should demonstrate that the actual building’s cooling demand is lower than the notional. A Dynamic Overheating Analysis to assess the overheating risk on any naturally ventilated spaces should be carried out. This should follow the CIBSE TM52 methodology for the London Design Summer Year 1 (DSY1) weather file: 2020s, High emission, 50% percentile scenario. The applicant should also investigate the risk of overheating using the DSY 2 & 3 weather files. | The Dynamic Overheating Analysis has been carried on. It followed the CIBSE TM52 methodology for London DSY1 weather file as well as for the future weather files, London DSY2 and 3 2020s, High Emissions, 50th percentile. Please refer to the TM52 Report. The area weighted average and total cooling demand for the actual and notional building was assessed and it is provided on the TM52 Report as well as for the Energy Strategy Report.
Be Clean
9 | The applicant has carried out an investigation and there are no existing or planned district heating networks within the vicinity of the proposed development. They should contact relevant stakeholders including the borough energy officer, local heat network operators and nearby developers and ask whether they know of any local heat network connection opportunities. Evidence of the correspondence should be submitted. | The investigation has been carried on and there are no existing/planned district heating network nearby of the proposed development. Please refer to the Energy Strategy Report to see more details of this as well as for the evidence of contacting the relevant stakeholders.
10 | The applicant should detail the type of system they are proposing. They should propose a site-wide or communal heat network supplied by a centralised energy centre. It should be confirmed that all apartments and non-domestic building uses will be connected to the heat network. (if applicable)They should maximise the heat loads that are connected to the site-wide heat network and any divergences from policy should be robustly justified. A drawing/schematic showing the route of the heat network/networks linking all buildings/uses on the site has been/should be provided alongside a drawing indicating the floor area, internal layout and location of the energy centre/centres. The applicant should provide a commitment that the development is designed to allow future connection to a district heating network. This should include a single point of connection to the district heating network. Drawings should be provided demonstrating space for heat exchangers in the energy centre/centres, and a safe-guarded pipe route to the site boundary, and sufficient space in cross section for primary district heating pipes where proposed routes are through utility corridors. This requirement is to be secured through a suitable condition or legal wording. | This has been included as part of the Energy Strategy Report. A drawing/schematic of the route of the heat network has been provided.
Be Green
11 | The applicant is proposing to install 106.3 kWp of PV. A detailed roof layout should be provided demonstrating that the roof’s potential for a PV installation has been maximised and clearly outlining any constraints to the provision of further PV, such as plant space or solar insolation levels. The applicant is expected to situate PV on any green/brown roof areas using biosolar arrangement and should indicate how PV can be integrated with any amenity areas. The on-site savings from renewable energy technologies should be maximised regardless of the London Plan targets having been met. The applicant should provide the capacity (kWp), total net area (m2) and annual output (kWh) of the proposed PV array. | We have re-calculated the amount of PV that we are intending to install. Roof layouts showing that the PV installation has been maximised and further PV details (capacity, total net area, annual output) can be found on the Energy Strategy Report as well as for the Operational Energy Report.
12 | Heat pumps are being proposed in the form of a (centralised) ASHP system. Further information on the heat pumps should be provided including: a. An estimate of the heating and/or cooling energy (MWh/annum) the heat pumps would provide to the development and the percentage of contribution to the site’s heat loads. They should demonstrate how the heat fraction from heat pump technologies has been maximised. b. Details of the Seasonal Coefficient of Performance (SCOP) and/or Seasonal Energy Efficiency ratio (SEER) and how these have been calculated for the specific proposed system's operation. This should incorporate the expected heat source and heat distribution temperatures (for space heat and hot water)and the distribution loss factor, which should be calculated based on the above information and used for calculation purposes. This information is even more prevalent given the extremely high COPS and SEERS which have been modelled. These are considered unacceptable by the GLA and should be revised before the next submission. | Find the details/evidence on the Energy Strategy Report and the Operational Energy Report. Evidence of SCOP and SEER can be found as part of the Technical Specifications attached to the submission.
Whole Life-Cycle Carbon Assessment
13 | The applicant has submitted a WLC assessment which will be reviewed separately; comments will be provided. The WLC assessment should be presented separately in excel using the GLA's WLC assessment template and should follow the GLA WLC guidance. The template and guidance are available here: https://www.london.gov.uk/what-we-do/planning/implementing-london-plan/london-plan-guidance/whole-life-cycle-carbon-assessments-guidance. Applicants will also be conditioned to submit a post-construction assessment to report on the development’s actual WLC emissions. | Please refer to the WLC Assessment provided for the Proposed Development for further information, in addition to GLA's WLC assessment template also completed for the scheme.
Be Seen Energy Monitoring
14 | A commitment should be provided that the development will be designed to enable post construction monitoring and that the information set out in the ‘Be Seen’ guidance is submitted to the GLA’s portal at the appropriate reporting stages. This will be secured through suitable legal wording. The 'Be Seen' reporting spreadsheet has been developed to enable development teams to capture all data offline before this is submitted via the webform. Once the planning stage CO2 emissions have been agreed with GLA, the applicant should confirm that the planning stage data has been submitted to GLA. | Please refer to the Be Seen reporting spreadsheet submitted. Suitable legal wording commenting that the development will be designed to enable post construction monitoring has been included as part of the energy Strategy Report.
Energy Use Intensity and Space Heating Demand Reporting
15 | EUI and space heating demands have been provided for the residential areas but not non-domestic. The applicant will need to re-submit the co-living space as this is considered non-domestic The applicant should detail the methodology used for these calculations. The applicant should report the EUI and space heating demand against the reference values in Table 4 of GLA guidance. The applicant should provide commentary if the expected performance differs from the reference values. | EUI and space heating demand have been re-calculated for the non-domestic spaces only, the methodology has been detailed on the calculations. Please refer to the Energy Strategy Report and the Operational Energy Report.
Other points
16 | The applicant should confirm the carbon shortfall in tonnes CO2 and the associated carbon offset payment that will be made to the borough. This should be calculated based on a net-zero carbon target for domestic and non-domestic proposals using the GLA’s recommended carbon offset price (£95/tonne) or, where a local price has been set, the borough’s carbon offset price. The draft s106 agreement should be submitted when available to evidence the carbon offset agreement with the borough. | Using the GLA's recommended carbon offset price. The carbon short fall in tonnes of CO2 and the associated carbon offset payment has been detailed on the Energy Strategy Report
17 | The applicant should provide the relevant modelling output sheets (i.e. TER, DER, BRUKL) for the baseline, be lean, be clean and be green stages of the energy hierarchy. | Please refer to the BRUKLs attached on the submission.
18 | The applicant should complete and submit the Good Homes Alliance Early Stage Overheating Risk Tool. | See attached completed Good Homes Alliance Early Stage Overheating Risk Tool
Move resolved comments under this section
Received; SAP 10.2 proposed and nothing further required
Received; SAP 10 proposed and nothing further required
Received; SAP 2012 proposed and nothing further required
Received; SAP 10.2 proposed but items still outstanding
Received; SAP 10 proposed but items still outstanding
Received; SAP 2012 proposed but items still outstanding
Not yet received - applicant to submit and provide reference --->
N/A

## CO2 performance
Unhide Column F-I if Hybrid Application
Domestic (detailed) - No domestic spaces assessed |  |  |  |  | Domestic (outline/detailed) |  |  |  | Site Wide
SAP 10.2 | Total residual regulated CO2 emissions | Regulated CO2 emissions reductions |  |  | SAP 10.2 | Total residual regulated CO2 emissions | Regulated CO2 emissions reductions |  | SAP 2012 | Total residual regulated CO2 emissions | Regulated CO2 emissions reductions
| (tonnes per annum) | (tonnes per annum) | (per cent) |  |  | (tonnes per annum) | (tonnes per annum) | (per cent) |  | (tonnes per annum) | (tonnes per annum) | (per cent)
Baseline i.e. 2021 Building Regulations |  |  |  |  | Baseline i.e. 2013 Building Regulations |  |  |  | Baseline i.e. 2021 Building Regulations | 129
Energy Efficiency |  | 0 | #DIV/0! |  | Energy Efficiency |  | 0 | #DIV/0! | Energy Efficiency | 109.5 | 19.5 | 15.12%
CHP |  | 0 | #DIV/0! |  | CHP |  | 0 | #DIV/0! | CHP | 109.5 | 0 | 0%
Renewable energy |  | 0 | #DIV/0! |  | Renewable energy |  | 0 | #DIV/0! | Renewable energy | 83.2 | 26.3 | 20.39%
Total |  | 0 | #DIV/0! |  | Total |  | 0 | #DIV/0! | Total | 96.9 | 45.8 | 35.5%
Hotel, CoLiving Block, Retail and Amenity spaces - Non-domestic (detailed) |  |  |  |  | Non-domestic (outline/detailed)
SAP 10.2 | Total residual regulated CO2 emissions | Regulated CO2 emissions reductions |  |  | SAP 10.2 | Total residual regulated CO2 emissions | Regulated CO2 emissions reductions
| (tonnes per annum) | (tonnes per annum) | (per cent) |  |  | (tonnes per annum) | (tonnes per annum) | (per cent)
Baseline i.e. 2021 Building Regulations | 129 |  |  |  | Baseline i.e. 2013 Building Regulations
Energy Efficiency | 109.5 | 19.5 | 15.12% |  | Energy Efficiency |  | 0 | #DIV/0!
CHP | 109.5 | 0 | 0% |  | CHP |  | 0 | #DIV/0!
Renewable energy | 83.2 | 26.3 | 20.39% |  | Renewable energy |  | 0 | #DIV/0!
Total |  | 45.8 | 35.5% |  | Total |  | 0 | #DIV/0!
Carbon offsetting (detailed) - TBC |  |  |  |  | Carbon offsetting (outline/detailed)
| Shortfall (tonnes per annum) | Shortfall (£) |  |  |  | Shortfall (tonnes per annum) | Shortfall (£)
Domestic | 0 | 0 |  |  | Domestic | 0 | 0
Non-domestic | 83.2 | 237120 |  |  | Non-domestic | 0 | 0
Total | 83.2 | 237120 |  |  | Total | 0 | 0