C9128 Premier Inn Uxbridge Bedroom Extension Part L Compliance Sheet

U-Values, Architectural & Building Data

|  | As Designed Specification – Element Description | Key Variable |
| --- | --- | --- |
| Floor - External Floor | IES Default Construction U-value 0.10 W.m-2.K-1 | 0.10 W.m-2.K-1 |
| Wall - External Wall | IES Default Construction U-value 0.15 W.m-2.K-1 | 0.15 W.m-2.K-1 |
| Roof | IES Default Construction U-value 0.10 W.m-2.K-1 | 0.10 W.m-2.K-1 |
| Internal Floor | IES Default Construction | N/A |
| Internal Wall | IES Default Construction | N/A |
| Internal Ceiling | IES Default Construction | N/A |
| Doors – Solid Door | Solid door, U-value 1.30 W.m-2.K-1 | 1.30 W.m-2.K-1 |
| Doors – Glazed Door | Double glazing U-value 1.10 W.m-2.K-1, G-value 0.40 | 1.10 W.m-2.K-1 0.40 |
| Doors – Glazed Entrance Door | Double glazing U-value 1.10 W.m-2.K-1, G-value 0.40 | 1.10 W.m-2.K-1 0.40 |
| Glazing - Window | Double glazing U-value 1.10 W.m-2.K-1, G-value 0.40 | 1.10 W.m-2.K-1 0.40 |
| Air Pressure | Maximum allowable Part L 2021 air permeability rate is 4.0 m3.h-1.m-2 @ 50Pa | 4.0 m3.h-1.m-2 @ 50Pa |
| Power Factor Correction | Typical value for new equipment is >0.95. However, the level of information required during a CIBSE audit that justifies inputting >0.95 can be prohibitive. Based on Littlehampton Specification. | >0.95 |

Mech & Elec.

|  | As Designed Specification – Element Description | Key Variable |
| --- | --- | --- |
| Space Heating System | Bedroom - ASHP – SCOP: 4.67 SEER: 6.08 EER: 5.29 Restaurant - ASHP – SCOP: 4.05 SEER: 5.90 EER: 3.97 Team Room - ASHP – SCOP: 3.9 SEER: 5.90 EER: 3.83 Office - ASHP – SCOP: 3.9 SEER: 5.9 EER: 3.83 Reception - ASHP – SCOP: 4.12 SEER: 3.61 EER: 3.61 (Bedroom based on EP200 Restaurant based on EP400) | SCOP, SEER, EER |
| Ventilation | Bedroom – MVHR – 1.1 SFP 0.80 Heat Recovery Efficacy (Bedroom Based on PREM3 Trickle SFP: 1.13 Boost SFP: 0.98) Restaurant / Office / Team Room / Reception – MVHR – 1.5 SFP 0.80 Heat Recovery Efficacy Glass Wash – Industrial Extract – 1.50 SFP 40ach Linen/Toilet – Extract Fan Remote from Zone – 0.4 SFP | SFP, Heat Recovery Rate & Flowrate |
| Hot Water System | SCOP – 4.3 Storage – 3000 l Storage Losses – (kWh//(l.day)) = 0.0047 Loop (Pipework) Length 5 m per bedroom (40) – 200 metres Loop (Pipework) Length Losses – Watts/m2 = 8W/m2 Pump Power - 100W | SCOP, Storage Volume, Storage Losses, Pipework Length, Pipework Losses, Secondary Circulation Pump Power |
| Lighting | Bedroom – 1.67 Power Density Shower – 2.0 Power Density – Estimate Corridor – 2.3 Power Density – Estimate Staircases – 1.5 Power Density – Estimate Glass Wash – 2.0 Power Density – Estimate Linen – 2.0 Power Density – Estimate Plant Room – 2.0 Power Density – Estimate Reception – 2.0 Power Density - Estimate Restaurant/Bar – 1.5 Power Density – Estimate Store – 2.0 Power Density – Estimate Toilet – 2.0 Power Density – Estimate Team Room – 2.0 Power Density – Estimate | Power Density: W/m2 & Lux |

| Lighting Lux Level | Bedroom – 227 lux – Calculated figure Office Area – 300 lux Shower – 100 lux Corridor – 100 lux – Calculated figure Glass Wash – 500 lux – Estimate Linen – 300 lux – Estimate Plant Room – 200 lux – Estimate Reception – 300 lux - Estimate Restaurant/Bar – 200 lux – Estimate Store /Archive – 100 lux – Calculated figure Toilet – 200 lux – Estimate Team Room – 100 lux - Estimate | 227 lux in Bedrooms |
| --- | --- | --- |
| Lighting Control | Bedroom – Switch Office Area - Switch Shower – Switch Corridor – Auto On/Dimmed Glass Wash – Switch Linen – Auto On/Off Plant Room – Switch Restaurant – None Store – Auto On/Off Toilet – Auto On/Off | None, Switch, PIR Dimming & PIR |
| Solar Photovoltaic Panel | 95.61 m2 22.6 % efficiency PV | 95.61 m2 PV |